## Dashboard
Castellan BESS — Behind-the-Meter Storage Model
Account 200027805928 · Ontario GS >50 kW · built from interval data + 22 months of bills
THE SITUATION
• Winter-heating load: peaks ~115–120 kW in winter, <25 kW summer (load factor 22%).
• Bill dominated by a demand charge ~$25.8/kW-month — each kW of peak ≈ $310/yr.
• A battery saves almost entirely by shaving the winter peak (flat energy rate → little arbitrage).
• Peaks are long plateaus (6–72 h) so the battery is energy-limited: duration matters, not power.
HEADLINE — value pick 50 kW / 150 kWh (live)
Yr-1 total benefit
Net capex (after ITC)
Simple payback
15-yr NPV @ discount
IRR
HOW TO USE
Assumptions | Edit yellow cells — tariff, battery, capex, ITC, value streams. All else recalcs.
Sizing Comparison | 9 sizes: benefit, capex, payback, NPV, IRR. Green = recommended.
Bill Impact | Month-by-month bill before vs after.
Dispatch | Hour-by-hour of what the battery does on a cold week + state of charge.
Cash Flow | 15-yr cash flow for two sizes with payback / NPV / IRR.
Backup Resilience | Outage runtime by season.
Sensitivity | Payback heat-map vs demand charge and battery cost.
⚠ Confirm the $25.84/kW demand charge (kW vs 15-min kVA) against the real tariff — it drives the whole result.

## Assumptions
Castellan BESS — Assumptions (edit the YELLOW cells; everything recalculates)
TARIFF (derived from 22 bills, R²=0.9994)
Energy rate ($/kWh) | 0.1109 | Blended commodity + delivery
Demand charge ($/kW-month) | 25.84 | ⚠ CONFIRM vs tariff — drives everything
Fixed monthly charge ($) | 137 | Not affected by BESS
Demand-rate escalation (%/yr) | 2.5% | Utility inflation
TOU energy spread on-vs-off ($/kWh) | 0 | Set >0 if on TOU/ULO to value arbitrage
Arbitrage cycles per year | 250 | Full charge/discharge cycles for arbitrage
BATTERY / TECH
Round-trip efficiency | 90%
Usable depth of discharge | 80% | SOC 10–90%
Capacity degradation (%/yr) | 2.5% | Lowers savings over time
CAPEX (installed, CAD)
Power cost ($/kW) | 400 | Inverter / PCS
Energy cost ($/kWh) | 500 | Battery modules — set 0 to test
Fixed install / BOS ($) | 20000 | EPC, interconnect, controls
Clean-Tech ITC (%) | 30% | Federal refundable credit
OPERATING / FINANCE (model horizon = 15 yrs)
O&M (% of capex / yr) | 1.5%
O&M inflation (%/yr) | 2%
Discount rate (%) | 8% | For NPV
Resilience / backup value ($/yr) | 0 | Optional $ you assign to outage protection

## Sizing Comparison
Battery Sizing Comparison — all formulas live off the Assumptions tab
Annual benefit = demand savings (kW shaved × demand rate) + arbitrage + resilience value.
Power (kW) | Energy (kWh) | Dur (h) | kW-mo shaved/yr | Demand savings $ | Arbitrage $/yr | Resilience $/yr | Yr-1 total benefit $ | Capex $ | ITC $ | Net capex $ | Payback (yr) | 15-yr NPV $ | IRR
30 | 60 |  | 153.9
50 | 100 |  | 199.7
50 | 150 |  | 238.7
75 | 150 |  | 238.7
100 | 200 |  | 261
100 | 300 |  | 285.8
100 | 400 |  | 301.2
150 | 300 |  | 285.8
200 | 400 |  | 301.2
Green = value pick. Change Energy cost to 0 on Assumptions and watch Capex/Payback/NPV/IRR all move.

## CF_Calc
Cash-flow engine (15 yrs) — feeds NPV/IRR on Sizing Comparison. Live.
size | net | benefit | capex | Y0 | Y1 | Y2 | Y3 | Y4 | Y5 | Y6 | Y7 | Y8 | Y9 | Y10 | Y11 | Y12 | Y13 | Y14 | Y15 | NPV | IRR
30/60
50/100
50/150
75/150
100/200
100/300
100/400
150/300
200/400

## Load Profile
Load Analysis — Calendar 2025 (representative year)
Annual energy | 224726
Peak demand | 114.9
Average load | 25.7
Load factor
Month | Energy (kWh) | Peak (kW) | Demand chg $ | Energy chg $ | Total $
Jan | 35978 | 80.9
Feb | 34421 | 90.6
Mar | 43051 | 112.4
Apr | 28133 | 81.2
May | 6245 | 29.5
Jun | 4765 | 26.5
Jul | 4316 | 21.3
Aug | 3468 | 24
Sep | 2927 | 16.9
Oct | 2606 | 18.4
Nov | 34658 | 114.9
Dec | 24158 | 70.9
TOTAL

## Bill Impact
Monthly Bill — Before vs After (50 kW / 150 kWh)
Month | Peak before kW | Peak after kW | kW shaved | Bill before $ | Bill after $ | Savings $
Jan | 80.9 | 54.7
Feb | 90.6 | 58.5
Mar | 112.4 | 93.6
Apr | 81.2 | 64.9
May | 29.5 | 9.9
Jun | 26.5 | 11.4
Jul | 21.3 | 6.3
Aug | 24 | 5.6
Sep | 16.9 | 5.3
Oct | 18.4 | 5.8
Nov | 114.9 | 90
Dec | 70.9 | 42.9
TOTAL

## Dispatch
What the Battery Does — cold week Mar 2025 (100 kW/300 kWh, ceiling ~80.9 kW)
Hour | Load kW | Net grid kW | SOC kWh
Mon 00:00 | 47.4 | 47.4 | 300
Mon 01:00 | 48.1 | 48.1 | 300
Mon 02:00 | 47.8 | 47.8 | 300
Mon 03:00 | 47.8 | 47.8 | 300
Mon 04:00 | 29.9 | 29.9 | 300
Mon 05:00 | 29.2 | 29.2 | 300
Mon 06:00 | 29.5 | 29.5 | 300
Mon 07:00 | 36.9 | 36.9 | 300
Mon 08:00 | 45.9 | 45.9 | 300
Mon 09:00 | 46 | 46 | 300
Mon 10:00 | 45.3 | 45.3 | 300
Mon 11:00 | 48 | 48 | 300
Mon 12:00 | 60.1 | 60.1 | 300
Mon 13:00 | 64 | 64 | 300
Mon 14:00 | 63.8 | 63.8 | 300
Mon 15:00 | 63.6 | 63.6 | 300
Mon 16:00 | 63.2 | 63.2 | 300
Mon 17:00 | 62.5 | 62.5 | 300
Mon 18:00 | 73.1 | 73.1 | 300
Mon 19:00 | 73.3 | 73.3 | 300
Mon 20:00 | 82.1 | 80.9 | 298.7
Mon 21:00 | 81.4 | 80.9 | 298.2
Mon 22:00 | 72.2 | 74.1 | 300
Mon 23:00 | 59.8 | 59.8 | 300
Tue 00:00 | 50.5 | 50.5 | 300
Tue 01:00 | 47.5 | 47.5 | 300
Tue 02:00 | 47.9 | 47.9 | 300
Tue 03:00 | 47.5 | 47.5 | 300
Tue 04:00 | 49.7 | 49.7 | 300
Tue 05:00 | 51.3 | 51.3 | 300
Tue 06:00 | 54.1 | 54.1 | 300
Tue 07:00 | 54.4 | 54.4 | 300
Tue 08:00 | 59.6 | 59.6 | 300
Tue 09:00 | 70.6 | 70.6 | 300
Tue 10:00 | 69.8 | 69.8 | 300
Tue 11:00 | 70 | 70 | 300
Tue 12:00 | 70.1 | 70.1 | 300
Tue 13:00 | 67 | 67 | 300
Tue 14:00 | 66.2 | 66.2 | 300
Tue 15:00 | 67.9 | 67.9 | 300
Tue 16:00 | 69.3 | 69.3 | 300
Tue 17:00 | 68.3 | 68.3 | 300
Tue 18:00 | 67 | 67 | 300
Tue 19:00 | 65.6 | 65.6 | 300
Tue 20:00 | 66.1 | 66.1 | 300
Tue 21:00 | 72.3 | 72.3 | 300
Tue 22:00 | 73.1 | 73.1 | 300
Tue 23:00 | 66.9 | 66.9 | 300
Wed 00:00 | 58.6 | 58.6 | 300
Wed 01:00 | 56.8 | 56.8 | 300
Wed 02:00 | 55.9 | 55.9 | 300
Wed 03:00 | 54.8 | 54.8 | 300
Wed 04:00 | 54 | 54 | 300
Wed 05:00 | 53.9 | 53.9 | 300
Wed 06:00 | 56.6 | 56.6 | 300
Wed 07:00 | 61.7 | 61.7 | 300
Wed 08:00 | 72.4 | 72.4 | 300
Wed 09:00 | 73 | 73 | 300
Wed 10:00 | 73.7 | 73.7 | 300
Wed 11:00 | 67.6 | 67.6 | 300
Wed 12:00 | 64.3 | 64.3 | 300
Wed 13:00 | 64.1 | 64.1 | 300
Wed 14:00 | 66.3 | 66.3 | 300
Wed 15:00 | 72.5 | 72.5 | 300
Wed 16:00 | 75.1 | 75.1 | 300
Wed 17:00 | 70.9 | 70.9 | 300
Wed 18:00 | 70.7 | 70.7 | 300
Wed 19:00 | 75.2 | 75.2 | 300
Wed 20:00 | 79.1 | 79.1 | 300
Wed 21:00 | 79.4 | 79.4 | 300
Wed 22:00 | 72.1 | 72.1 | 300
Wed 23:00 | 68.6 | 68.6 | 300
Thu 00:00 | 68.4 | 68.4 | 300
Thu 01:00 | 68 | 68 | 300
Thu 02:00 | 67.9 | 67.9 | 300
Thu 03:00 | 67.7 | 67.7 | 300
Thu 04:00 | 65.3 | 65.3 | 300
Thu 05:00 | 59.8 | 59.8 | 300
Thu 06:00 | 60.1 | 60.1 | 300
Thu 07:00 | 53.8 | 53.8 | 300
Thu 08:00 | 51.1 | 51.1 | 300
Thu 09:00 | 54.1 | 54.1 | 300
Thu 10:00 | 66.8 | 66.8 | 300
Thu 11:00 | 61.7 | 61.7 | 300
Thu 12:00 | 57.8 | 57.8 | 300
Thu 13:00 | 55.6 | 55.6 | 300
Thu 14:00 | 53.5 | 53.5 | 300
Thu 15:00 | 53.8 | 53.8 | 300
Thu 16:00 | 57.5 | 57.5 | 300
Thu 17:00 | 71.7 | 71.7 | 300
Thu 18:00 | 64.2 | 64.2 | 300
Thu 19:00 | 57.7 | 57.7 | 300
Thu 20:00 | 57.9 | 57.9 | 300
Thu 21:00 | 57.4 | 57.4 | 300
Thu 22:00 | 48.7 | 48.7 | 300
Thu 23:00 | 46.9 | 46.9 | 300
Fri 00:00 | 46.7 | 46.7 | 300
Fri 01:00 | 45.9 | 45.9 | 300
Fri 02:00 | 46.2 | 46.2 | 300
Fri 03:00 | 45.8 | 45.8 | 300
Fri 04:00 | 45.8 | 45.8 | 300
Fri 05:00 | 45.8 | 45.8 | 300
Fri 06:00 | 46.4 | 46.4 | 300
Fri 07:00 | 50.8 | 50.8 | 300
Fri 08:00 | 55.4 | 55.4 | 300
Fri 09:00 | 58.8 | 58.8 | 300
Fri 10:00 | 58.9 | 58.9 | 300
Fri 11:00 | 63.7 | 63.7 | 300
Fri 12:00 | 67.2 | 67.2 | 300
Fri 13:00 | 66.5 | 66.5 | 300
Fri 14:00 | 66.2 | 66.2 | 300
Fri 15:00 | 65.7 | 65.7 | 300
Fri 16:00 | 70.8 | 70.8 | 300
Fri 17:00 | 71.2 | 71.2 | 300
Fri 18:00 | 70.5 | 70.5 | 300
Fri 19:00 | 61.1 | 61.1 | 300
Fri 20:00 | 50.6 | 50.6 | 300
Fri 21:00 | 47.5 | 47.5 | 300
Fri 22:00 | 46.1 | 46.1 | 300
Fri 23:00 | 46.5 | 46.5 | 300
Sat 00:00 | 47.5 | 47.5 | 300
Sat 01:00 | 48 | 48 | 300
Sat 02:00 | 46.4 | 46.4 | 300
Sat 03:00 | 46.4 | 46.4 | 300
Sat 04:00 | 46.4 | 46.4 | 300
Sat 05:00 | 46.5 | 46.5 | 300
Sat 06:00 | 46.4 | 46.4 | 300
Sat 07:00 | 46.6 | 46.6 | 300
Sat 08:00 | 52.8 | 52.8 | 300
Sat 09:00 | 54.4 | 54.4 | 300
Sat 10:00 | 54.2 | 54.2 | 300
Sat 11:00 | 56.7 | 56.7 | 300
Sat 12:00 | 60.8 | 60.8 | 300
Sat 13:00 | 63.4 | 63.4 | 300
Sat 14:00 | 67.8 | 67.8 | 300
Sat 15:00 | 69.4 | 69.4 | 300
Sat 16:00 | 67.4 | 67.4 | 300
Sat 17:00 | 62.4 | 62.4 | 300
Sat 18:00 | 54.3 | 54.3 | 300
Sat 19:00 | 48.5 | 48.5 | 300
Sat 20:00 | 47.6 | 47.6 | 300
Sat 21:00 | 51.2 | 51.2 | 300
Sat 22:00 | 53.5 | 53.5 | 300
Sat 23:00 | 50.6 | 50.6 | 300
Sun 00:00 | 49.7 | 49.7 | 300
Sun 01:00 | 48.3 | 48.3 | 300
Sun 02:00 | 47.2 | 47.2 | 300
Sun 03:00 | 46.9 | 46.9 | 300
Sun 04:00 | 46.9 | 46.9 | 300
Sun 05:00 | 47.2 | 47.2 | 300
Sun 06:00 | 46.6 | 46.6 | 300
Sun 07:00 | 46.9 | 46.9 | 300
Sun 08:00 | 51.5 | 51.5 | 300
Sun 09:00 | 54.5 | 54.5 | 300
Sun 10:00 | 57.4 | 57.4 | 300
Sun 11:00 | 60.1 | 60.1 | 300
Sun 12:00 | 62.5 | 62.5 | 300
Sun 13:00 | 65.7 | 65.7 | 300
Sun 14:00 | 62.4 | 62.4 | 300
Sun 15:00 | 61.7 | 61.7 | 300
Sun 16:00 | 64.1 | 64.1 | 300
Sun 17:00 | 76 | 76 | 300
Sun 18:00 | 76.7 | 76.7 | 300
Sun 19:00 | 76.7 | 76.7 | 300
Sun 20:00 | 76.5 | 76.5 | 300
Sun 21:00 | 77.2 | 77.2 | 300
Sun 22:00 | 77.2 | 77.2 | 300
Sun 23:00 | 76.5 | 76.5 | 300

## Cash Flow
15-Year Cash Flow — pulls live from CF_Calc
These two sizes mirror the CF_Calc engine. Change Assumptions and they move.
Value pick: 50/150 |  |  | Deep shave: 100/300
Year | Net cash flow $ | Cumulative $ | Year | Net cash flow $ | Cumulative $
0 |  |  | 0
1 |  |  | 1
2 |  |  | 2
3 |  |  | 3
4 |  |  | 4
5 |  |  | 5
6 |  |  | 6
7 |  |  | 7
8 |  |  | 8
9 |  |  | 9
10 |  |  | 10
11 |  |  | 11
12 |  |  | 12
13 |  |  | 13
14 |  |  | 14
15 |  |  | 15
Payback (yr) |  |  | Payback (yr)
NPV |  |  | NPV
IRR |  |  | IRR

## Backup Resilience
Backup / Resilience — outage runtime (hours)
Usable = Energy × DoD (Assumptions!B13). Runtime = usable ÷ load served.
Energy kWh | Usable kWh | Winter ~48 kW | Shoulder ~25 kW | Summer ~5 kW | Critical ~10 kW
60
100
150
200
300
400

## Sensitivity
Sensitivity — Payback (yrs) of 50/150 vs demand charge & battery cost
Responds to the ITC assumption. Net capex=150×$/kWh×(1−ITC); savings=238.7×demand-rate.
Demand $/kW ↓ / Battery $/kWh → | 400 | 500 | 600 | 700 | 800
10
15
20
25.84
30
40
Cells = simple payback in years. Lower is better.