## BOM with Cost-Down
Residential Solar + BESS Upgrade — BOM with Cost-Down Analysis
75 kW PV array ¦ ~650 kWh Li-ion BESS ¦ 480V 3Ø ¦ SMA Sunny Tripower CORE1 + Sunny Island cluster
Category | Item | Description | Qty | Scope | Current Est. ($CAD) | Necessity | Cost-Down Action | Quoted Price (CAD) | Total Price (CAD) | Potential Savings ($CAD) | Notes / Source
Main Equipment | PV Inverter | SMA SunnyBoy 7.7kW | 10 | PV | 12000 | ELIMINATE | OUT OF SCOPE — remove from BOM (per client direction) | 4520 | 45200 | -33200 | Originally $12K (480V 3Ø). Confirm coverage by another scope/contractor.
Main Equipment | Battery Inverter | LuxPower GEN-HB-US 25KW (parallel cluster) | 3 | BATTERY | 35000 | REQUIRED | Validate 5-unit cluster sizing vs. actual peak load — possible to reduce to 3-4 units? 3 units confirmed | 6200 | 18600 | 16400 | Grid-forming. Each Sunny Island ~$7K. Right-sizing could drop 1-2 units. right sized - LuxPower GEN-HB-US-25kW -qty 3, quote recieved
Main Equipment | Battery System | 48V Li-ion BESS (~650 kWh) | 1 system | EXISTING | 0 | EXISTING | No action — client already owns |  |  | 0 | Sunk cost — excluded from active BOM total. Original quote was $520K.
Main Equipment | PV Modules | ~75 kW DC array (500W modules) 600V DC System | 150 | PV | 16500 | REQUIRED | Spec 550W+ modules to reduce count to ~135 — saves on connectors, racking, labour 15kW per tracker - BO can be sourcing it |  |  | 2000 | $200/module is reasonable. Tier-2 brands could save further but check warranty terms.
Main Equipment | EMS Controller | SMA Data Manager / Microgrid Controller | 1 | SHARED | 3500 | REQUIRED | Keep — required for grid-forming coordination |  |  | 0 | Recommended by SMA for multi-inverter clusters.
PV DC Side | PV Wire | #10 AWG Cu PV Wire (USE-2) | As req'd | PV | 15000 | REVIEW | Re-quote — $15K appears HIGH. ~450m of #10 PV wire for 75kW should be ~$1.5-3K. Needs to be confirmed on site with site visit from Rajib/BO/Arun after confirmation on PV module wattage/volt config (June) |  |  | 11000 | Verify takeoff. Likely overestimated by ~10x.
PV DC Side | Home Run | 4 AWG | 250 m | PV | 5000 | REQUIRED | Confirm voltage drop calc to validate 4 AWG vs 6 AWG - based on PV module wattage |  |  | 500 | Reasonable. Gauge optimization could yield small savings.
PV DC Side | Connectors | MC4 compatible | 310 | PV | 1500 | REQUIRED | Use module-matched connectors to avoid type mismatch issues |  |  | 0 | $5/connector — fair pricing. 310 = 150 modules x 2 + spares.
PV DC Side | DC Disconnect | 1000V DC isolator | 1-2 | PV | 1200 | ELIMINATE | REMOVE — CORE1 has integrated DC inputs. Confirm AHJ does not require external disconnect |  |  | 1200 | Note in original BOM flagged as Optional.
PV DC Side | Cable Management | Conduit + tray + clips (underground rated) | As req'd | SHARED | 15000 | REVIEW | VE option: above-ground tray where feasible vs underground rated conduit |  |  | 4000 | Underground rated drives cost. Mostly PV DC runs — could split scope.
Battery DC | DC Busbar | Copper busbar ≥1200 A | 2 | BATTERY | 7500 | REQUIRED | Keep — main + and - bus |  |  | 0 | Standard for cluster of this size.
Battery DC | Battery Rack Fuses | 250-300 A DC fuses | 8-12 | BATTERY | 2200 | REVIEW | Choose either fuses OR breakers per rack — typically not both |  |  | 2200 | If rack breakers (next row) are kept, fuses become redundant. Confirm with BMS spec.
Battery DC | Battery Rack Breaker | 250-300 A DC Breaker | 8-12 | BATTERY | 11000 | REQUIRED | Keep breakers (preferred over fuses for resettable protection) |  |  | 0 | If kept, eliminate fuses above for $2.2K savings.
Battery DC | Battery Disconnect | 1200 A DC disconnect | 1 | BATTERY | 6000 | REQUIRED | Keep — main isolation, code requirement |  |  | 0 | Critical safety device.
Battery DC | Battery Cables | 4/0 AWG Cu (or parallel sets) | As req'd | BATTERY | 22000 | REQUIRED | Explore aluminum equivalent where rack landings permit (~30-40% material savings) |  |  | 5000 | Cu pricing is volatile. Confirm OEM-approved Al lugs.
Battery DC | BMS | Integrated BMS | 1 system | BATTERY | 0 | REQUIRED | Included with battery |  |  | 0 | No cost — bundled.
AC Power | AC Main Panel | 480V 3Ø distribution panel | 1 | SHARED | 12000 | ELIMINATE | CONFIRM client can re-use existing panel — original BOM flagged this as a possibility |  |  | 12000 | Largest single cost-down opportunity. Verify panel ampacity and breaker space.
AC Power | PV Feeder Cable | #4 AWG Cu | As req'd | PV | 3000 | REQUIRED | Keep — sized appropriately |  |  | 0 | CORE1 to panel feeder.
AC Power | Battery Inverter Cable | 4/0 AWG Cu | As req'd | BATTERY | 10000 | REVIEW | Re-quote with firm takeoff — original notes flag range as $2-12K (overestimated) |  |  | 5000 | Use mid-range $5K based on typical Sunny Island runs.
AC Power | Main Bus Cable | 3/0 AWG Cu | As req'd | SHARED | 9000 | REQUIRED | Keep — panel distribution |  |  | 0 | Standard sizing.
Protection | PV Breaker | 80 A, 3P | 1 | PV | 500 | REQUIRED | Keep |  |  | 0 | CORE1 output protection.
Protection | Battery Inverter Breakers | 70 A, 3P | 5 | BATTERY | 2500 | REQUIRED | Keep — one per inverter |  |  | 0 | Reduces if inverter count drops.
Protection | Main Breaker | 150 A, 3P | 1 | SHARED | 1200 | REQUIRED | Keep |  |  | 0 | AC bus main.
Protection | Surge Protection | Type 1 or 2 SPD (AC & DC) | 4 | SHARED | 3500 | RECOMMENDED | Downgrade to Type 2 only on AC side if not required by code/insurance |  |  | 1000 | Type 1 typically only required if exposed to direct lightning.
Grounding | Ground Conductor | #2 AWG Cu stranded | 350m | SHARED | 7000 | REQUIRED | Keep |  |  | 0 | Equipment grounding.
Grounding | Ground Rods | 5/8" x 8 ft Cu rods | 4-6 | SHARED | 500 | REQUIRED | Keep — original qty (46085) was a typo, corrected to 4-6 |  |  | 0 | Site dependent. Verify against soil resistivity.
Grounding | Ground Bus | Copper ground bar | 1 | SHARED | 600 | REQUIRED | Keep |  |  | 0 | Panel grounding.
Grounding | Labels & Signage | NEC/CEC compliant | All cabinets | SHARED | 1200 | REQUIRED | Keep — code/safety compliance |  |  | 0 | Non-negotiable for AHJ approval.
Controls | Monitoring System | SMA monitoring portal | 1 | SHARED | 0 | REQUIRED | Included with EMS |  |  | 0 | Bundled — no cost.
Controls | Energy Meter | Internal PV/BESS meter | 1 | SHARED | 2000 | ELIMINATE | REMOVE — site already has revenue-grade meter; original BOM flagged 'Not required' |  |  | 2000 | Quick win. Confirm client doesn't want internal monitoring view.
Controls | Communication Cables | Ethernet / RS485 | 1000m | SHARED | 2500 | REQUIRED | Keep — inverter comms |  |  | 0 | Validate run length — could trim if not full 1000m.
Engineering | Basic SLD + Layout + Prelim BOM | PV design and integration included | - | SHARED | 13000 | REQUIRED | Keep |  |  | 0 | Foundational deliverable.
Engineering | Detailed Electrical Design | CEC compliance | - | SHARED | 7500 | REQUIRED | Keep |  |  | 0 | Required for permitting.
Engineering | Battery Integration & Control Design | - | - | BATTERY | 5500 | REQUIRED | Keep |  |  | 0 | Critical for grid-forming coordination.
Engineering | PEng Stamping | If required by AHJ | - | SHARED | 0 | ELIMINATE | Confirm AHJ requirement — typically required at this scale |  |  | 0 | Cost TBD. Budget $2-5K placeholder.
Studies | Short Circuit Study | - | - | SHARED | 3000 | REQUIRED | MOVE TO COST-DOWN — confirm AHJ requirement; defer if not mandatory |  |  | 3000 | Often bundled with Protection Study — see opportunity to combine.
Studies | Protection Study | - | - | SHARED | 7500 | ELIMINATE | MOVE TO COST-DOWN — confirm AHJ requirement; defer if not mandatory |  |  | 7500 | If kept, bundle with SC Study for combined cost ~$8.5K vs $10.5K.
Studies | Arc Flash Study | - | - | SHARED | 8000 | ELIMINATE | MOVE TO COST-DOWN — confirm AHJ requirement; at 480V res/light commercial often not mandatory |  |  | 8000 | Original BOM noted $5K min if needed.
Studies | Fire Suppression | Battery room fire suppression | - | BATTERY | 0 | ELIMINATE | MOVE TO COST-DOWN — eliminate scope by using outdoor/rated enclosure |  |  | 0 | Cost TBD if required. Outdoor enclosure removes need entirely.
Studies | Ventilation Study & Upgrade | - | - | BATTERY | 0 | ELIMINATE | MOVE TO COST-DOWN — eliminate scope by using outdoor enclosure |  |  | 0 | Cost TBD if required. Outdoor enclosure removes need entirely.
Labour | Labour and Trenching | PV + BESS install | - | SHARED | 77500 | REQUIRED | Get firm quotes from 2-3 contractors; consider sub-scope splits |  |  | 10000 | Original range $55-100K. Used midpoint. Competitive bid could trim 10-15%.
TOTALS |  |  | Active BOM Total → |  | 330900 |  | Total Potential Savings → |  |  | 57600
|  |  | Optimized Target → |  | 273300
SCOPE BREAKDOWN
Scope |  |  |  |  | Current Cost |  | Savings Identified |  |  | Optimized Target
PV |  |  |  |  | 54700 |  |  |  |  | -18500 | 73200
BATTERY |  |  |  |  | 101700 |  |  |  |  | 28600 | 73100
SHARED |  |  |  |  | 174500 |  |  |  |  | 47500 | 127000
HVAC | mini-split | 2.5-3k | 15 kw split
Senville
5-10k

## Cost-Down Summary
Cost-Down Opportunities — Ranked by Impact
Rank | Opportunity | Type | Effort | Savings ($CAD) | Decision Owner / Action
1 | Re-use existing AC main panel | Eliminate | Low | 12000 | Client confirmation — verify panel ampacity and available breaker space
2 | Remove PV Inverter (out of scope) | Eliminate | Low | 12000 | Client confirmed — covered by another scope/contractor
3 | Re-quote PV Wire (likely 10x overestimated) | Re-quote | Low | 11000 | Procurement — get firm vendor quote based on actual takeoff
4 | Defer Arc Flash Study if AHJ allows | Eliminate | Low | 8000 | Engineering — confirm AHJ requirement at 480V residential
5 | Defer Protection Study if AHJ allows | Eliminate | Low | 7500 | Engineering — confirm AHJ requirement; bundle with SC if both kept
6 | Right-size battery inverter cluster (5 → 3-4) | Re-spec | Medium | 7000 | Engineering — load analysis to validate peak demand
7 | Aluminum battery cabling where permitted | Substitute | Medium | 5000 | Engineering — confirm OEM-approved Al lugs at rack landings
8 | Refine Battery Inverter Cable takeoff | Re-quote | Low | 5000 | Procurement — get firm takeoff from layout
9 | Above-ground cable tray vs underground | Re-spec | Medium | 4000 | Engineering — site walk to identify above-ground runs
10 | Defer Short Circuit Study if AHJ allows | Eliminate | Low | 3000 | Engineering — confirm AHJ requirement
11 | Eliminate redundant rack fuses (keep breakers) | Eliminate | Low | 2200 | Engineering — confirm BMS spec doesn't require both
12 | Spec 550W+ PV modules (reduce count) | Re-spec | Low | 2000 | Procurement — verify module availability and warranty
13 | Eliminate internal energy meter | Eliminate | Low | 2000 | Client confirmation — site has revenue-grade meter
14 | Eliminate redundant external DC disconnect | Eliminate | Low | 1200 | Engineering — confirm CORE1 integrated input meets AHJ
15 | Downgrade Type 1 SPD to Type 2 (AC side) | Re-spec | Low | 1000 | Engineering — confirm lightning exposure assessment
16 | Optimize home run gauge (4 → 6 AWG if VD permits) | Re-spec | Low | 500 | Engineering — voltage drop calc
17 | Eliminate Fire Suppression scope (outdoor enclosure) | Eliminate | Medium | 0 | Engineering — spec outdoor/rated battery enclosure (avoids unknown future cost)
18 | Eliminate Ventilation scope (outdoor enclosure) | Eliminate | Medium | 0 | Engineering — spec outdoor/rated battery enclosure (avoids unknown future cost)
19 | Competitive bid for labour/trenching | Re-quote | Medium | 10000 | Procurement — solicit 2-3 quotes; consider scope splits
|  |  | TOTAL POTENTIAL SAVINGS → | 93400
QUICK WINS (Low effort, immediate)
Low-effort items totalling ~$73,400 — these require only client/AHJ confirmations and re-quotes, no design changes:
• AC panel re-use ($12K) • Remove PV Inverter ($12K) • PV wire re-quote ($11K) • Arc flash deferral ($8K) • Protection study deferral ($7.5K) • Battery inverter cable re-quote ($5K) • Short circuit study deferral ($3K) • Eliminate fuses ($2.2K) • Module re-spec ($2K) • Eliminate energy meter ($2K) • Eliminate DC disconnect ($1.2K) • Downgrade SPD ($1K) • Home run gauge ($0.5K)

## Notes & Assumptions
Notes, Assumptions & Data Hygiene
LEGEND
REQUIRED | Core to system function or code/safety compliance — keep as-is
RECOMMENDED | Best practice but reducible — review for cost-down
OPTIONAL | Nice-to-have, can be eliminated without functional impact
REVIEW | Pricing, sizing, or necessity needs validation before proceeding
ELIMINATE | Confirmed candidate for removal — quick win
EXISTING | Already owned by client — no active cost
DATA HYGIENE FIXES FROM ORIGINAL BOM
Ground Rods qty | Original showed '46085' — corrected to 4-6 (typo)
PV Inverter row | Original had stray '1.5' value at end of row — removed
Prices in Notes column | Pricing in 'Notes' column moved to dedicated price column
Battery System ($520K) | Marked EXISTING — excluded from active total since client already owns
Labour cost | Original showed range '$55,000-$100,000' — used midpoint $77,500 for analysis
KEY ASSUMPTIONS
System voltage | 480V 3Ø confirmed throughout
Battery chemistry | Li-ion (assumed — confirms BMS, fire safety, ventilation requirements)
Site type | Residential (with light commercial characteristics given 75kW PV / 650 kWh BESS)
Currency | All values in CAD
AHJ | Assumed Ontario ESA — confirm specific jurisdiction for code-driven items
ITEMS REQUIRING CLIENT/AHJ DECISIONS
Existing AC panel re-use | Single largest savings — needs client confirmation
Arc Flash Study requirement | $8K item — confirm with AHJ whether mandatory
PEng Stamping | Cost TBD — typically required at this scale
Fire Safety scope | Cost TBD — depends on battery enclosure type/location
Ventilation scope | Cost TBD — outdoor enclosure can eliminate scope
ITEMS NOT IN ORIGINAL BOM (FLAG FOR REVIEW)
Permitting fees | Not listed — typically $500-2,000
Commissioning & testing | Not listed separately — confirm if bundled in labour
Spare parts / warranty | Not listed — consider 2-5% spares budget
Contingency | No contingency line — recommend 10% of hard costs