## Summary
Metric | Value
engine | quest
annual_load_kwh | 175530
peak_load_kw | 114.9
annual_pv_kwh | 95265
status_quo_bill_cad | 22289
pv_only_bill_cad | 11323
project_bill_cad | 8503
annual_pv_savings_cad | 10966
annual_battery_savings_cad | 2821
annual_total_savings_cad | 13787
annual_energy_savings_cad | 2833
annual_demand_savings_cad | 0
avg_monthly_peak_reduction_kw | -36.4
solar_self_consumption_no_battery_pct | 33.3
solar_self_consumption_with_battery_pct | 33.4
capex / bom_base_cad | 330900
capex / bom_scenario | current_total
capex / battery_capex_cad | 0
capex / adders_cad | 0
capex / contingency_cad | 33090
capex / total_capex_cad | 363990
annual_maintenance_cad | 2000
metrics / total_capex_cad | 363990
metrics / year1_savings_cad | 13786.81
metrics / npv_cad | -228637.11
metrics / irr_pct | -1.94
metrics / simple_payback_years
metrics / discount_rate_pct | 8
metrics / project_life_years | 20
sizing_recommendation / recommended_kwh | 1300
sizing_recommendation / recommended_kw | 150
sizing_recommendation / npv_at_recommended_cad | -227867
sizing_recommendation / note | Existing pack is ~650 kWh; recommendation is the NPV-maximising size across the swept range under current assumptions.

## Assumptions
Group | Parameter | Value
battery | energy_capacity_kwh | 650
battery | power_rating_kw | 75
battery | round_trip_efficiency | 0.88
battery | state_of_charge_min | 0.1
battery | state_of_charge_max | 0.9
battery | state_of_charge_init | 0.5
battery | self_discharge_efficiency | 1
battery | transformer_rating_kw | 1000
battery | annual_degradation_rate | 0.02
battery | battery_capex_included | FALSE
battery | battery_capex_cad | 0
battery | replacement_year | 0
battery | replacement_cost_cad | 0
financial | currency | CAD
financial | discount_rate | 0.08
financial | project_life_years | 20
financial | electricity_escalation_rate | 0.03
financial | opex_escalation_rate | 0.02
financial | annual_maintenance_cad | 2000
financial | pv_degradation_rate | 0.005
financial | bom_scenario | current_total
financial | contingency_pct | 0.1
financial | capex_overrides / installed_cost_cad
financial | capex_overrides / epc_install_cost_cad | 0
financial | capex_overrides / interconnection_cost_cad | 0
financial | capex_overrides / engineering_cost_cad | 0
financial | capex_overrides / other_adders_cad | 0
operating | model_year | 2025
operating | solver | glpk
operating | engine | auto
operating | apply_intraday_load_shape | FALSE
operating | load_value_interpretation | hourly_kw
operating | representative_window | most_recent_12_months
operating | load_source_column | metered
operating | solar / pv_system_kw | 75
operating | solar / latitude_deg | 44
operating | solar / target_capacity_factor | 0.145
operating | solar / monthly_irradiance_factors | [0.45, 0.62, 0.88, 1.05, 1.22, 1.28, 1.3, 1.18, 0.95, 0.68, 0.42, 0.35]
rate | name | Ontario RPP Time-of-Use
rate | utility | Ontario (assumed)
rate | currency | CAD
rate | plan | tou
rate | energy_rates_cad_per_kwh / off_peak | 0.098
rate | energy_rates_cad_per_kwh / mid_peak | 0.157
rate | energy_rates_cad_per_kwh / on_peak | 0.203
rate | energy_rates_cad_per_kwh / ulo_overnight | 0.039
rate | energy_rates_cad_per_kwh / flat | 0.122
rate | tou_periods / summer_months | [5, 6, 7, 8, 9, 10]
rate | tou_periods / on_peak_hours_summer | [11, 12, 13, 14, 15, 16]
rate | tou_periods / mid_peak_hours_summer | [7, 8, 9, 10, 17, 18]
rate | tou_periods / on_peak_hours_winter | [7, 8, 9, 10, 17, 18]
rate | tou_periods / mid_peak_hours_winter | [11, 12, 13, 14, 15, 16]
rate | ulo_overnight_hours | [23, 0, 1, 2, 3, 4, 5, 6]
rate | ulo_on_peak_hours_weekday | [16, 17, 18, 19, 20]
rate | demand_charge_cad_per_kw | 0
rate | net_metering / enabled | TRUE
rate | net_metering / credit_mode | flat
rate | net_metering / sell_price_cad_per_kwh | 0.098

## BOM (full)
category | item | description | qty | scope | necessity | unit_cost | total_cost | capex_opex | included | notes
Main Equipment | PV Inverter | SMA SunnyBoy 7.7kW | 10 | PV | ELIMINATE | 1200 | 12000 | CAPEX | FALSE | Originally $12K (480V 3Ø). Confirm coverage by another scope/contractor.
Main Equipment | Battery Inverter | LuxPower GEN-HB-US 25KW (parallel cluster) | 3 | BATTERY | REQUIRED | 11666.67 | 35000 | CAPEX | TRUE | Grid-forming. Each Sunny Island ~$7K. Right-sizing could drop 1-2 units. right sized - LuxPower GEN-HB-US-25kW -qty 3, quote recieved
Main Equipment | Battery System | 48V Li-ion BESS (~650 kWh) | 1 system | EXISTING | EXISTING | 0 | 0 | CAPEX | FALSE | Sunk cost — excluded from active BOM total. Original quote was $520K.
Main Equipment | PV Modules | ~75 kW DC array (500W modules) 600V DC System | 150 | PV | REQUIRED | 110 | 16500 | CAPEX | TRUE | $200/module is reasonable. Tier-2 brands could save further but check warranty terms.
Main Equipment | EMS Controller | SMA Data Manager / Microgrid Controller | 1 | SHARED | REQUIRED | 3500 | 3500 | CAPEX | TRUE | Recommended by SMA for multi-inverter clusters.
PV DC Side | PV Wire | #10 AWG Cu PV Wire (USE-2) | As req'd | PV | REVIEW | 15000 | 15000 | CAPEX | TRUE | Verify takeoff. Likely overestimated by ~10x.
PV DC Side | Home Run | 4 AWG | 250 m | PV | REQUIRED | 5000 | 5000 | CAPEX | TRUE | Reasonable. Gauge optimization could yield small savings.
PV DC Side | Connectors | MC4 compatible | 310 | PV | REQUIRED | 4.84 | 1500 | CAPEX | TRUE | $5/connector — fair pricing. 310 = 150 modules x 2 + spares.
PV DC Side | DC Disconnect | 1000V DC isolator | 1-2 | PV | ELIMINATE | 1200 | 1200 | CAPEX | FALSE | Note in original BOM flagged as Optional.
PV DC Side | Cable Management | Conduit + tray + clips (underground rated) | As req'd | SHARED | REVIEW | 15000 | 15000 | CAPEX | TRUE | Underground rated drives cost. Mostly PV DC runs — could split scope.
Battery DC | DC Busbar | Copper busbar ≥1200 A | 2 | BATTERY | REQUIRED | 3750 | 7500 | CAPEX | TRUE | Standard for cluster of this size.
Battery DC | Battery Rack Fuses | 250-300 A DC fuses | 8-12 | BATTERY | REVIEW | 2200 | 2200 | CAPEX | TRUE | If rack breakers (next row) are kept, fuses become redundant. Confirm with BMS spec.
Battery DC | Battery Rack Breaker | 250-300 A DC Breaker | 8-12 | BATTERY | REQUIRED | 11000 | 11000 | CAPEX | TRUE | If kept, eliminate fuses above for $2.2K savings.
Battery DC | Battery Disconnect | 1200 A DC disconnect | 1 | BATTERY | REQUIRED | 6000 | 6000 | CAPEX | TRUE | Critical safety device.
Battery DC | Battery Cables | 4/0 AWG Cu (or parallel sets) | As req'd | BATTERY | REQUIRED | 22000 | 22000 | CAPEX | TRUE | Cu pricing is volatile. Confirm OEM-approved Al lugs.
Battery DC | BMS | Integrated BMS | 1 system | BATTERY | REQUIRED | 0 | 0 | CAPEX | TRUE | No cost — bundled.
AC Power | AC Main Panel | 480V 3Ø distribution panel | 1 | SHARED | ELIMINATE | 12000 | 12000 | CAPEX | FALSE | Largest single cost-down opportunity. Verify panel ampacity and breaker space.
AC Power | PV Feeder Cable | #4 AWG Cu | As req'd | PV | REQUIRED | 3000 | 3000 | CAPEX | TRUE | CORE1 to panel feeder.
AC Power | Battery Inverter Cable | 4/0 AWG Cu | As req'd | BATTERY | REVIEW | 10000 | 10000 | CAPEX | TRUE | Use mid-range $5K based on typical Sunny Island runs.
AC Power | Main Bus Cable | 3/0 AWG Cu | As req'd | SHARED | REQUIRED | 9000 | 9000 | CAPEX | TRUE | Standard sizing.
Protection | PV Breaker | 80 A, 3P | 1 | PV | REQUIRED | 500 | 500 | CAPEX | TRUE | CORE1 output protection.
Protection | Battery Inverter Breakers | 70 A, 3P | 5 | BATTERY | REQUIRED | 500 | 2500 | CAPEX | TRUE | Reduces if inverter count drops.
Protection | Main Breaker | 150 A, 3P | 1 | SHARED | REQUIRED | 1200 | 1200 | CAPEX | TRUE | AC bus main.
Protection | Surge Protection | Type 1 or 2 SPD (AC & DC) | 4 | SHARED | RECOMMENDED | 875 | 3500 | CAPEX | TRUE | Type 1 typically only required if exposed to direct lightning.
Grounding | Ground Conductor | #2 AWG Cu stranded | 350m | SHARED | REQUIRED | 7000 | 7000 | CAPEX | TRUE | Equipment grounding.
Grounding | Ground Rods | 5/8" x 8 ft Cu rods | 4-6 | SHARED | REQUIRED | 500 | 500 | CAPEX | TRUE | Site dependent. Verify against soil resistivity.
Grounding | Ground Bus | Copper ground bar | 1 | SHARED | REQUIRED | 600 | 600 | CAPEX | TRUE | Panel grounding.
Grounding | Labels & Signage | NEC/CEC compliant | All cabinets | SHARED | REQUIRED | 1200 | 1200 | CAPEX | TRUE | Non-negotiable for AHJ approval.
Controls | Monitoring System | SMA monitoring portal | 1 | SHARED | REQUIRED | 0 | 0 | CAPEX | TRUE | Bundled — no cost.
Controls | Energy Meter | Internal PV/BESS meter | 1 | SHARED | ELIMINATE | 2000 | 2000 | CAPEX | FALSE | Quick win. Confirm client doesn't want internal monitoring view.
Controls | Communication Cables | Ethernet / RS485 | 1000m | SHARED | REQUIRED | 2500 | 2500 | CAPEX | TRUE | Validate run length — could trim if not full 1000m.
Engineering | Basic SLD + Layout + Prelim BOM | PV design and integration included | - | SHARED | REQUIRED | 13000 | 13000 | CAPEX | TRUE | Foundational deliverable.
Engineering | Detailed Electrical Design | CEC compliance | - | SHARED | REQUIRED | 7500 | 7500 | CAPEX | TRUE | Required for permitting.
Engineering | Battery Integration & Control Design | - | - | BATTERY | REQUIRED | 5500 | 5500 | CAPEX | TRUE | Critical for grid-forming coordination.
Engineering | PEng Stamping | If required by AHJ | - | SHARED | ELIMINATE | 0 | 0 | CAPEX | FALSE | Cost TBD. Budget $2-5K placeholder.
Studies | Short Circuit Study | - | - | SHARED | REQUIRED | 3000 | 3000 | CAPEX | TRUE | Often bundled with Protection Study — see opportunity to combine.
Studies | Protection Study | - | - | SHARED | ELIMINATE | 7500 | 7500 | CAPEX | FALSE | If kept, bundle with SC Study for combined cost ~$8.5K vs $10.5K.
Studies | Arc Flash Study | - | - | SHARED | ELIMINATE | 8000 | 8000 | CAPEX | FALSE | Original BOM noted $5K min if needed.
Studies | Fire Suppression | Battery room fire suppression | - | BATTERY | ELIMINATE | 0 | 0 | CAPEX | FALSE | Cost TBD if required. Outdoor enclosure removes need entirely.
Studies | Ventilation Study & Upgrade | - | - | BATTERY | ELIMINATE | 0 | 0 | CAPEX | FALSE | Cost TBD if required. Outdoor enclosure removes need entirely.
Labour | Labour and Trenching | PV + BESS install | - | SHARED | REQUIRED | 77500 | 77500 | CAPEX | TRUE | Original range $55-100K. Used midpoint. Competitive bid could trim 10-15%.

## BOM Totals
Metric | Value
active_bom_total_cad | 330900
optimized_target_cad | 273300
line_items_included_total_cad | 288200
scope: BATTERY | 101700
scope: PV | 41500
scope: SHARED | 145000

## CAPEX line items
category | item | description | qty | scope | necessity | unit_cost | total_cost | capex_opex | included | notes | qty_num
Main Equipment | Battery Inverter | LuxPower GEN-HB-US 25KW (parallel cluster) | 3 | BATTERY | REQUIRED | 11666.67 | 35000 | CAPEX | TRUE | Grid-forming. Each Sunny Island ~$7K. Right-sizing could drop 1-2 units. right sized - LuxPower GEN-HB-US-25kW -qty 3, quote recieved | 3
Main Equipment | PV Modules | ~75 kW DC array (500W modules) 600V DC System | 150 | PV | REQUIRED | 110 | 16500 | CAPEX | TRUE | $200/module is reasonable. Tier-2 brands could save further but check warranty terms. | 150
Main Equipment | EMS Controller | SMA Data Manager / Microgrid Controller | 1 | SHARED | REQUIRED | 3500 | 3500 | CAPEX | TRUE | Recommended by SMA for multi-inverter clusters. | 1
PV DC Side | PV Wire | #10 AWG Cu PV Wire (USE-2) | As req'd | PV | REVIEW | 15000 | 15000 | CAPEX | TRUE | Verify takeoff. Likely overestimated by ~10x.
PV DC Side | Home Run | 4 AWG | 250 m | PV | REQUIRED | 5000 | 5000 | CAPEX | TRUE | Reasonable. Gauge optimization could yield small savings.
PV DC Side | Connectors | MC4 compatible | 310 | PV | REQUIRED | 4.84 | 1500 | CAPEX | TRUE | $5/connector — fair pricing. 310 = 150 modules x 2 + spares. | 310
PV DC Side | Cable Management | Conduit + tray + clips (underground rated) | As req'd | SHARED | REVIEW | 15000 | 15000 | CAPEX | TRUE | Underground rated drives cost. Mostly PV DC runs — could split scope.
Battery DC | DC Busbar | Copper busbar ≥1200 A | 2 | BATTERY | REQUIRED | 3750 | 7500 | CAPEX | TRUE | Standard for cluster of this size. | 2
Battery DC | Battery Rack Fuses | 250-300 A DC fuses | 8-12 | BATTERY | REVIEW | 2200 | 2200 | CAPEX | TRUE | If rack breakers (next row) are kept, fuses become redundant. Confirm with BMS spec.
Battery DC | Battery Rack Breaker | 250-300 A DC Breaker | 8-12 | BATTERY | REQUIRED | 11000 | 11000 | CAPEX | TRUE | If kept, eliminate fuses above for $2.2K savings.
Battery DC | Battery Disconnect | 1200 A DC disconnect | 1 | BATTERY | REQUIRED | 6000 | 6000 | CAPEX | TRUE | Critical safety device. | 1
Battery DC | Battery Cables | 4/0 AWG Cu (or parallel sets) | As req'd | BATTERY | REQUIRED | 22000 | 22000 | CAPEX | TRUE | Cu pricing is volatile. Confirm OEM-approved Al lugs.
Battery DC | BMS | Integrated BMS | 1 system | BATTERY | REQUIRED | 0 | 0 | CAPEX | TRUE | No cost — bundled.
AC Power | PV Feeder Cable | #4 AWG Cu | As req'd | PV | REQUIRED | 3000 | 3000 | CAPEX | TRUE | CORE1 to panel feeder.
AC Power | Battery Inverter Cable | 4/0 AWG Cu | As req'd | BATTERY | REVIEW | 10000 | 10000 | CAPEX | TRUE | Use mid-range $5K based on typical Sunny Island runs.
AC Power | Main Bus Cable | 3/0 AWG Cu | As req'd | SHARED | REQUIRED | 9000 | 9000 | CAPEX | TRUE | Standard sizing.
Protection | PV Breaker | 80 A, 3P | 1 | PV | REQUIRED | 500 | 500 | CAPEX | TRUE | CORE1 output protection. | 1
Protection | Battery Inverter Breakers | 70 A, 3P | 5 | BATTERY | REQUIRED | 500 | 2500 | CAPEX | TRUE | Reduces if inverter count drops. | 5
Protection | Main Breaker | 150 A, 3P | 1 | SHARED | REQUIRED | 1200 | 1200 | CAPEX | TRUE | AC bus main. | 1
Protection | Surge Protection | Type 1 or 2 SPD (AC & DC) | 4 | SHARED | RECOMMENDED | 875 | 3500 | CAPEX | TRUE | Type 1 typically only required if exposed to direct lightning. | 4
Grounding | Ground Conductor | #2 AWG Cu stranded | 350m | SHARED | REQUIRED | 7000 | 7000 | CAPEX | TRUE | Equipment grounding.
Grounding | Ground Rods | 5/8" x 8 ft Cu rods | 4-6 | SHARED | REQUIRED | 500 | 500 | CAPEX | TRUE | Site dependent. Verify against soil resistivity.
Grounding | Ground Bus | Copper ground bar | 1 | SHARED | REQUIRED | 600 | 600 | CAPEX | TRUE | Panel grounding. | 1
Grounding | Labels & Signage | NEC/CEC compliant | All cabinets | SHARED | REQUIRED | 1200 | 1200 | CAPEX | TRUE | Non-negotiable for AHJ approval.
Controls | Monitoring System | SMA monitoring portal | 1 | SHARED | REQUIRED | 0 | 0 | CAPEX | TRUE | Bundled — no cost. | 1
Controls | Communication Cables | Ethernet / RS485 | 1000m | SHARED | REQUIRED | 2500 | 2500 | CAPEX | TRUE | Validate run length — could trim if not full 1000m.
Engineering | Basic SLD + Layout + Prelim BOM | PV design and integration included | - | SHARED | REQUIRED | 13000 | 13000 | CAPEX | TRUE | Foundational deliverable.
Engineering | Detailed Electrical Design | CEC compliance | - | SHARED | REQUIRED | 7500 | 7500 | CAPEX | TRUE | Required for permitting.
Engineering | Battery Integration & Control Design | - | - | BATTERY | REQUIRED | 5500 | 5500 | CAPEX | TRUE | Critical for grid-forming coordination.
Studies | Short Circuit Study | - | - | SHARED | REQUIRED | 3000 | 3000 | CAPEX | TRUE | Often bundled with Protection Study — see opportunity to combine.
Labour | Labour and Trenching | PV + BESS install | - | SHARED | REQUIRED | 77500 | 77500 | CAPEX | TRUE | Original range $55-100K. Used midpoint. Competitive bid could trim 10-15%.

## Monthly Results
month | bill_without | bill_with | energy_without | energy_with | demand_without | demand_with | nem_without | nem_with | peak_without_kw | peak_with_kw
1 | 2700.3135 | 2195.1781 | 2700.3135 | 2195.1781 | 0 | 0 | 0 | -2.0698e-13 | 61.44 | 126.66
2 | 2301.3398 | 1900.0026 | 2304.8663 | 1903.5291 | 0 | 0 | -3.5265 | -3.5265 | 67.08 | 109.68
3 | 3071.2346 | 2584.9168 | 3074.226 | 2585.266 | 0 | 0 | -2.9915 | -0.34914 | 109.08 | 163.6873
4 | 995.1145 | 766.3439 | 1487.567 | 1253.7719 | 0 | 0 | -492.4525 | -487.428 | 72.12 | 130.68
5 | -969.3545 | -970.9223 | 205.1964 | 203.6286 | 0 | 0 | -1174.5509 | -1174.5509 | 28.32 | 45.6387
6 | -1084.6866 | -1085.0153 | 177.3994 | 177.0707 | 0 | 0 | -1262.086 | -1262.086 | 24.12 | 24.12
7 | -1154.3498 | -1155.0817 | 153.8128 | 153.0809 | 0 | 0 | -1308.1626 | -1308.1626 | 17.7 | 17.7
8 | -909.9728 | -911.7094 | 154.6263 | 152.8896 | 0 | 0 | -1064.5991 | -1064.5991 | 20.16 | 20.16
9 | -470.4726 | -474.2348 | 153.646 | 149.8838 | 0 | 0 | -624.1187 | -624.1187 | 16.86 | 48.6404
10 | -120.1367 | -136.5514 | 173.9818 | 153.4229 | 0 | 0 | -294.1186 | -289.9743 | 18.36 | 80.22
11 | 4028.6813 | 3422.355 | 4028.6813 | 3422.355 | 0 | 0 | 0 | -2.3031e-13 | 114.9 | 168.9
12 | 2935.4304 | 2367.232 | 2935.6339 | 2367.232 | 0 | 0 | -0.20349 | -2.7993e-13 | 66.8636 | 117.84

## Cash Flow
year | pv_savings_cad | battery_savings_cad | gross_savings_cad | opex_cad | replacement_cad | net_cash_flow_cad | discounted_cash_flow_cad | cumulative_net_cad | cumulative_discounted_cad
1 | 10966.19 | 2820.63 | 13786.81 | 2000 | 0 | 11786.81 | 10913.72 | -352203.19 | -353076.28
2 | 11238.7 | 2847.14 | 14085.84 | 2040 | 0 | 12045.84 | 10327.37 | -340157.35 | -342748.91
3 | 11517.69 | 2872.71 | 14390.4 | 2080.8 | 0 | 12309.6 | 9771.75 | -327847.75 | -332977.16
4 | 11803.3 | 2897.25 | 14700.55 | 2122.42 | 0 | 12578.13 | 9245.3 | -315269.62 | -323731.86
5 | 12095.69 | 2920.67 | 15016.36 | 2164.86 | 0 | 12851.5 | 8746.51 | -302418.12 | -314985.35
6 | 12395 | 2942.89 | 15337.89 | 2208.16 | 0 | 13129.73 | 8273.96 | -289288.39 | -306711.39
7 | 12701.38 | 2963.82 | 15665.19 | 2252.32 | 0 | 13412.87 | 7826.28 | -275875.52 | -298885.11
8 | 13014.98 | 2983.35 | 15998.34 | 2297.37 | 0 | 13700.96 | 7402.2 | -262174.56 | -291482.91
9 | 13335.97 | 3001.39 | 16337.37 | 2343.32 | 0 | 13994.05 | 7000.51 | -248180.51 | -284482.4
10 | 13664.51 | 3017.83 | 16682.34 | 2390.19 | 0 | 14292.15 | 6620.03 | -233888.36 | -277862.37
11 | 14000.76 | 3032.55 | 17033.31 | 2437.99 | 0 | 14595.32 | 6259.68 | -219293.04 | -271602.69
12 | 14344.88 | 3045.44 | 17390.32 | 2486.75 | 0 | 14903.57 | 5918.41 | -204389.47 | -265684.28
13 | 14697.05 | 3056.37 | 17753.42 | 2536.48 | 0 | 15216.94 | 5595.24 | -189172.53 | -260089.04
14 | 15057.44 | 3065.22 | 18122.66 | 2587.21 | 0 | 15535.45 | 5289.21 | -173637.08 | -254799.83
15 | 15426.23 | 3071.85 | 18498.07 | 2638.96 | 0 | 15859.12 | 4999.45 | -157777.96 | -249800.38
16 | 15803.59 | 3076.11 | 18879.7 | 2691.74 | 0 | 16187.97 | 4725.11 | -141589.99 | -245075.27
17 | 16189.71 | 3077.87 | 19267.58 | 2745.57 | 0 | 16522.01 | 4465.39 | -125067.98 | -240609.88
18 | 16584.78 | 3076.96 | 19661.74 | 2800.48 | 0 | 16861.26 | 4219.51 | -108206.72 | -236390.37
19 | 16988.97 | 3073.23 | 20062.21 | 2856.49 | 0 | 17205.71 | 3986.77 | -91001.01 | -232403.6
20 | 17402.5 | 3066.51 | 20469.01 | 2913.62 | 0 | 17555.38 | 3766.48 | -73445.63 | -228637.12

## Sens - Battery Size
battery_kwh | battery_kw | battery_savings_cad | year1_savings_cad | npv_cad | irr_pct | simple_payback_years
325 | 37.5 | 2130 | 13096 | -235754 | -2.36
488 | 56.31 | 2653 | 13619 | -230368 | -2.04
650 | 75 | 2821 | 13787 | -228637 | -1.94
812 | 93.69 | 2869 | 13835 | -228140 | -1.91
975 | 112.5 | 2889 | 13855 | -227930 | -1.9
1300 | 150 | 2895 | 13862 | -227867 | -1.89

## Sens - CAPEX
capex_multiplier | total_capex_cad | npv_cad | irr_pct | simple_payback_years
0.8 | 291192 | -155839 | -0.02
0.9 | 327591 | -192238 | -1.05
1 | 363990 | -228637 | -1.94
1.1 | 400389 | -265036 | -2.72
1.2 | 436788 | -301435 | -3.41

## Sens - Electricity Rate
rate_multiplier | year1_savings_cad | npv_cad | irr_pct | simple_payback_years
0.8 | 11029 | -260249 | -4.06
0.9 | 12408 | -244443 | -2.95
1 | 13787 | -228637 | -1.94
1.1 | 15165 | -212831 | -1.01
1.2 | 16544 | -197025 | -0.14
1.5 | 20680 | -149607 | 2.19 | 16.45

## Sens - Degradation
battery_degradation_rate | npv_cad | irr_pct | simple_payback_years
0 | -223145 | -1.47
0.01 | -225891 | -1.7
0.02 | -228637 | -1.94
0.03 | -231383 | -2.18
0.05 | -236875 | -2.7

## Sens - Discount Rate
discount_rate | npv_cad | irr_pct | simple_payback_years
0.04 | -171861 | -1.94
0.06 | -203917 | -1.94
0.08 | -228637 | -1.94
0.1 | -247962 | -1.94
0.12 | -263273 | -1.94

## Hourly Dispatch
datetime | load_kw | pv_kw | charge_kw | discharge_kw | soc_kwh | net_with_kw | net_without_kw
2025-01-01 00:00:00 | 22.68 | 0 | 0 | 0 | 325 | 22.68 | 22.68
2025-01-01 01:00:00 | 22.14 | 0 | 0 | 0 | 325 | 22.14 | 22.14
2025-01-01 02:00:00 | 24.48 | 0 | 0 | 0 | 325 | 24.48 | 24.48
2025-01-01 03:00:00 | 22.62 | 0 | 0 | 0 | 325 | 22.62 | 22.62
2025-01-01 04:00:00 | 22.38 | 0 | 0 | 0 | 325 | 22.38 | 22.38
2025-01-01 05:00:00 | 22.56 | 0 | 0 | 0 | 325 | 22.56 | 22.56
2025-01-01 06:00:00 | 22.92 | 0 | 0 | 0 | 325 | 22.92 | 22.92
2025-01-01 07:00:00 | 23.82 | 0 | 0 | 0 | 325 | 23.82 | 23.82
2025-01-01 08:00:00 | 24.9 | 2.7904 | 0 | 0 | 325 | 22.1096 | 22.1096
2025-01-01 09:00:00 | 23.88 | 5.3836 | 0 | 0 | 325 | 18.4964 | 18.4964
2025-01-01 10:00:00 | 22.68 | 7.2174 | 0 | 0 | 325 | 15.4626 | 15.4626
2025-01-01 11:00:00 | 22.08 | 8.1666 | 0 | 0 | 325 | 13.9134 | 13.9134
2025-01-01 12:00:00 | 21.6 | 8.1666 | 0 | 0 | 325 | 13.4334 | 13.4334
2025-01-01 13:00:00 | 22.68 | 7.2174 | 0 | 0 | 325 | 15.4626 | 15.4626
2025-01-01 14:00:00 | 21.9 | 5.3836 | 0 | 0 | 325 | 16.5164 | 16.5164
2025-01-01 15:00:00 | 29.7 | 2.7904 | 0 | 0 | 325 | 26.9096 | 26.9096
2025-01-01 16:00:00 | 31.38 | 0 | 0 | 0 | 325 | 31.38 | 31.38
2025-01-01 17:00:00 | 31.38 | 0 | 0 | 0 | 325 | 31.38 | 31.38
2025-01-01 18:00:00 | 31.32 | 0 | 0 | 0 | 325 | 31.32 | 31.32
2025-01-01 19:00:00 | 35.76 | 0 | 0 | 0 | 325 | 35.76 | 35.76
2025-01-01 20:00:00 | 32.04 | 0 | 0 | 0 | 325 | 32.04 | 32.04
2025-01-01 21:00:00 | 31.08 | 0 | 0 | 0 | 325 | 31.08 | 31.08
2025-01-01 22:00:00 | 34.2 | 0 | 0 | 0 | 325 | 34.2 | 34.2
2025-01-01 23:00:00 | 24.24 | 0 | 0 | 0 | 325 | 24.24 | 24.24
2025-01-02 00:00:00 | 22.62 | 0 | 0 | 0 | 325 | 22.62 | 22.62
2025-01-02 01:00:00 | 23.88 | 0 | 0 | 0 | 325 | 23.88 | 23.88
2025-01-02 02:00:00 | 22.26 | 0 | 0 | 0 | 325 | 22.26 | 22.26
2025-01-02 03:00:00 | 23.4 | 0 | 0 | 0 | 325 | 23.4 | 23.4
2025-01-02 04:00:00 | 22.2 | 0 | 0 | 0 | 325 | 22.2 | 22.2
2025-01-02 05:00:00 | 22.32 | 0 | 63.8802 | 0 | 381.2146 | 86.2002 | 22.32
2025-01-02 06:00:00 | 23.34 | 0 | 0 | 0 | 381.2146 | 23.34 | 23.34
2025-01-02 07:00:00 | 23.04 | 0 | 0 | 23.04 | 358.1746 | 0 | 23.04
2025-01-02 08:00:00 | 22.02 | 2.8147 | 0 | 19.2053 | 338.9693 | -4.6185e-14 | 19.2053
2025-01-02 09:00:00 | 22.38 | 5.4095 | 0 | 16.9705 | 321.9988 | 7.1054e-15 | 16.9705
2025-01-02 10:00:00 | 22.62 | 7.2444 | 0 | 15.3756 | 306.6232 | 4.2633e-14 | 15.3756
2025-01-02 11:00:00 | 22.56 | 8.1941 | 0 | 14.3659 | 292.2573 | -1.5987e-14 | 14.3659
2025-01-02 12:00:00 | 22.02 | 8.1941 | 0 | 13.8259 | 278.4314 | -1.4211e-14 | 13.8259
2025-01-02 13:00:00 | 23.34 | 7.2444 | 0 | 16.0956 | 262.3358 | 4.2633e-14 | 16.0956
2025-01-02 14:00:00 | 22.02 | 5.4095 | 0 | 16.6105 | 245.7253 | 7.1054e-15 | 16.6105
2025-01-02 15:00:00 | 31.5 | 2.8147 | 0 | 28.6853 | 217.04 | -4.6185e-14 | 28.6853
2025-01-02 16:00:00 | 50.4 | 0 | 0 | 50.4 | 166.64 | 0 | 50.4
2025-01-02 17:00:00 | 53.64 | 0 | 0 | 53.64 | 113 | 0 | 53.64
2025-01-02 18:00:00 | 48 | 0 | 0 | 48 | 65 | 0 | 48
2025-01-02 19:00:00 | 45.78 | 0 | 68.9631 | 0 | 125.6875 | 114.7431 | 45.78
2025-01-02 20:00:00 | 35.64 | 0 | 0 | 0 | 125.6875 | 35.64 | 35.64
2025-01-02 21:00:00 | 25.92 | 0 | 0 | 0 | 125.6875 | 25.92 | 25.92
2025-01-02 22:00:00 | 23.64 | 0 | 0 | 0 | 125.6875 | 23.64 | 23.64
2025-01-02 23:00:00 | 23.1 | 0 | 0 | 0 | 125.6875 | 23.1 | 23.1
2025-01-03 00:00:00 | 22.8 | 0 | 0 | 0 | 125.6875 | 22.8 | 22.8
2025-01-03 01:00:00 | 22.32 | 0 | 0 | 0 | 125.6875 | 22.32 | 22.32
2025-01-03 02:00:00 | 22.56 | 0 | 75 | 0 | 191.6875 | 97.56 | 22.56
2025-01-03 03:00:00 | 22.26 | 0 | 75 | 0 | 257.6875 | 97.26 | 22.26
2025-01-03 04:00:00 | 22.56 | 0 | 75 | 0 | 323.6875 | 97.56 | 22.56
2025-01-03 05:00:00 | 22.74 | 0 | 75 | 0 | 389.6875 | 97.74 | 22.74
2025-01-03 06:00:00 | 22.74 | 0 | 75 | 0 | 455.6875 | 97.74 | 22.74
2025-01-03 07:00:00 | 22.14 | 0 | 0 | 22.14 | 433.5475 | 0 | 22.14
2025-01-03 08:00:00 | 22.26 | 2.8411 | 0 | 19.4189 | 414.1286 | 3.5527e-14 | 19.4189
2025-01-03 09:00:00 | 22.86 | 5.4376 | 0 | 17.4224 | 396.7062 | 2.1316e-14 | 17.4224
2025-01-03 10:00:00 | 22.38 | 7.2736 | 0 | 15.1064 | 381.5998 | -1.7764e-14 | 15.1064
2025-01-03 11:00:00 | 30.36 | 8.224 | 0 | 22.136 | 359.4638 | 7.1054e-15 | 22.136
2025-01-03 12:00:00 | 45.9 | 8.224 | 0 | 37.676 | 321.7878 | 7.1054e-15 | 37.676
2025-01-03 13:00:00 | 48.6 | 7.2736 | 0 | 41.3264 | 280.4614 | -1.4211e-14 | 41.3264
2025-01-03 14:00:00 | 46.98 | 5.4376 | 0 | 41.5424 | 238.9189 | 1.4211e-14 | 41.5424
2025-01-03 15:00:00 | 50.04 | 2.8411 | 0 | 47.1989 | 191.72 | 3.5527e-14 | 47.1989
2025-01-03 16:00:00 | 41.4 | 0 | 0 | 41.4 | 150.32 | 0 | 41.4
2025-01-03 17:00:00 | 45.6 | 0 | 0 | 45.6 | 104.72 | 0 | 45.6
2025-01-03 18:00:00 | 39.72 | 0 | 0 | 39.72 | 65 | 0 | 39.72
2025-01-03 19:00:00 | 39.72 | 0 | 0 | 0 | 65 | 39.72 | 39.72
2025-01-03 20:00:00 | 38.16 | 0 | 0 | 0 | 65 | 38.16 | 38.16
2025-01-03 21:00:00 | 36.42 | 0 | 0 | 0 | 65 | 36.42 | 36.42
2025-01-03 22:00:00 | 37.14 | 0 | 0 | 0 | 65 | 37.14 | 37.14
2025-01-03 23:00:00 | 36.84 | 0 | 0 | 0 | 65 | 36.84 | 36.84
2025-01-04 00:00:00 | 36.72 | 0 | 0 | 0 | 65 | 36.72 | 36.72
2025-01-04 01:00:00 | 35.4 | 0 | 0 | 0 | 65 | 35.4 | 35.4
2025-01-04 02:00:00 | 23.04 | 0 | 0 | 0 | 65 | 23.04 | 23.04
2025-01-04 03:00:00 | 38.64 | 0 | 0 | 0 | 65 | 38.64 | 38.64
2025-01-04 04:00:00 | 39.18 | 0 | 0 | 0 | 65 | 39.18 | 39.18
2025-01-04 05:00:00 | 39.12 | 0 | 0 | 0 | 65 | 39.12 | 39.12
2025-01-04 06:00:00 | 39.42 | 0 | 0 | 0 | 65 | 39.42 | 39.42
2025-01-04 07:00:00 | 30.24 | 0 | 0 | 0 | 65 | 30.24 | 30.24
2025-01-04 08:00:00 | 25.86 | 2.8695 | 0 | 0 | 65 | 22.9905 | 22.9905
2025-01-04 09:00:00 | 35.76 | 5.4678 | 0 | 0 | 65 | 30.2922 | 30.2922
2025-01-04 10:00:00 | 41.16 | 7.3051 | 0 | 0 | 65 | 33.8549 | 33.8549
2025-01-04 11:00:00 | 52.14 | 8.2561 | 0 | 0 | 65 | 43.8839 | 43.8839
2025-01-04 12:00:00 | 47.64 | 8.2561 | 0 | 0 | 65 | 39.3839 | 39.3839
2025-01-04 13:00:00 | 42.9 | 7.3051 | 0 | 0 | 65 | 35.5949 | 35.5949
2025-01-04 14:00:00 | 41.22 | 5.4678 | 0 | 0 | 65 | 35.7522 | 35.7522
2025-01-04 15:00:00 | 39.18 | 2.8695 | 0 | 0 | 65 | 36.3105 | 36.3105
2025-01-04 16:00:00 | 31.44 | 0 | 0 | 0 | 65 | 31.44 | 31.44
2025-01-04 17:00:00 | 23.52 | 0 | 0 | 0 | 65 | 23.52 | 23.52
2025-01-04 18:00:00 | 22.2 | 0 | 0 | 0 | 65 | 22.2 | 22.2
2025-01-04 19:00:00 | 22.5 | 0 | 0 | 0 | 65 | 22.5 | 22.5
2025-01-04 20:00:00 | 22.5 | 0 | 0 | 0 | 65 | 22.5 | 22.5
2025-01-04 21:00:00 | 22.26 | 0 | 0 | 0 | 65 | 22.26 | 22.26
2025-01-04 22:00:00 | 29.58 | 0 | 0 | 0 | 65 | 29.58 | 29.58
2025-01-04 23:00:00 | 38.82 | 0 | 0 | 0 | 65 | 38.82 | 38.82
2025-01-05 00:00:00 | 38.58 | 0 | 0 | 0 | 65 | 38.58 | 38.58
2025-01-05 01:00:00 | 28.44 | 0 | 0 | 0 | 65 | 28.44 | 28.44
2025-01-05 02:00:00 | 22.2 | 0 | 0 | 0 | 65 | 22.2 | 22.2
2025-01-05 03:00:00 | 23.4 | 0 | 0 | 0 | 65 | 23.4 | 23.4
2025-01-05 04:00:00 | 22.26 | 0 | 0 | 0 | 65 | 22.26 | 22.26
2025-01-05 05:00:00 | 22.14 | 0 | 0 | 0 | 65 | 22.14 | 22.14
2025-01-05 06:00:00 | 22.38 | 0 | 0 | 0 | 65 | 22.38 | 22.38
2025-01-05 07:00:00 | 22.02 | 0 | 0 | 0 | 65 | 22.02 | 22.02
2025-01-05 08:00:00 | 35.16 | 2.8999 | 0 | 0 | 65 | 32.2601 | 32.2601
2025-01-05 09:00:00 | 50.22 | 5.5001 | 0 | 0 | 65 | 44.7199 | 44.7199
2025-01-05 10:00:00 | 49.2 | 7.3388 | 0 | 0 | 65 | 41.8612 | 41.8612
2025-01-05 11:00:00 | 46.98 | 8.2905 | 0 | 0 | 65 | 38.6895 | 38.6895
2025-01-05 12:00:00 | 45.96 | 8.2905 | 0 | 0 | 65 | 37.6695 | 37.6695
2025-01-05 13:00:00 | 46.92 | 7.3388 | 0 | 0 | 65 | 39.5812 | 39.5812
2025-01-05 14:00:00 | 41.94 | 5.5001 | 0 | 0 | 65 | 36.4399 | 36.4399
2025-01-05 15:00:00 | 40.08 | 2.8999 | 65.2075 | 0 | 122.3826 | 102.3877 | 37.1801
2025-01-05 16:00:00 | 23.34 | 0 | 0 | 0 | 122.3826 | 23.34 | 23.34
2025-01-05 17:00:00 | 23.28 | 0 | 0 | 0 | 122.3826 | 23.28 | 23.28
2025-01-05 18:00:00 | 22.44 | 0 | 0 | 0 | 122.3826 | 22.44 | 22.44
2025-01-05 19:00:00 | 32.34 | 0 | 0 | 0 | 122.3826 | 32.34 | 32.34
2025-01-05 20:00:00 | 38.82 | 0 | 0 | 0 | 122.3826 | 38.82 | 38.82
2025-01-05 21:00:00 | 44.64 | 0 | 0 | 0 | 122.3826 | 44.64 | 44.64
2025-01-05 22:00:00 | 42.72 | 0 | 0 | 0 | 122.3826 | 42.72 | 42.72
2025-01-05 23:00:00 | 41.04 | 0 | 0 | 0 | 122.3826 | 41.04 | 41.04
2025-01-06 00:00:00 | 38.58 | 0 | 0 | 0 | 122.3826 | 38.58 | 38.58
2025-01-06 01:00:00 | 29.76 | 0 | 75 | 0 | 188.3826 | 104.76 | 29.76
2025-01-06 02:00:00 | 21.66 | 0 | 75 | 0 | 254.3826 | 96.66 | 21.66
2025-01-06 03:00:00 | 22.02 | 0 | 75 | 0 | 320.3826 | 97.02 | 22.02
2025-01-06 04:00:00 | 22.8 | 0 | 75 | 0 | 386.3826 | 97.8 | 22.8
2025-01-06 05:00:00 | 21.9 | 0 | 75 | 0 | 452.3826 | 96.9 | 21.9
2025-01-06 06:00:00 | 31.92 | 0 | 75 | 0 | 518.3826 | 106.92 | 31.92
2025-01-06 07:00:00 | 38.58 | 0 | 0 | 38.58 | 479.8026 | 0 | 38.58
2025-01-06 08:00:00 | 38.76 | 2.9323 | 0 | 35.8277 | 443.9749 | 2.1316e-14 | 35.8277
2025-01-06 09:00:00 | 49.26 | 5.5346 | 0 | 43.7254 | 400.2495 | -3.5527e-14 | 43.7254
2025-01-06 10:00:00 | 46.86 | 7.3747 | 0 | 39.4853 | 360.7641 | 2.1316e-14 | 39.4853
2025-01-06 11:00:00 | 46.74 | 8.3272 | 0 | 38.4128 | 322.3513 | -3.5527e-14 | 38.4128
2025-01-06 12:00:00 | 45.9 | 8.3272 | 0 | 37.5728 | 284.7785 | -3.5527e-14 | 37.5728
2025-01-06 13:00:00 | 34.8 | 7.3747 | 0 | 27.4253 | 257.3531 | 1.7764e-14 | 27.4253
2025-01-06 14:00:00 | 28.74 | 5.5346 | 0 | 23.2054 | 234.1477 | -3.5527e-14 | 23.2054
2025-01-06 15:00:00 | 41.28 | 2.9323 | 0 | 38.3477 | 195.8 | 2.1316e-14 | 38.3477
2025-01-06 16:00:00 | 45.66 | 0 | 0 | 45.66 | 150.14 | 0 | 45.66
2025-01-06 17:00:00 | 43.56 | 0 | 0 | 43.56 | 106.58 | 0 | 43.56
2025-01-06 18:00:00 | 41.58 | 0 | 0 | 41.58 | 65 | 0 | 41.58
2025-01-06 19:00:00 | 39 | 0 | 75 | 0 | 131 | 114 | 39
2025-01-06 20:00:00 | 44.34 | 0 | 51.985 | 0 | 176.7468 | 96.325 | 44.34
2025-01-06 21:00:00 | 47.7 | 0 | 0 | 0 | 176.7468 | 47.7 | 47.7
2025-01-06 22:00:00 | 51.6 | 0 | 0 | 0 | 176.7468 | 51.6 | 51.6
2025-01-06 23:00:00 | 34.08 | 0 | 0 | 0 | 176.7468 | 34.08 | 34.08
2025-01-07 00:00:00 | 24.66 | 0 | 0 | 0 | 176.7468 | 24.66 | 24.66
2025-01-07 01:00:00 | 22.14 | 0 | 75 | 0 | 242.7468 | 97.14 | 22.14
2025-01-07 02:00:00 | 27.36 | 0 | 75 | 0 | 308.7468 | 102.36 | 27.36
2025-01-07 03:00:00 | 36.24 | 0 | 75 | 0 | 374.7468 | 111.24 | 36.24
2025-01-07 04:00:00 | 29.16 | 0 | 75 | 0 | 440.7468 | 104.16 | 29.16
2025-01-07 05:00:00 | 37.92 | 0 | 75 | 0 | 506.7468 | 112.92 | 37.92
2025-01-07 06:00:00 | 38.28 | 0 | 75 | 0 | 572.7468 | 113.28 | 38.28
2025-01-07 07:00:00 | 48.66 | 0 | 0 | 48.66 | 524.0868 | 0 | 48.66
2025-01-07 08:00:00 | 61.2 | 2.9667 | 0 | 58.2333 | 465.8534 | -1.4211e-14 | 58.2333
2025-01-07 09:00:00 | 58.38 | 5.5711 | 0 | 52.8089 | 413.0446 | -4.2633e-14 | 52.8089
2025-01-07 10:00:00 | 49.26 | 7.4128 | 0 | 41.8472 | 371.1973 | 1.4211e-14 | 41.8472
2025-01-07 11:00:00 | 44.88 | 8.366 | 0 | 36.514 | 334.6834 | 3.5527e-14 | 36.514
2025-01-07 12:00:00 | 40.38 | 8.366 | 0 | 32.014 | 302.6694 | 3.5527e-14 | 32.014
2025-01-07 13:00:00 | 38.1 | 7.4128 | 0 | 30.6872 | 271.9822 | 1.7764e-14 | 30.6872
2025-01-07 14:00:00 | 38.16 | 5.5711 | 0 | 32.5889 | 239.3933 | 4.9738e-14 | 32.5889
2025-01-07 15:00:00 | 38.04 | 2.9667 | 0 | 35.0733 | 204.32 | -2.1316e-14 | 35.0733
2025-01-07 16:00:00 | 45.96 | 0 | 0 | 45.96 | 158.36 | 0 | 45.96
2025-01-07 17:00:00 | 48 | 0 | 0 | 48 | 110.36 | 0 | 48
2025-01-07 18:00:00 | 45.36 | 0 | 0 | 45.36 | 65 | 0 | 45.36
2025-01-07 19:00:00 | 45.96 | 0 | 75 | 0 | 131 | 120.96 | 45.96
2025-01-07 20:00:00 | 50.34 | 0 | 16.0386 | 0 | 145.114 | 66.3786 | 50.34
2025-01-07 21:00:00 | 47.88 | 0 | 0 | 0 | 145.114 | 47.88 | 47.88
2025-01-07 22:00:00 | 42.36 | 0 | 0 | 0 | 145.114 | 42.36 | 42.36
2025-01-07 23:00:00 | 41.1 | 0 | 0 | 0 | 145.114 | 41.1 | 41.1
2025-01-08 00:00:00 | 38.46 | 0 | 0 | 0 | 145.114 | 38.46 | 38.46
2025-01-08 01:00:00 | 25.68 | 0 | 75 | 0 | 211.114 | 100.68 | 25.68
2025-01-08 02:00:00 | 22.14 | 0 | 75 | 0 | 277.114 | 97.14 | 22.14
2025-01-08 03:00:00 | 22.56 | 0 | 75 | 0 | 343.114 | 97.56 | 22.56
2025-01-08 04:00:00 | 36.84 | 0 | 75 | 0 | 409.114 | 111.84 | 36.84
2025-01-08 05:00:00 | 37.68 | 0 | 75 | 0 | 475.114 | 112.68 | 37.68
2025-01-08 06:00:00 | 38.04 | 0 | 75 | 0 | 541.114 | 113.04 | 38.04
2025-01-08 07:00:00 | 37.74 | 0 | 0 | 37.74 | 503.374 | 0 | 37.74
2025-01-08 08:00:00 | 37.62 | 3.0031 | 0 | 34.6169 | 468.7571 | 2.8422e-14 | 34.6169
2025-01-08 09:00:00 | 49.56 | 5.6098 | 0 | 43.9502 | 424.8068 | -4.2633e-14 | 43.9502
2025-01-08 10:00:00 | 46.74 | 7.453 | 0 | 39.287 | 385.5199 | -2.1316e-14 | 39.287
2025-01-08 11:00:00 | 45.66 | 8.4071 | 0 | 37.2529 | 348.267 | 1.4211e-14 | 37.2529
2025-01-08 12:00:00 | 43.5 | 8.4071 | 0 | 35.0929 | 313.1741 | 2.1316e-14 | 35.0929
2025-01-08 13:00:00 | 41.58 | 7.453 | 0 | 34.127 | 279.0471 | -2.1316e-14 | 34.127
2025-01-08 14:00:00 | 38.46 | 5.6098 | 0 | 32.8502 | 246.1969 | -4.2633e-14 | 32.8502
2025-01-08 15:00:00 | 38.94 | 3.0031 | 0 | 35.9369 | 210.26 | 2.8422e-14 | 35.9369
2025-01-08 16:00:00 | 52.26 | 0 | 0 | 52.26 | 158 | 0 | 52.26
2025-01-08 17:00:00 | 48.12 | 0 | 0 | 48.12 | 109.88 | 0 | 48.12
2025-01-08 18:00:00 | 44.88 | 0 | 0 | 44.88 | 65 | 0 | 44.88
2025-01-08 19:00:00 | 43.86 | 0 | 75 | 0 | 131 | 118.86 | 43.86
2025-01-08 20:00:00 | 41.4 | 0 | 36.5278 | 0 | 163.1444 | 77.9278 | 41.4
2025-01-08 21:00:00 | 37.92 | 0 | 0 | 0 | 163.1444 | 37.92 | 37.92
2025-01-08 22:00:00 | 39 | 0 | 0 | 0 | 163.1444 | 39 | 39
2025-01-08 23:00:00 | 38.52 | 0 | 0 | 0 | 163.1444 | 38.52 | 38.52
2025-01-09 00:00:00 | 37.8 | 0 | 0 | 0 | 163.1444 | 37.8 | 37.8
2025-01-09 01:00:00 | 38.58 | 0 | 75 | 0 | 229.1444 | 113.58 | 38.58
2025-01-09 02:00:00 | 38.7 | 0 | 75 | 0 | 295.1444 | 113.7 | 38.7
2025-01-09 03:00:00 | 38.04 | 0 | 75 | 0 | 361.1444 | 113.04 | 38.04
2025-01-09 04:00:00 | 38.46 | 0 | 75 | 0 | 427.1444 | 113.46 | 38.46
2025-01-09 05:00:00 | 38.82 | 0 | 75 | 0 | 493.1444 | 113.82 | 38.82
2025-01-09 06:00:00 | 38.58 | 0 | 75 | 0 | 559.1444 | 113.58 | 38.58
2025-01-09 07:00:00 | 38.04 | 0 | 0 | 38.04 | 521.1044 | 0 | 38.04
2025-01-09 08:00:00 | 38.4 | 3.0414 | 0 | 35.3586 | 485.7458 | -2.1316e-14 | 35.3586
2025-01-09 09:00:00 | 38.52 | 5.6505 | 0 | 32.8695 | 452.8764 | -1.4211e-14 | 32.8695
2025-01-09 10:00:00 | 38.22 | 7.4954 | 0 | 30.7246 | 422.1518 | -1.4211e-14 | 30.7246
2025-01-09 11:00:00 | 38.16 | 8.4504 | 0 | 29.7096 | 392.4422 | -1.0658e-14 | 29.7096
2025-01-09 12:00:00 | 38.46 | 8.4504 | 0 | 30.0096 | 362.4326 | -3.5527e-15 | 30.0096
2025-01-09 13:00:00 | 38.7 | 7.4954 | 0 | 31.2046 | 331.2281 | -1.0658e-14 | 31.2046
2025-01-09 14:00:00 | 45.9 | 5.6505 | 0 | 40.2495 | 290.9786 | -1.4211e-14 | 40.2495
2025-01-09 15:00:00 | 51.3 | 3.0414 | 0 | 48.2586 | 242.72 | 7.816e-14 | 48.2586
2025-01-09 16:00:00 | 55.08 | 0 | 0 | 55.08 | 187.64 | 0 | 55.08
2025-01-09 17:00:00 | 61.44 | 0 | 0 | 61.44 | 126.2 | 0 | 61.44
2025-01-09 18:00:00 | 61.2 | 0 | 0 | 61.2 | 65 | 0 | 61.2
2025-01-09 19:00:00 | 55.92 | 0 | 70.74 | 0 | 127.2512 | 126.66 | 55.92
2025-01-09 20:00:00 | 55.38 | 0 | 36.0307 | 0 | 158.9582 | 91.4107 | 55.38
2025-01-09 21:00:00 | 55.14 | 0 | 0 | 0 | 158.9582 | 55.14 | 55.14
2025-01-09 22:00:00 | 53.22 | 0 | 0 | 0 | 158.9582 | 53.22 | 53.22
2025-01-09 23:00:00 | 53.1 | 0 | 0 | 0 | 158.9582 | 53.1 | 53.1
2025-01-10 00:00:00 | 49.2 | 0 | 0 | 0 | 158.9582 | 49.2 | 49.2
2025-01-10 01:00:00 | 38.46 | 0 | 75 | 0 | 224.9582 | 113.46 | 38.46
2025-01-10 02:00:00 | 39.36 | 0 | 75 | 0 | 290.9582 | 114.36 | 39.36
2025-01-10 03:00:00 | 39.24 | 0 | 75 | 0 | 356.9582 | 114.24 | 39.24
2025-01-10 04:00:00 | 39.3 | 0 | 75 | 0 | 422.9582 | 114.3 | 39.3
2025-01-10 05:00:00 | 28.26 | 0 | 75 | 0 | 488.9582 | 103.26 | 28.26
2025-01-10 06:00:00 | 21.6 | 0 | 75 | 0 | 554.9582 | 96.6 | 21.6
2025-01-10 07:00:00 | 22.14 | 0 | 0 | 22.14 | 532.8182 | 0 | 22.14
2025-01-10 08:00:00 | 27.54 | 3.0817 | 0 | 24.4583 | 508.3599 | -4.6185e-14 | 24.4583
2025-01-10 09:00:00 | 50.58 | 5.6933 | 0 | 44.8867 | 463.4732 | 2.8422e-14 | 44.8867
2025-01-10 10:00:00 | 57.78 | 7.54 | 0 | 50.24 | 413.2332 | 0 | 50.24
2025-01-10 11:00:00 | 60.66 | 8.4959 | 0 | 52.1641 | 361.0691 | -2.8422e-14 | 52.1641
2025-01-10 12:00:00 | 58.14 | 8.4959 | 0 | 49.6441 | 311.425 | -2.8422e-14 | 49.6441
2025-01-10 13:00:00 | 49.38 | 7.54 | 0 | 41.84 | 269.585 | 0 | 41.84
2025-01-10 14:00:00 | 42.42 | 5.6933 | 0 | 36.7267 | 232.8583 | -7.1054e-14 | 36.7267
2025-01-10 15:00:00 | 45.66 | 3.0817 | 0 | 42.5783 | 190.28 | -4.2633e-14 | 42.5783
2025-01-10 16:00:00 | 44.94 | 0 | 0 | 44.94 | 145.34 | 0 | 44.94
2025-01-10 17:00:00 | 40.56 | 0 | 0 | 40.56 | 104.78 | 0 | 40.56
2025-01-10 18:00:00 | 39.78 | 0 | 0 | 39.78 | 65 | 0 | 39.78
2025-01-10 19:00:00 | 39.42 | 0 | 0 | 0 | 65 | 39.42 | 39.42
2025-01-10 20:00:00 | 37.8 | 0 | 0 | 0 | 65 | 37.8 | 37.8
2025-01-10 21:00:00 | 37.08 | 0 | 0 | 0 | 65 | 37.08 | 37.08
2025-01-10 22:00:00 | 20.88 | 0 | 0 | 0 | 65 | 20.88 | 20.88
2025-01-10 23:00:00 | 20.76 | 0 | 0 | 0 | 65 | 20.76 | 20.76
2025-01-11 00:00:00 | 22.14 | 0 | 0 | 0 | 65 | 22.14 | 22.14
2025-01-11 01:00:00 | 37.32 | 0 | 0 | 0 | 65 | 37.32 | 37.32
2025-01-11 02:00:00 | 38.34 | 0 | 0 | 0 | 65 | 38.34 | 38.34
2025-01-11 03:00:00 | 36.3 | 0 | 0 | 0 | 65 | 36.3 | 36.3
2025-01-11 04:00:00 | 33.42 | 0 | 0 | 0 | 65 | 33.42 | 33.42
2025-01-11 05:00:00 | 22.2 | 0 | 0 | 0 | 65 | 22.2 | 22.2
2025-01-11 06:00:00 | 21.18 | 0 | 0 | 0 | 65 | 21.18 | 21.18
2025-01-11 07:00:00 | 21 | 0 | 0 | 0 | 65 | 21 | 21
2025-01-11 08:00:00 | 27.24 | 3.1239 | 0 | 0 | 65 | 24.1161 | 24.1161
2025-01-11 09:00:00 | 48.84 | 5.7381 | 0 | 0 | 65 | 43.1019 | 43.1019
2025-01-11 10:00:00 | 53.58 | 7.5866 | 0 | 0 | 65 | 45.9934 | 45.9934
2025-01-11 11:00:00 | 48 | 8.5435 | 0 | 0 | 65 | 39.4565 | 39.4565
2025-01-11 12:00:00 | 43.26 | 8.5435 | 0 | 0 | 65 | 34.7165 | 34.7165
2025-01-11 13:00:00 | 39.54 | 7.5866 | 0 | 0 | 65 | 31.9534 | 31.9534
2025-01-11 14:00:00 | 46.86 | 5.7381 | 0 | 0 | 65 | 41.1219 | 41.1219
2025-01-11 15:00:00 | 36.78 | 3.1239 | 0 | 0 | 65 | 33.6561 | 33.6561
2025-01-11 16:00:00 | 35.1 | 0 | 0 | 0 | 65 | 35.1 | 35.1
2025-01-11 17:00:00 | 36.42 | 0 | 0 | 0 | 65 | 36.42 | 36.42
2025-01-11 18:00:00 | 35.7 | 0 | 0 | 0 | 65 | 35.7 | 35.7
2025-01-11 19:00:00 | 36.42 | 0 | 0 | 0 | 65 | 36.42 | 36.42
2025-01-11 20:00:00 | 35.88 | 0 | 0 | 0 | 65 | 35.88 | 35.88
2025-01-11 21:00:00 | 43.74 | 0 | 0 | 0 | 65 | 43.74 | 43.74
2025-01-11 22:00:00 | 38.34 | 0 | 0 | 0 | 65 | 38.34 | 38.34
2025-01-11 23:00:00 | 37.32 | 0 | 0 | 0 | 65 | 37.32 | 37.32
2025-01-12 00:00:00 | 34.38 | 0 | 0 | 0 | 65 | 34.38 | 34.38
2025-01-12 01:00:00 | 21.12 | 0 | 0 | 0 | 65 | 21.12 | 21.12
2025-01-12 02:00:00 | 21.72 | 0 | 0 | 0 | 65 | 21.72 | 21.72
2025-01-12 03:00:00 | 21.12 | 0 | 0 | 0 | 65 | 21.12 | 21.12
2025-01-12 04:00:00 | 21.78 | 0 | 0 | 0 | 65 | 21.78 | 21.78
2025-01-12 05:00:00 | 27.42 | 0 | 0 | 0 | 65 | 27.42 | 27.42
2025-01-12 06:00:00 | 39.48 | 0 | 0 | 0 | 65 | 39.48 | 39.48
2025-01-12 07:00:00 | 40.2 | 0 | 0 | 0 | 65 | 40.2 | 40.2
2025-01-12 08:00:00 | 47.34 | 3.1681 | 0 | 0 | 65 | 44.1719 | 44.1719
2025-01-12 09:00:00 | 38.1 | 5.785 | 0 | 0 | 65 | 32.315 | 32.315
2025-01-12 10:00:00 | 47.4 | 7.6354 | 0 | 0 | 65 | 39.7646 | 39.7646
2025-01-12 11:00:00 | 46.74 | 8.5933 | 0 | 0 | 65 | 38.1467 | 38.1467
2025-01-12 12:00:00 | 43.14 | 8.5933 | 0 | 0 | 65 | 34.5467 | 34.5467
2025-01-12 13:00:00 | 40.14 | 7.6354 | 0 | 0 | 65 | 32.5046 | 32.5046
2025-01-12 14:00:00 | 31.98 | 5.785 | 0 | 0 | 65 | 26.195 | 26.195
2025-01-12 15:00:00 | 21.78 | 3.1681 | 0 | 0 | 65 | 18.6119 | 18.6119
2025-01-12 16:00:00 | 20.94 | 0 | 75 | 0 | 131 | 95.94 | 20.94
2025-01-12 17:00:00 | 25.32 | 0 | 41.1702 | 0 | 167.2298 | 66.4902 | 25.32
2025-01-12 18:00:00 | 33.78 | 0 | 0 | 0 | 167.2298 | 33.78 | 33.78
2025-01-12 19:00:00 | 40.92 | 0 | 0 | 0 | 167.2298 | 40.92 | 40.92
2025-01-12 20:00:00 | 45.6 | 0 | 0 | 0 | 167.2298 | 45.6 | 45.6
2025-01-12 21:00:00 | 45.84 | 0 | 0 | 0 | 167.2298 | 45.84 | 45.84
2025-01-12 22:00:00 | 42.96 | 0 | 0 | 0 | 167.2298 | 42.96 | 42.96
2025-01-12 23:00:00 | 29.16 | 0 | 0 | 0 | 167.2298 | 29.16 | 29.16
2025-01-13 00:00:00 | 24.06 | 0 | 0 | 0 | 167.2298 | 24.06 | 24.06
2025-01-13 01:00:00 | 22.38 | 0 | 0 | 0 | 167.2298 | 22.38 | 22.38
2025-01-13 02:00:00 | 22.62 | 0 | 75 | 0 | 233.2298 | 97.62 | 22.62
2025-01-13 03:00:00 | 37.44 | 0 | 75 | 0 | 299.2298 | 112.44 | 37.44
2025-01-13 04:00:00 | 36.96 | 0 | 75 | 0 | 365.2298 | 111.96 | 36.96
2025-01-13 05:00:00 | 41.58 | 0 | 75 | 0 | 431.2298 | 116.58 | 41.58
2025-01-13 06:00:00 | 51.66 | 0 | 75 | 0 | 497.2298 | 126.66 | 51.66
2025-01-13 07:00:00 | 40.92 | 0.0057199 | 0 | 40.9143 | 456.3155 | 2.1316e-14 | 40.9143
2025-01-13 08:00:00 | 39.3 | 3.2142 | 0 | 36.0858 | 420.2296 | 4.2633e-14 | 36.0858
2025-01-13 09:00:00 | 38.28 | 5.8339 | 0 | 32.4461 | 387.7835 | 1.4211e-14 | 32.4461
2025-01-13 10:00:00 | 45.6 | 7.6863 | 0 | 37.9137 | 349.8698 | -4.9738e-14 | 37.9137
2025-01-13 11:00:00 | 44.64 | 8.6451 | 0 | 35.9949 | 313.8749 | 4.2633e-14 | 35.9949
2025-01-13 12:00:00 | 42.66 | 8.6451 | 0 | 34.0149 | 279.86 | 4.2633e-14 | 34.0149
2025-01-13 13:00:00 | 38.46 | 7.6863 | 0 | 30.7737 | 249.0863 | -4.6185e-14 | 30.7737
2025-01-13 14:00:00 | 37.08 | 5.8339 | 0 | 31.2461 | 217.8401 | 3.5527e-15 | 31.2461
2025-01-13 15:00:00 | 36.72 | 3.2142 | 0 | 33.5058 | 184.3343 | 4.2633e-14 | 33.5058
2025-01-13 16:00:00 | 37.62 | 0.0057199 | 0 | 37.6143 | 146.72 | 1.4211e-14 | 37.6143
2025-01-13 17:00:00 | 37.98 | 0 | 0 | 37.98 | 108.74 | 0 | 37.98
2025-01-13 18:00:00 | 43.74 | 0 | 0 | 43.74 | 65 | 0 | 43.74
2025-01-13 19:00:00 | 45.24 | 0 | 75 | 0 | 131 | 120.24 | 45.24
2025-01-13 20:00:00 | 48.42 | 0 | 52.8064 | 0 | 177.4697 | 101.2264 | 48.42
2025-01-13 21:00:00 | 48.06 | 0 | 0 | 0 | 177.4697 | 48.06 | 48.06
2025-01-13 22:00:00 | 50.64 | 0 | 0 | 0 | 177.4697 | 50.64 | 50.64
2025-01-13 23:00:00 | 40.02 | 0 | 0 | 0 | 177.4697 | 40.02 | 40.02
2025-01-14 00:00:00 | 40.08 | 0 | 0 | 0 | 177.4697 | 40.08 | 40.08
2025-01-14 01:00:00 | 39.12 | 0 | 0 | 0 | 177.4697 | 39.12 | 39.12
2025-01-14 02:00:00 | 36.66 | 0 | 75 | 0 | 243.4697 | 111.66 | 36.66
2025-01-14 03:00:00 | 37.26 | 0 | 75 | 0 | 309.4697 | 112.26 | 37.26
2025-01-14 04:00:00 | 36.9 | 0 | 75 | 0 | 375.4697 | 111.9 | 36.9
2025-01-14 05:00:00 | 37.74 | 0 | 75 | 0 | 441.4697 | 112.74 | 37.74
2025-01-14 06:00:00 | 37.02 | 0 | 75 | 0 | 507.4697 | 112.02 | 37.02
2025-01-14 07:00:00 | 36.84 | 0.050126 | 0 | 36.7899 | 470.6798 | -4.9738e-14 | 36.7899
2025-01-14 08:00:00 | 43.26 | 3.2621 | 0 | 39.9979 | 430.6819 | 2.1316e-14 | 39.9979
2025-01-14 09:00:00 | 47.4 | 5.8847 | 0 | 41.5153 | 389.1666 | 4.2633e-14 | 41.5153
2025-01-14 10:00:00 | 46.26 | 7.7391 | 0 | 38.5209 | 350.6458 | 2.1316e-14 | 38.5209
2025-01-14 11:00:00 | 44.64 | 8.6991 | 0 | 35.9409 | 314.7048 | -7.1054e-15 | 35.9409
2025-01-14 12:00:00 | 42.3 | 8.6991 | 0 | 33.6009 | 281.1039 | -1.4211e-14 | 33.6009
2025-01-14 13:00:00 | 38.64 | 7.7391 | 0 | 30.9009 | 250.2031 | 2.8422e-14 | 30.9009
2025-01-14 14:00:00 | 37.68 | 5.8847 | 0 | 31.7953 | 218.4078 | 4.2633e-14 | 31.7953
2025-01-14 15:00:00 | 36.96 | 3.2621 | 0 | 33.6979 | 184.7099 | 2.8422e-14 | 33.6979
2025-01-14 16:00:00 | 37.8 | 0.050126 | 0 | 37.7499 | 146.96 | 4.2633e-14 | 37.7499
2025-01-14 17:00:00 | 38.88 | 0 | 0 | 38.88 | 108.08 | 0 | 38.88
2025-01-14 18:00:00 | 43.08 | 0 | 0 | 43.08 | 65 | 0 | 43.08
2025-01-14 19:00:00 | 51.48 | 0 | 0 | 0 | 65 | 51.48 | 51.48
2025-01-14 20:00:00 | 54.72 | 0 | 49.0798 | 0 | 108.1902 | 103.7998 | 54.72
2025-01-14 21:00:00 | 46.98 | 0 | 0 | 0 | 108.1902 | 46.98 | 46.98
2025-01-14 22:00:00 | 27.54 | 0 | 0 | 0 | 108.1902 | 27.54 | 27.54
2025-01-14 23:00:00 | 24.6 | 0 | 0 | 0 | 108.1902 | 24.6 | 24.6
2025-01-15 00:00:00 | 24.9 | 0 | 0 | 0 | 108.1902 | 24.9 | 24.9
2025-01-15 01:00:00 | 23.04 | 0 | 0 | 0 | 108.1902 | 23.04 | 23.04
2025-01-15 02:00:00 | 21.72 | 0 | 0 | 0 | 108.1902 | 21.72 | 21.72
2025-01-15 03:00:00 | 21.96 | 0 | 0 | 0 | 108.1902 | 21.96 | 21.96
2025-01-15 04:00:00 | 22.14 | 0 | 75 | 0 | 174.1902 | 97.14 | 22.14
2025-01-15 05:00:00 | 21.78 | 0 | 75 | 0 | 240.1902 | 96.78 | 21.78
2025-01-15 06:00:00 | 21.3 | 0 | 75 | 0 | 306.1902 | 96.3 | 21.3
2025-01-15 07:00:00 | 21.18 | 0.09629 | 0 | 21.0837 | 285.1065 | -1.0658e-14 | 21.0837
2025-01-15 08:00:00 | 22.32 | 3.3119 | 0 | 19.0081 | 266.0984 | 4.2633e-14 | 19.0081
2025-01-15 09:00:00 | 21.06 | 5.9375 | 0 | 15.1225 | 250.9759 | -3.0198e-14 | 15.1225
2025-01-15 10:00:00 | 21.72 | 7.7941 | 0 | 13.9259 | 237.05 | 1.4211e-14 | 13.9259
2025-01-15 11:00:00 | 21.6 | 8.7551 | 0 | 12.8449 | 224.2051 | -4.2633e-14 | 12.8449
2025-01-15 12:00:00 | 21.84 | 8.7551 | 0 | 13.0849 | 211.1202 | -4.4409e-14 | 13.0849
2025-01-15 13:00:00 | 21.24 | 7.7941 | 0 | 13.4459 | 197.6743 | 1.4211e-14 | 13.4459
2025-01-15 14:00:00 | 21.36 | 5.9375 | 0 | 15.4225 | 182.2518 | -3.0198e-14 | 15.4225
2025-01-15 15:00:00 | 23.58 | 3.3119 | 0 | 20.2681 | 161.9837 | 3.908e-14 | 20.2681
2025-01-15 16:00:00 | 35.22 | 0.09629 | 0 | 35.1237 | 126.86 | -1.4211e-14 | 35.1237
2025-01-15 17:00:00 | 31.14 | 0 | 0 | 31.14 | 95.72 | 0 | 31.14
2025-01-15 18:00:00 | 30.72 | 0 | 0 | 30.72 | 65 | 0 | 30.72
2025-01-15 19:00:00 | 34.02 | 0 | 0 | 0 | 65 | 34.02 | 34.02
2025-01-15 20:00:00 | 38.46 | 0 | 0 | 0 | 65 | 38.46 | 38.46
2025-01-15 21:00:00 | 39.48 | 0 | 0 | 0 | 65 | 39.48 | 39.48
2025-01-15 22:00:00 | 25.62 | 0 | 64.4904 | 0 | 121.7516 | 90.1104 | 25.62
2025-01-15 23:00:00 | 22.8 | 0 | 0 | 0 | 121.7516 | 22.8 | 22.8
2025-01-16 00:00:00 | 21.72 | 0 | 0 | 0 | 121.7516 | 21.72 | 21.72
2025-01-16 01:00:00 | 22.02 | 0 | 0 | 0 | 121.7516 | 22.02 | 22.02
2025-01-16 02:00:00 | 22.38 | 0 | 0 | 0 | 121.7516 | 22.38 | 22.38
2025-01-16 03:00:00 | 21.84 | 0 | 0 | 0 | 121.7516 | 21.84 | 21.84
2025-01-16 04:00:00 | 22.02 | 0 | 75 | 0 | 187.7516 | 97.02 | 22.02
2025-01-16 05:00:00 | 21.96 | 0 | 75 | 0 | 253.7516 | 96.96 | 21.96
2025-01-16 06:00:00 | 21.78 | 0 | 75 | 0 | 319.7516 | 96.78 | 21.78
2025-01-16 07:00:00 | 22.14 | 0.1442 | 0 | 21.9958 | 297.7558 | 3.5527e-14 | 21.9958
2025-01-16 08:00:00 | 21.6 | 3.3636 | 0 | 18.2364 | 279.5194 | 3.5527e-14 | 18.2364
2025-01-16 09:00:00 | 21.24 | 5.9923 | 0 | 15.2477 | 264.2717 | 1.954e-14 | 15.2477
2025-01-16 10:00:00 | 21.24 | 7.851 | 0 | 13.389 | 250.8827 | 3.1974e-14 | 13.389
2025-01-16 11:00:00 | 21.84 | 8.8131 | 0 | 13.0269 | 237.8558 | -7.1054e-15 | 13.0269
2025-01-16 12:00:00 | 21.66 | 8.8131 | 0 | 12.8469 | 225.0089 | -7.1054e-15 | 12.8469
2025-01-16 13:00:00 | 21.06 | 7.851 | 0 | 13.209 | 211.7999 | 3.1974e-14 | 13.209
2025-01-16 14:00:00 | 21.42 | 5.9923 | 0 | 15.4277 | 196.3722 | 2.1316e-14 | 15.4277
2025-01-16 15:00:00 | 29.46 | 3.3636 | 0 | 26.0964 | 170.2758 | 3.5527e-14 | 26.0964
2025-01-16 16:00:00 | 35.4 | 0.1442 | 0 | 35.2558 | 135.02 | 3.5527e-14 | 35.2558
2025-01-16 17:00:00 | 36.72 | 0 | 0 | 36.72 | 98.3 | 0 | 36.72
2025-01-16 18:00:00 | 33.3 | 0 | 0 | 33.3 | 65 | 0 | 33.3
2025-01-16 19:00:00 | 24.66 | 0 | 75 | 0 | 131 | 99.66 | 24.66
2025-01-16 20:00:00 | 35.1 | 0 | 75 | 0 | 197 | 110.1 | 35.1
2025-01-16 21:00:00 | 40.26 | 0 | 16.4023 | 0 | 211.434 | 56.6623 | 40.26
2025-01-16 22:00:00 | 38.22 | 0 | 0 | 0 | 211.434 | 38.22 | 38.22
2025-01-16 23:00:00 | 23.7 | 0 | 0 | 0 | 211.434 | 23.7 | 23.7
2025-01-17 00:00:00 | 21.24 | 0 | 0 | 0 | 211.434 | 21.24 | 21.24
2025-01-17 01:00:00 | 21.72 | 0 | 0 | 0 | 211.434 | 21.72 | 21.72
2025-01-17 02:00:00 | 21.78 | 0 | 0 | 0 | 211.434 | 21.78 | 21.78
2025-01-17 03:00:00 | 27.06 | 0 | 75 | 0 | 277.434 | 102.06 | 27.06
2025-01-17 04:00:00 | 37.14 | 0 | 75 | 0 | 343.434 | 112.14 | 37.14
2025-01-17 05:00:00 | 37.32 | 0 | 75 | 0 | 409.434 | 112.32 | 37.32
2025-01-17 06:00:00 | 38.4 | 0 | 75 | 0 | 475.434 | 113.4 | 38.4
2025-01-17 07:00:00 | 32.22 | 0.19383 | 0 | 32.0262 | 443.4079 | 0 | 32.0262
2025-01-17 08:00:00 | 21 | 3.4171 | 0 | 17.5829 | 425.825 | 2.4869e-14 | 17.5829
2025-01-17 09:00:00 | 21 | 6.0489 | 0 | 14.9511 | 410.8739 | -1.7764e-14 | 14.9511
2025-01-17 10:00:00 | 21.24 | 7.9099 | 0 | 13.3301 | 397.5438 | 7.1054e-15 | 13.3301
2025-01-17 11:00:00 | 32.16 | 8.8732 | 0 | 23.2868 | 374.257 | -3.908e-14 | 23.2868
2025-01-17 12:00:00 | 36.9 | 8.8732 | 0 | 28.0268 | 346.2302 | -3.908e-14 | 28.0268
2025-01-17 13:00:00 | 41.7 | 7.9099 | 0 | 33.7901 | 312.4401 | 1.4211e-14 | 33.7901
2025-01-17 14:00:00 | 48.54 | 6.0489 | 0 | 42.4911 | 269.949 | -1.4211e-14 | 42.4911
2025-01-17 15:00:00 | 62.7 | 3.4171 | 0 | 59.2829 | 210.6662 | 2.8422e-14 | 59.2829
2025-01-17 16:00:00 | 59.94 | 0.19383 | 0 | 59.7462 | 150.92 | 0 | 59.7462
2025-01-17 17:00:00 | 44.58 | 0 | 0 | 44.58 | 106.34 | 0 | 44.58
2025-01-17 18:00:00 | 41.34 | 0 | 0 | 41.34 | 65 | 0 | 41.34
2025-01-17 19:00:00 | 27.96 | 0 | 0 | 0 | 65 | 27.96 | 27.96
2025-01-17 20:00:00 | 23.34 | 0 | 0 | 0 | 65 | 23.34 | 23.34
2025-01-17 21:00:00 | 21.24 | 0 | 0 | 0 | 65 | 21.24 | 21.24
2025-01-17 22:00:00 | 22.5 | 0 | 0 | 0 | 65 | 22.5 | 22.5
2025-01-17 23:00:00 | 21.42 | 0 | 0 | 0 | 65 | 21.42 | 21.42
2025-01-18 00:00:00 | 21.24 | 0 | 0 | 0 | 65 | 21.24 | 21.24
2025-01-18 01:00:00 | 21.24 | 0 | 0 | 0 | 65 | 21.24 | 21.24
2025-01-18 02:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-01-18 03:00:00 | 21.42 | 0 | 0 | 0 | 65 | 21.42 | 21.42
2025-01-18 04:00:00 | 22.5 | 0 | 0 | 0 | 65 | 22.5 | 22.5
2025-01-18 05:00:00 | 21.36 | 0 | 0 | 0 | 65 | 21.36 | 21.36
2025-01-18 06:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-01-18 07:00:00 | 21.48 | 0.24518 | 0 | 0 | 65 | 21.2348 | 21.2348
2025-01-18 08:00:00 | 24.72 | 3.4724 | 0 | 0 | 65 | 21.2476 | 21.2476
2025-01-18 09:00:00 | 34.56 | 6.1075 | 0 | 0 | 65 | 28.4525 | 28.4525
2025-01-18 10:00:00 | 44.88 | 7.9708 | 0 | 0 | 65 | 36.9092 | 36.9092
2025-01-18 11:00:00 | 37.74 | 8.9353 | 0 | 0 | 65 | 28.8047 | 28.8047
2025-01-18 12:00:00 | 28.32 | 8.9353 | 0 | 0 | 65 | 19.3847 | 19.3847
2025-01-18 13:00:00 | 25.38 | 7.9708 | 0 | 0 | 65 | 17.4092 | 17.4092
2025-01-18 14:00:00 | 24.54 | 6.1075 | 0 | 0 | 65 | 18.4325 | 18.4325
2025-01-18 15:00:00 | 23.34 | 3.4724 | 0 | 0 | 65 | 19.8676 | 19.8676
2025-01-18 16:00:00 | 21.12 | 0.24518 | 0 | 0 | 65 | 20.8748 | 20.8748
2025-01-18 17:00:00 | 21.84 | 0 | 0 | 0 | 65 | 21.84 | 21.84
2025-01-18 18:00:00 | 22.2 | 0 | 0 | 0 | 65 | 22.2 | 22.2
2025-01-18 19:00:00 | 21.66 | 0 | 0 | 0 | 65 | 21.66 | 21.66
2025-01-18 20:00:00 | 22.02 | 0 | 0 | 0 | 65 | 22.02 | 22.02
2025-01-18 21:00:00 | 21.48 | 0 | 0 | 0 | 65 | 21.48 | 21.48
2025-01-18 22:00:00 | 21.66 | 0 | 0 | 0 | 65 | 21.66 | 21.66
2025-01-18 23:00:00 | 21.42 | 0 | 0 | 0 | 65 | 21.42 | 21.42
2025-01-19 00:00:00 | 22.5 | 0 | 0 | 0 | 65 | 22.5 | 22.5
2025-01-19 01:00:00 | 22.02 | 0 | 0 | 0 | 65 | 22.02 | 22.02
2025-01-19 02:00:00 | 21.18 | 0 | 0 | 0 | 65 | 21.18 | 21.18
2025-01-19 03:00:00 | 21.72 | 0 | 0 | 0 | 65 | 21.72 | 21.72
2025-01-19 04:00:00 | 22.44 | 0 | 0 | 0 | 65 | 22.44 | 22.44
2025-01-19 05:00:00 | 21.54 | 0 | 0 | 0 | 65 | 21.54 | 21.54
2025-01-19 06:00:00 | 21.48 | 0 | 0 | 0 | 65 | 21.48 | 21.48
2025-01-19 07:00:00 | 21.48 | 0.29822 | 0 | 0 | 65 | 21.1818 | 21.1818
2025-01-19 08:00:00 | 27.42 | 3.5296 | 0 | 0 | 65 | 23.8904 | 23.8904
2025-01-19 09:00:00 | 31.56 | 6.1679 | 0 | 0 | 65 | 25.3921 | 25.3921
2025-01-19 10:00:00 | 30.3 | 8.0335 | 0 | 0 | 65 | 22.2665 | 22.2665
2025-01-19 11:00:00 | 30.18 | 8.9993 | 0 | 0 | 65 | 21.1807 | 21.1807
2025-01-19 12:00:00 | 26.16 | 8.9993 | 0 | 0 | 65 | 17.1607 | 17.1607
2025-01-19 13:00:00 | 23.28 | 8.0335 | 0 | 0 | 65 | 15.2465 | 15.2465
2025-01-19 14:00:00 | 21.72 | 6.1679 | 0 | 0 | 65 | 15.5521 | 15.5521
2025-01-19 15:00:00 | 22.14 | 3.5296 | 0 | 0 | 65 | 18.6104 | 18.6104
2025-01-19 16:00:00 | 25.38 | 0.29822 | 0 | 0 | 65 | 25.0818 | 25.0818
2025-01-19 17:00:00 | 22.14 | 0 | 0 | 0 | 65 | 22.14 | 22.14
2025-01-19 18:00:00 | 21.48 | 0 | 0 | 0 | 65 | 21.48 | 21.48
2025-01-19 19:00:00 | 35.7 | 0 | 0 | 0 | 65 | 35.7 | 35.7
2025-01-19 20:00:00 | 38.04 | 0 | 0 | 0 | 65 | 38.04 | 38.04
2025-01-19 21:00:00 | 36.6 | 0 | 0 | 0 | 65 | 36.6 | 36.6
2025-01-19 22:00:00 | 35.88 | 0 | 0 | 0 | 65 | 35.88 | 35.88
2025-01-19 23:00:00 | 26.28 | 0 | 0 | 0 | 65 | 26.28 | 26.28
2025-01-20 00:00:00 | 25.44 | 0 | 0 | 0 | 65 | 25.44 | 25.44
2025-01-20 01:00:00 | 24.66 | 0 | 0 | 0 | 65 | 24.66 | 24.66
2025-01-20 02:00:00 | 21.36 | 0 | 0 | 0 | 65 | 21.36 | 21.36
2025-01-20 03:00:00 | 22.98 | 0 | 0 | 0 | 65 | 22.98 | 22.98
2025-01-20 04:00:00 | 21.42 | 0 | 0 | 0 | 65 | 21.42 | 21.42
2025-01-20 05:00:00 | 22.02 | 0 | 0 | 0 | 65 | 22.02 | 22.02
2025-01-20 06:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-01-20 07:00:00 | 21.84 | 0.35295 | 0 | 0 | 65 | 21.487 | 21.487
2025-01-20 08:00:00 | 25.68 | 3.5884 | 0 | 0 | 65 | 22.0916 | 22.0916
2025-01-20 09:00:00 | 21.6 | 6.2302 | 0 | 0 | 65 | 15.3698 | 15.3698
2025-01-20 10:00:00 | 21.96 | 8.0982 | 0 | 0 | 65 | 13.8618 | 13.8618
2025-01-20 11:00:00 | 21.54 | 9.0652 | 0 | 0 | 65 | 12.4748 | 12.4748
2025-01-20 12:00:00 | 21.72 | 9.0652 | 0 | 0 | 65 | 12.6548 | 12.6548
2025-01-20 13:00:00 | 21.78 | 8.0982 | 0 | 0 | 65 | 13.6818 | 13.6818
2025-01-20 14:00:00 | 21.72 | 6.2302 | 0 | 0 | 65 | 15.4898 | 15.4898
2025-01-20 15:00:00 | 21.6 | 3.5884 | 0 | 0 | 65 | 18.0116 | 18.0116
2025-01-20 16:00:00 | 21.48 | 0.35295 | 0 | 0 | 65 | 21.127 | 21.127
2025-01-20 17:00:00 | 33.36 | 0 | 0 | 0 | 65 | 33.36 | 33.36
2025-01-20 18:00:00 | 31.14 | 0 | 0 | 0 | 65 | 31.14 | 31.14
2025-01-20 19:00:00 | 35.46 | 0 | 0 | 0 | 65 | 35.46 | 35.46
2025-01-20 20:00:00 | 52.14 | 0 | 0 | 0 | 65 | 52.14 | 52.14
2025-01-20 21:00:00 | 53.52 | 0 | 0 | 0 | 65 | 53.52 | 53.52
2025-01-20 22:00:00 | 43.62 | 0 | 0 | 0 | 65 | 43.62 | 43.62
2025-01-20 23:00:00 | 25.38 | 0 | 0 | 0 | 65 | 25.38 | 25.38
2025-01-21 00:00:00 | 24.78 | 0 | 0 | 0 | 65 | 24.78 | 24.78
2025-01-21 01:00:00 | 22.14 | 0 | 0 | 0 | 65 | 22.14 | 22.14
2025-01-21 02:00:00 | 22.8 | 0 | 0 | 0 | 65 | 22.8 | 22.8
2025-01-21 03:00:00 | 22.38 | 0 | 70.6922 | 0 | 127.2091 | 93.0722 | 22.38
2025-01-21 04:00:00 | 22.08 | 0 | 75 | 0 | 193.2091 | 97.08 | 22.08
2025-01-21 05:00:00 | 21.78 | 0 | 75 | 0 | 259.2091 | 96.78 | 21.78
2025-01-21 06:00:00 | 22.02 | 0 | 75 | 0 | 325.2091 | 97.02 | 22.02
2025-01-21 07:00:00 | 22.5 | 0.40934 | 0 | 22.0907 | 303.1184 | 4.2633e-14 | 22.0907
2025-01-21 08:00:00 | 25.38 | 3.6491 | 0 | 21.7309 | 281.3875 | -1.7764e-14 | 21.7309
2025-01-21 09:00:00 | 34.32 | 6.2943 | 0 | 28.0257 | 253.3618 | 3.908e-14 | 28.0257
2025-01-21 10:00:00 | 31.08 | 8.1648 | 0 | 22.9152 | 230.4466 | 2.8422e-14 | 22.9152
2025-01-21 11:00:00 | 30.6 | 9.133 | 0 | 21.467 | 208.9796 | 3.5527e-14 | 21.467
2025-01-21 12:00:00 | 29.1 | 9.133 | 0 | 19.967 | 189.0126 | 3.5527e-14 | 19.967
2025-01-21 13:00:00 | 26.1 | 8.1648 | 0 | 17.9352 | 171.0774 | 3.1974e-14 | 17.9352
2025-01-21 14:00:00 | 22.26 | 6.2943 | 0 | 15.9657 | 155.1118 | 3.908e-14 | 15.9657
2025-01-21 15:00:00 | 22.38 | 3.6491 | 0 | 18.7309 | 136.3808 | -1.7764e-14 | 18.7309
2025-01-21 16:00:00 | 21.66 | 0.40934 | 0 | 21.2507 | 115.1302 | 4.2633e-14 | 21.2507
2025-01-21 17:00:00 | 21.84 | 0 | 0 | 21.84 | 93.2902 | 0 | 21.84
2025-01-21 18:00:00 | 26.46 | 0 | 0 | 26.46 | 66.8302 | 0 | 26.46
2025-01-21 19:00:00 | 36.96 | 0 | 0 | 0 | 66.8302 | 36.96 | 36.96
2025-01-21 20:00:00 | 38.64 | 0 | 0 | 0 | 66.8302 | 38.64 | 38.64
2025-01-21 21:00:00 | 36.9 | 0 | 0 | 0 | 66.8302 | 36.9 | 36.9
2025-01-21 22:00:00 | 32.04 | 0 | 0 | 0 | 66.8302 | 32.04 | 32.04
2025-01-21 23:00:00 | 42.3 | 0 | 0 | 0 | 66.8302 | 42.3 | 42.3
2025-01-22 00:00:00 | 40.56 | 0 | 0 | 0 | 66.8302 | 40.56 | 40.56
2025-01-22 01:00:00 | 34.86 | 0 | 0 | 0 | 66.8302 | 34.86 | 34.86
2025-01-22 02:00:00 | 21.78 | 0 | 0 | 0 | 66.8302 | 21.78 | 21.78
2025-01-22 03:00:00 | 22.02 | 0 | 75 | 0 | 132.8302 | 97.02 | 22.02
2025-01-22 04:00:00 | 22.2 | 0 | 75 | 0 | 198.8302 | 97.2 | 22.2
2025-01-22 05:00:00 | 21.24 | 0 | 75 | 0 | 264.8302 | 96.24 | 21.24
2025-01-22 06:00:00 | 21.72 | 0 | 75 | 0 | 330.8302 | 96.72 | 21.72
2025-01-22 07:00:00 | 21.6 | 0.46737 | 0 | 21.1326 | 309.6975 | -3.5527e-14 | 21.1326
2025-01-22 08:00:00 | 21.54 | 3.7114 | 0 | 17.8286 | 291.869 | 1.0658e-14 | 17.8286
2025-01-22 09:00:00 | 28.68 | 6.3602 | 0 | 22.3198 | 269.5492 | -1.0658e-14 | 22.3198
2025-01-22 10:00:00 | 37.14 | 8.2332 | 0 | 28.9068 | 240.6424 | 2.4869e-14 | 28.9068
2025-01-22 11:00:00 | 37.08 | 9.2027 | 0 | 27.8773 | 212.7651 | -2.4869e-14 | 27.8773
2025-01-22 12:00:00 | 23.04 | 9.2027 | 0 | 13.8373 | 198.9278 | -2.1316e-14 | 13.8373
2025-01-22 13:00:00 | 21.54 | 8.2332 | 0 | 13.3068 | 185.621 | 2.3093e-14 | 13.3068
2025-01-22 14:00:00 | 22.14 | 6.3602 | 0 | 15.7798 | 169.8412 | -1.0658e-14 | 15.7798
2025-01-22 15:00:00 | 26.82 | 3.7114 | 0 | 23.1086 | 146.7326 | 1.0658e-14 | 23.1086
2025-01-22 16:00:00 | 22.14 | 0.46737 | 0 | 21.6726 | 125.06 | -3.5527e-14 | 21.6726
2025-01-22 17:00:00 | 21.36 | 0 | 0 | 21.36 | 103.7 | 0 | 21.36
2025-01-22 18:00:00 | 38.7 | 0 | 0 | 38.7 | 65 | 0 | 38.7
2025-01-22 19:00:00 | 45.9 | 0 | 0 | 0 | 65 | 45.9 | 45.9
2025-01-22 20:00:00 | 44.22 | 0 | 0 | 0 | 65 | 44.22 | 44.22
2025-01-22 21:00:00 | 29.04 | 0 | 0 | 0 | 65 | 29.04 | 29.04
2025-01-22 22:00:00 | 24.48 | 0 | 69.0954 | 0 | 125.8039 | 93.5754 | 24.48
2025-01-22 23:00:00 | 21.42 | 0 | 0 | 0 | 125.8039 | 21.42 | 21.42
2025-01-23 00:00:00 | 22.32 | 0 | 0 | 0 | 125.8039 | 22.32 | 22.32
2025-01-23 01:00:00 | 21.72 | 0 | 0 | 0 | 125.8039 | 21.72 | 21.72
2025-01-23 02:00:00 | 22.14 | 0 | 0 | 0 | 125.8039 | 22.14 | 22.14
2025-01-23 03:00:00 | 22.38 | 0 | 0 | 0 | 125.8039 | 22.38 | 22.38
2025-01-23 04:00:00 | 21.78 | 0 | 75 | 0 | 191.8039 | 96.78 | 21.78
2025-01-23 05:00:00 | 21.96 | 0 | 75 | 0 | 257.8039 | 96.96 | 21.96
2025-01-23 06:00:00 | 22.44 | 0 | 75 | 0 | 323.8039 | 97.44 | 22.44
2025-01-23 07:00:00 | 21.54 | 0.52703 | 0 | 21.013 | 302.791 | -4.6185e-14 | 21.013
2025-01-23 08:00:00 | 21.36 | 3.7755 | 0 | 17.5845 | 285.2065 | -7.1054e-15 | 17.5845
2025-01-23 09:00:00 | 22.44 | 6.4279 | 0 | 16.0121 | 269.1944 | 7.1054e-15 | 16.0121
2025-01-23 10:00:00 | 21.78 | 8.3034 | 0 | 13.4766 | 255.7177 | -2.8422e-14 | 13.4766
2025-01-23 11:00:00 | 21.54 | 9.2742 | 0 | 12.2658 | 243.452 | -1.4211e-14 | 12.2658
2025-01-23 12:00:00 | 21.96 | 9.2742 | 0 | 12.6858 | 230.7662 | -1.2434e-14 | 12.6858
2025-01-23 13:00:00 | 21.78 | 8.3034 | 0 | 13.4766 | 217.2896 | -2.8422e-14 | 13.4766
2025-01-23 14:00:00 | 22.08 | 6.4279 | 0 | 15.6521 | 201.6375 | 5.3291e-15 | 15.6521
2025-01-23 15:00:00 | 31.32 | 3.7755 | 0 | 27.5445 | 174.093 | -7.1054e-15 | 27.5445
2025-01-23 16:00:00 | 37.74 | 0.52703 | 0 | 37.213 | 136.88 | -4.2633e-14 | 37.213
2025-01-23 17:00:00 | 39.12 | 0 | 0 | 39.12 | 97.76 | 0 | 39.12
2025-01-23 18:00:00 | 32.76 | 0 | 0 | 32.76 | 65 | 0 | 32.76
2025-01-23 19:00:00 | 29.16 | 0 | 13.5006 | 0 | 76.8805 | 42.6606 | 29.16
2025-01-23 20:00:00 | 26.58 | 0 | 0 | 0 | 76.8805 | 26.58 | 26.58
2025-01-23 21:00:00 | 26.46 | 0 | 0 | 0 | 76.8805 | 26.46 | 26.46
2025-01-23 22:00:00 | 25.02 | 0 | 0 | 0 | 76.8805 | 25.02 | 25.02
2025-01-23 23:00:00 | 22.98 | 0 | 0 | 0 | 76.8805 | 22.98 | 22.98
2025-01-24 00:00:00 | 23.04 | 0 | 0 | 0 | 76.8805 | 23.04 | 23.04
2025-01-24 01:00:00 | 22.98 | 0 | 0 | 0 | 76.8805 | 22.98 | 22.98
2025-01-24 02:00:00 | 22.02 | 0 | 0 | 0 | 76.8805 | 22.02 | 22.02
2025-01-24 03:00:00 | 23.16 | 0 | 75 | 0 | 142.8805 | 98.16 | 23.16
2025-01-24 04:00:00 | 22.2 | 0 | 75 | 0 | 208.8805 | 97.2 | 22.2
2025-01-24 05:00:00 | 23.1 | 0 | 75 | 0 | 274.8805 | 98.1 | 23.1
2025-01-24 06:00:00 | 22.8 | 0 | 75 | 0 | 340.8805 | 97.8 | 22.8
2025-01-24 07:00:00 | 22.26 | 0.5883 | 0 | 21.6717 | 319.2088 | 4.6185e-14 | 21.6717
2025-01-24 08:00:00 | 22.56 | 3.8413 | 0 | 18.7187 | 300.4901 | 4.6185e-14 | 18.7187
2025-01-24 09:00:00 | 31.14 | 6.4973 | 0 | 24.6427 | 275.8473 | 3.5527e-14 | 24.6427
2025-01-24 10:00:00 | 30.78 | 8.3754 | 0 | 22.4046 | 253.4427 | 4.2633e-14 | 22.4046
2025-01-24 11:00:00 | 30.66 | 9.3475 | 0 | 21.3125 | 232.1302 | 3.908e-14 | 21.3125
2025-01-24 12:00:00 | 30.6 | 9.3475 | 0 | 21.2525 | 210.8778 | 4.2633e-14 | 21.2525
2025-01-24 13:00:00 | 28.38 | 8.3754 | 0 | 20.0046 | 190.8732 | 4.2633e-14 | 20.0046
2025-01-24 14:00:00 | 22.98 | 6.4973 | 0 | 16.4827 | 174.3904 | 3.1974e-14 | 16.4827
2025-01-24 15:00:00 | 29.7 | 3.8413 | 0 | 25.8587 | 148.5317 | 4.6185e-14 | 25.8587
2025-01-24 16:00:00 | 31.62 | 0.5883 | 0 | 31.0317 | 117.5 | 4.6185e-14 | 31.0317
2025-01-24 17:00:00 | 27.6 | 0 | 0 | 27.6 | 89.9 | 0 | 27.6
2025-01-24 18:00:00 | 24.9 | 0 | 0 | 24.9 | 65 | 0 | 24.9
2025-01-24 19:00:00 | 28.8 | 0 | 0 | 0 | 65 | 28.8 | 28.8
2025-01-24 20:00:00 | 32.58 | 0 | 0 | 0 | 65 | 32.58 | 32.58
2025-01-24 21:00:00 | 31.08 | 0 | 0 | 0 | 65 | 31.08 | 31.08
2025-01-24 22:00:00 | 30.84 | 0 | 0 | 0 | 65 | 30.84 | 30.84
2025-01-24 23:00:00 | 28.86 | 0 | 0 | 0 | 65 | 28.86 | 28.86
2025-01-25 00:00:00 | 24.48 | 0 | 0 | 0 | 65 | 24.48 | 24.48
2025-01-25 01:00:00 | 23.04 | 0 | 0 | 0 | 65 | 23.04 | 23.04
2025-01-25 02:00:00 | 21.78 | 0 | 0 | 0 | 65 | 21.78 | 21.78
2025-01-25 03:00:00 | 21.9 | 0 | 0 | 0 | 65 | 21.9 | 21.9
2025-01-25 04:00:00 | 22.5 | 0 | 0 | 0 | 65 | 22.5 | 22.5
2025-01-25 05:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-01-25 06:00:00 | 21.9 | 0 | 0 | 0 | 65 | 21.9 | 21.9
2025-01-25 07:00:00 | 21.78 | 0.65116 | 0 | 0 | 65 | 21.1288 | 21.1288
2025-01-25 08:00:00 | 21.96 | 3.9087 | 0 | 0 | 65 | 18.0513 | 18.0513
2025-01-25 09:00:00 | 26.7 | 6.5684 | 0 | 0 | 65 | 20.1316 | 20.1316
2025-01-25 10:00:00 | 30.24 | 8.4491 | 0 | 0 | 65 | 21.7909 | 21.7909
2025-01-25 11:00:00 | 30.06 | 9.4226 | 0 | 0 | 65 | 20.6374 | 20.6374
2025-01-25 12:00:00 | 27.24 | 9.4226 | 0 | 0 | 65 | 17.8174 | 17.8174
2025-01-25 13:00:00 | 24.66 | 8.4491 | 0 | 0 | 65 | 16.2109 | 16.2109
2025-01-25 14:00:00 | 24.36 | 6.5684 | 0 | 0 | 65 | 17.7916 | 17.7916
2025-01-25 15:00:00 | 23.1 | 3.9087 | 0 | 0 | 65 | 19.1913 | 19.1913
2025-01-25 16:00:00 | 21.84 | 0.65116 | 0 | 0 | 65 | 21.1888 | 21.1888
2025-01-25 17:00:00 | 22.2 | 0 | 0 | 0 | 65 | 22.2 | 22.2
2025-01-25 18:00:00 | 21.66 | 0 | 0 | 0 | 65 | 21.66 | 21.66
2025-01-25 19:00:00 | 22.44 | 0 | 0 | 0 | 65 | 22.44 | 22.44
2025-01-25 20:00:00 | 22.14 | 0 | 0 | 0 | 65 | 22.14 | 22.14
2025-01-25 21:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-01-25 22:00:00 | 22.5 | 0 | 0 | 0 | 65 | 22.5 | 22.5
2025-01-25 23:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-01-26 00:00:00 | 21.84 | 0 | 0 | 0 | 65 | 21.84 | 21.84
2025-01-26 01:00:00 | 22.26 | 0 | 0 | 0 | 65 | 22.26 | 22.26
2025-01-26 02:00:00 | 21.96 | 0 | 0 | 0 | 65 | 21.96 | 21.96
2025-01-26 03:00:00 | 22.44 | 0 | 0 | 0 | 65 | 22.44 | 22.44
2025-01-26 04:00:00 | 22.8 | 0 | 0 | 0 | 65 | 22.8 | 22.8
2025-01-26 05:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-01-26 06:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-01-26 07:00:00 | 21.84 | 0.71559 | 0 | 0 | 65 | 21.1244 | 21.1244
2025-01-26 08:00:00 | 22.56 | 3.9777 | 0 | 0 | 65 | 18.5823 | 18.5823
2025-01-26 09:00:00 | 21.96 | 6.6412 | 0 | 0 | 65 | 15.3188 | 15.3188
2025-01-26 10:00:00 | 25.62 | 8.5245 | 0 | 0 | 65 | 17.0955 | 17.0955
2025-01-26 11:00:00 | 24.48 | 9.4995 | 0 | 0 | 65 | 14.9805 | 14.9805
2025-01-26 12:00:00 | 21.6 | 9.4995 | 0 | 0 | 65 | 12.1005 | 12.1005
2025-01-26 13:00:00 | 23.28 | 8.5245 | 0 | 0 | 65 | 14.7555 | 14.7555
2025-01-26 14:00:00 | 21.6 | 6.6412 | 0 | 0 | 65 | 14.9588 | 14.9588
2025-01-26 15:00:00 | 21.48 | 3.9777 | 0 | 0 | 65 | 17.5023 | 17.5023
2025-01-26 16:00:00 | 21.84 | 0.71559 | 0 | 0 | 65 | 21.1244 | 21.1244
2025-01-26 17:00:00 | 29.4 | 0 | 0 | 0 | 65 | 29.4 | 29.4
2025-01-26 18:00:00 | 33.06 | 0 | 0 | 0 | 65 | 33.06 | 33.06
2025-01-26 19:00:00 | 36.9 | 0 | 0 | 0 | 65 | 36.9 | 36.9
2025-01-26 20:00:00 | 38.94 | 0 | 29.3975 | 0 | 90.8698 | 68.3375 | 38.94
2025-01-26 21:00:00 | 36.66 | 0 | 0 | 0 | 90.8698 | 36.66 | 36.66
2025-01-26 22:00:00 | 30.12 | 0 | 0 | 0 | 90.8698 | 30.12 | 30.12
2025-01-26 23:00:00 | 25.26 | 0 | 0 | 0 | 90.8698 | 25.26 | 25.26
2025-01-27 00:00:00 | 25.62 | 0 | 0 | 0 | 90.8698 | 25.62 | 25.62
2025-01-27 01:00:00 | 23.94 | 0 | 0 | 0 | 90.8698 | 23.94 | 23.94
2025-01-27 02:00:00 | 21.78 | 0 | 0 | 0 | 90.8698 | 21.78 | 21.78
2025-01-27 03:00:00 | 22.86 | 0 | 0 | 0 | 90.8698 | 22.86 | 22.86
2025-01-27 04:00:00 | 22.14 | 0 | 75 | 0 | 156.8698 | 97.14 | 22.14
2025-01-27 05:00:00 | 21.72 | 0 | 75 | 0 | 222.8698 | 96.72 | 21.72
2025-01-27 06:00:00 | 22.86 | 0 | 75 | 0 | 288.8698 | 97.86 | 22.86
2025-01-27 07:00:00 | 21.96 | 0.78156 | 0 | 21.1784 | 267.6913 | -1.0658e-14 | 21.1784
2025-01-27 08:00:00 | 21.6 | 4.0483 | 0 | 17.5517 | 250.1396 | 3.5527e-15 | 17.5517
2025-01-27 09:00:00 | 22.32 | 6.7156 | 0 | 15.6044 | 234.5352 | -1.4211e-14 | 15.6044
2025-01-27 10:00:00 | 24.24 | 8.6017 | 0 | 15.6383 | 218.8969 | -3.3751e-14 | 15.6383
2025-01-27 11:00:00 | 24.78 | 9.578 | 0 | 15.202 | 203.6949 | -3.5527e-14 | 15.202
2025-01-27 12:00:00 | 24.24 | 9.578 | 0 | 14.662 | 189.0329 | -3.908e-14 | 14.662
2025-01-27 13:00:00 | 23.64 | 8.6017 | 0 | 15.0383 | 173.9945 | -3.1974e-14 | 15.0383
2025-01-27 14:00:00 | 24.12 | 6.7156 | 0 | 17.4044 | 156.5901 | -1.4211e-14 | 17.4044
2025-01-27 15:00:00 | 21.12 | 4.0483 | 0 | 17.0717 | 139.5184 | 0 | 17.0717
2025-01-27 16:00:00 | 22.2 | 0.78156 | 0 | 21.4184 | 118.1 | -1.0658e-14 | 21.4184
2025-01-27 17:00:00 | 21.3 | 0 | 0 | 21.3 | 96.8 | 0 | 21.3
2025-01-27 18:00:00 | 31.8 | 0 | 0 | 31.8 | 65 | 0 | 31.8
2025-01-27 19:00:00 | 32.88 | 0 | 0 | 0 | 65 | 32.88 | 32.88
2025-01-27 20:00:00 | 39.72 | 0 | 0 | 0 | 65 | 39.72 | 39.72
2025-01-27 21:00:00 | 39.9 | 0 | 0 | 0 | 65 | 39.9 | 39.9
2025-01-27 22:00:00 | 34.02 | 0 | 0 | 0 | 65 | 34.02 | 34.02
2025-01-27 23:00:00 | 30.72 | 0 | 0 | 0 | 65 | 30.72 | 30.72
2025-01-28 00:00:00 | 24.66 | 0 | 0 | 0 | 65 | 24.66 | 24.66
2025-01-28 01:00:00 | 25.62 | 0 | 0 | 0 | 65 | 25.62 | 25.62
2025-01-28 02:00:00 | 23.88 | 0 | 0 | 0 | 65 | 23.88 | 23.88
2025-01-28 03:00:00 | 22.26 | 0 | 57.3186 | 0 | 115.4404 | 79.5786 | 22.26
2025-01-28 04:00:00 | 22.44 | 0 | 75 | 0 | 181.4404 | 97.44 | 22.44
2025-01-28 05:00:00 | 22.2 | 0 | 75 | 0 | 247.4404 | 97.2 | 22.2
2025-01-28 06:00:00 | 22.08 | 0 | 75 | 0 | 313.4404 | 97.08 | 22.08
2025-01-28 07:00:00 | 22.44 | 0.84905 | 0 | 21.5909 | 291.8494 | 3.908e-14 | 21.5909
2025-01-28 08:00:00 | 28.08 | 4.1205 | 0 | 23.9595 | 267.8899 | -1.4211e-14 | 23.9595
2025-01-28 09:00:00 | 27.78 | 6.7917 | 0 | 20.9883 | 246.9016 | 3.1974e-14 | 20.9883
2025-01-28 10:00:00 | 25.38 | 8.6804 | 0 | 16.6996 | 230.202 | -1.0658e-14 | 16.6996
2025-01-28 11:00:00 | 24.72 | 9.6581 | 0 | 15.0619 | 215.1402 | 0 | 15.0619
2025-01-28 12:00:00 | 25.44 | 9.6581 | 0 | 15.7819 | 199.3583 | 1.7764e-15 | 15.7819
2025-01-28 13:00:00 | 22.56 | 8.6804 | 0 | 13.8796 | 185.4788 | -1.0658e-14 | 13.8796
2025-01-28 14:00:00 | 22.08 | 6.7917 | 0 | 15.2883 | 170.1904 | 2.8422e-14 | 15.2883
2025-01-28 15:00:00 | 22.26 | 4.1205 | 0 | 18.1395 | 152.0509 | -7.1054e-15 | 18.1395
2025-01-28 16:00:00 | 21.66 | 0.84905 | 0 | 20.8109 | 131.24 | 3.908e-14 | 20.8109
2025-01-28 17:00:00 | 30.48 | 0 | 0 | 30.48 | 100.76 | 0 | 30.48
2025-01-28 18:00:00 | 35.76 | 0 | 0 | 35.76 | 65 | 0 | 35.76
2025-01-28 19:00:00 | 31.44 | 0 | 0 | 0 | 65 | 31.44 | 31.44
2025-01-28 20:00:00 | 38.76 | 0 | 29.3128 | 0 | 90.7952 | 68.0728 | 38.76
2025-01-28 21:00:00 | 39.54 | 0 | 0 | 0 | 90.7952 | 39.54 | 39.54
2025-01-28 22:00:00 | 33.24 | 0 | 0 | 0 | 90.7952 | 33.24 | 33.24
2025-01-28 23:00:00 | 28.86 | 0 | 0 | 0 | 90.7952 | 28.86 | 28.86
2025-01-29 00:00:00 | 24.66 | 0 | 0 | 0 | 90.7952 | 24.66 | 24.66
2025-01-29 01:00:00 | 25.02 | 0 | 0 | 0 | 90.7952 | 25.02 | 25.02
2025-01-29 02:00:00 | 23.1 | 0 | 0 | 0 | 90.7952 | 23.1 | 23.1
2025-01-29 03:00:00 | 21.54 | 0 | 0 | 0 | 90.7952 | 21.54 | 21.54
2025-01-29 04:00:00 | 22.92 | 0 | 75 | 0 | 156.7952 | 97.92 | 22.92
2025-01-29 05:00:00 | 21.78 | 0 | 75 | 0 | 222.7952 | 96.78 | 21.78
2025-01-29 06:00:00 | 22.14 | 0 | 75 | 0 | 288.7952 | 97.14 | 22.14
2025-01-29 07:00:00 | 21.96 | 0.91805 | 0 | 21.0419 | 267.7533 | 1.4211e-14 | 21.0419
2025-01-29 08:00:00 | 25.02 | 4.1943 | 0 | 20.8257 | 246.9276 | 7.1054e-15 | 20.8257
2025-01-29 09:00:00 | 23.7 | 6.8693 | 0 | 16.8307 | 230.0969 | 4.9738e-14 | 16.8307
2025-01-29 10:00:00 | 21.54 | 8.7608 | 0 | 12.7792 | 217.3177 | 0 | 12.7792
2025-01-29 11:00:00 | 22.02 | 9.7399 | 0 | 12.2801 | 205.0376 | -4.4409e-14 | 12.2801
2025-01-29 12:00:00 | 24.12 | 9.7399 | 0 | 14.3801 | 190.6576 | -4.2633e-14 | 14.3801
2025-01-29 13:00:00 | 21.54 | 8.7608 | 0 | 12.7792 | 177.8784 | 0 | 12.7792
2025-01-29 14:00:00 | 21.06 | 6.8693 | 0 | 14.1907 | 163.6877 | 4.7962e-14 | 14.1907
2025-01-29 15:00:00 | 22.02 | 4.1943 | 0 | 17.8257 | 145.8619 | 7.1054e-15 | 17.8257
2025-01-29 16:00:00 | 21.42 | 0.91805 | 0 | 20.5019 | 125.36 | 1.4211e-14 | 20.5019
2025-01-29 17:00:00 | 27.9 | 0 | 0 | 27.9 | 97.46 | 0 | 27.9
2025-01-29 18:00:00 | 32.46 | 0 | 0 | 32.46 | 65 | 0 | 32.46
2025-01-29 19:00:00 | 33.12 | 0 | 75 | 0 | 131 | 108.12 | 33.12
2025-01-29 20:00:00 | 32.7 | 0 | 5.4485 | 0 | 135.7947 | 38.1485 | 32.7
2025-01-29 21:00:00 | 32.46 | 0 | 0 | 0 | 135.7947 | 32.46 | 32.46
2025-01-29 22:00:00 | 32.76 | 0 | 0 | 0 | 135.7947 | 32.76 | 32.76
2025-01-29 23:00:00 | 32.64 | 0 | 0 | 0 | 135.7947 | 32.64 | 32.64
2025-01-30 00:00:00 | 32.88 | 0 | 0 | 0 | 135.7947 | 32.88 | 32.88
2025-01-30 01:00:00 | 32.88 | 0 | 0 | 0 | 135.7947 | 32.88 | 32.88
2025-01-30 02:00:00 | 32.7 | 0 | 0 | 0 | 135.7947 | 32.7 | 32.7
2025-01-30 03:00:00 | 12.96 | 0 | 75 | 0 | 201.7947 | 87.96 | 12.96
2025-01-30 04:00:00 | 19.32 | 0 | 75 | 0 | 267.7947 | 94.32 | 19.32
2025-01-30 05:00:00 | 31.62 | 0 | 75 | 0 | 333.7947 | 106.62 | 31.62
2025-01-30 06:00:00 | 31.5 | 0 | 75 | 0 | 399.7947 | 106.5 | 31.5
2025-01-30 07:00:00 | 31.8 | 0.98853 | 0 | 30.8115 | 368.9832 | 3.5527e-15 | 30.8115
2025-01-30 08:00:00 | 30.9 | 4.2695 | 0 | 26.6305 | 342.3528 | -3.5527e-15 | 26.6305
2025-01-30 09:00:00 | 30.3 | 6.9485 | 0 | 23.3515 | 319.0013 | -7.1054e-15 | 23.3515
2025-01-30 10:00:00 | 30.48 | 8.8428 | 0 | 21.6372 | 297.364 | 3.5527e-14 | 21.6372
2025-01-30 11:00:00 | 30 | 9.8233 | 0 | 20.1767 | 277.1874 | 3.908e-14 | 20.1767
2025-01-30 12:00:00 | 29.4 | 9.8233 | 0 | 19.5767 | 257.6107 | 3.5527e-14 | 19.5767
2025-01-30 13:00:00 | 29.52 | 8.8428 | 0 | 20.6772 | 236.9334 | 3.5527e-14 | 20.6772
2025-01-30 14:00:00 | 30.9 | 6.9485 | 0 | 23.9515 | 212.9819 | -7.1054e-15 | 23.9515
2025-01-30 15:00:00 | 33.54 | 4.2695 | 0 | 29.2705 | 183.7115 | -3.5527e-15 | 29.2705
2025-01-30 16:00:00 | 42.9 | 0.98853 | 0 | 41.9115 | 141.8 | 9.9476e-14 | 41.9115
2025-01-30 17:00:00 | 41.4 | 0 | 0 | 41.4 | 100.4 | 0 | 41.4
2025-01-30 18:00:00 | 35.4 | 0 | 0 | 35.4 | 65 | 0 | 35.4
2025-01-30 19:00:00 | 26.7 | 0 | 73.3399 | 0 | 129.5391 | 100.0399 | 26.7
2025-01-30 20:00:00 | 23.64 | 0 | 0 | 0 | 129.5391 | 23.64 | 23.64
2025-01-30 21:00:00 | 24.48 | 0 | 0 | 0 | 129.5391 | 24.48 | 24.48
2025-01-30 22:00:00 | 23.52 | 0 | 0 | 0 | 129.5391 | 23.52 | 23.52
2025-01-30 23:00:00 | 20.34 | 0 | 0 | 0 | 129.5391 | 20.34 | 20.34
2025-01-31 00:00:00 | 21.12 | 0 | 0 | 0 | 129.5391 | 21.12 | 21.12
2025-01-31 01:00:00 | 21.18 | 0 | 0 | 0 | 129.5391 | 21.18 | 21.18
2025-01-31 02:00:00 | 20.7 | 0 | 0 | 0 | 129.5391 | 20.7 | 20.7
2025-01-31 03:00:00 | 20.82 | 0 | 0 | 0 | 129.5391 | 20.82 | 20.82
2025-01-31 04:00:00 | 21.66 | 0 | 75 | 0 | 195.5391 | 96.66 | 21.66
2025-01-31 05:00:00 | 20.88 | 0 | 75 | 0 | 261.5391 | 95.88 | 20.88
2025-01-31 06:00:00 | 20.4 | 0 | 75 | 0 | 327.5391 | 95.4 | 20.4
2025-01-31 07:00:00 | 21.3 | 1.0605 | 0 | 20.2395 | 307.2995 | -4.6185e-14 | 20.2395
2025-01-31 08:00:00 | 20.82 | 4.3463 | 0 | 16.4737 | 290.8258 | 4.2633e-14 | 16.4737
2025-01-31 09:00:00 | 20.88 | 7.0292 | 0 | 13.8508 | 276.975 | -2.1316e-14 | 13.8508
2025-01-31 10:00:00 | 20.34 | 8.9263 | 0 | 11.4137 | 265.5613 | 2.8422e-14 | 11.4137
2025-01-31 11:00:00 | 26.04 | 9.9083 | 0 | 16.1317 | 249.4295 | 7.1054e-15 | 16.1317
2025-01-31 12:00:00 | 30.72 | 9.9083 | 0 | 20.8117 | 228.6178 | 7.1054e-15 | 20.8117
2025-01-31 13:00:00 | 30.72 | 8.9263 | 0 | 21.7937 | 206.824 | 2.8422e-14 | 21.7937
2025-01-31 14:00:00 | 30.9 | 7.0292 | 0 | 23.8708 | 182.9532 | -2.1316e-14 | 23.8708
2025-01-31 15:00:00 | 36.9 | 4.3463 | 0 | 32.5537 | 150.3995 | 4.2633e-14 | 32.5537
2025-01-31 16:00:00 | 33.48 | 1.0605 | 0 | 32.4195 | 117.98 | -4.9738e-14 | 32.4195
2025-01-31 17:00:00 | 27.18 | 0 | 0 | 27.18 | 90.8 | 0 | 27.18
2025-01-31 18:00:00 | 25.8 | 0 | 0 | 25.8 | 65 | 0 | 25.8
2025-01-31 19:00:00 | 25.38 | 0 | 70.4545 | 0 | 127 | 95.8345 | 25.38
2025-01-31 20:00:00 | 23.7 | 0 | 75 | 0 | 193 | 98.7 | 23.7
2025-01-31 21:00:00 | 23.52 | 0 | 75 | 0 | 259 | 98.52 | 23.52
2025-01-31 22:00:00 | 22.68 | 0 | 75 | 0 | 325 | 97.68 | 22.68
2025-01-31 23:00:00 | 22.98 | 0 | 0 | 0 | 325 | 22.98 | 22.98
2025-02-01 00:00:00 | 24.18 | 0 | 0 | 0 | 325 | 24.18 | 24.18
2025-02-01 01:00:00 | 22.8 | 0 | 0 | 0 | 325 | 22.8 | 22.8
2025-02-01 02:00:00 | 23.1 | 0 | 0 | 0 | 325 | 23.1 | 23.1
2025-02-01 03:00:00 | 23.1 | 0 | 0 | 0 | 325 | 23.1 | 23.1
2025-02-01 04:00:00 | 23.76 | 0 | 0 | 0 | 325 | 23.76 | 23.76
2025-02-01 05:00:00 | 23.34 | 0 | 0 | 0 | 325 | 23.34 | 23.34
2025-02-01 06:00:00 | 23.16 | 0 | 0 | 0 | 325 | 23.16 | 23.16
2025-02-01 07:00:00 | 23.04 | 1.5622 | 0 | 0 | 325 | 21.4778 | 21.4778
2025-02-01 08:00:00 | 22.98 | 6.096 | 0 | 0 | 325 | 16.884 | 16.884
2025-02-01 09:00:00 | 22.92 | 9.7979 | 0 | 0 | 325 | 13.1221 | 13.1221
2025-02-01 10:00:00 | 23.16 | 12.4155 | 0 | 0 | 325 | 10.7445 | 10.7445
2025-02-01 11:00:00 | 23.28 | 13.7705 | 0 | 0 | 325 | 9.5095 | 9.5095
2025-02-01 12:00:00 | 22.8 | 13.7705 | 0 | 0 | 325 | 9.0295 | 9.0295
2025-02-01 13:00:00 | 22.44 | 12.4155 | 0 | 0 | 325 | 10.0245 | 10.0245
2025-02-01 14:00:00 | 22.5 | 9.7979 | 0 | 0 | 325 | 12.7021 | 12.7021
2025-02-01 15:00:00 | 22.74 | 6.096 | 0 | 0 | 325 | 16.644 | 16.644
2025-02-01 16:00:00 | 22.98 | 1.5622 | 0 | 0 | 325 | 21.4178 | 21.4178
2025-02-01 17:00:00 | 22.8 | 0 | 0 | 0 | 325 | 22.8 | 22.8
2025-02-01 18:00:00 | 22.44 | 0 | 0 | 0 | 325 | 22.44 | 22.44
2025-02-01 19:00:00 | 22.98 | 0 | 0 | 0 | 325 | 22.98 | 22.98
2025-02-01 20:00:00 | 23.58 | 0 | 0 | 0 | 325 | 23.58 | 23.58
2025-02-01 21:00:00 | 22.8 | 0 | 0 | 0 | 325 | 22.8 | 22.8
2025-02-01 22:00:00 | 23.58 | 0 | 0 | 0 | 325 | 23.58 | 23.58
2025-02-01 23:00:00 | 25.08 | 0 | 0 | 0 | 325 | 25.08 | 25.08
2025-02-02 00:00:00 | 24.3 | 0 | 0 | 0 | 325 | 24.3 | 24.3
2025-02-02 01:00:00 | 23.58 | 0 | 0 | 0 | 325 | 23.58 | 23.58
2025-02-02 02:00:00 | 22.98 | 0 | 0 | 0 | 325 | 22.98 | 22.98
2025-02-02 03:00:00 | 23.04 | 0 | 0 | 0 | 325 | 23.04 | 23.04
2025-02-02 04:00:00 | 23.04 | 0 | 0 | 0 | 325 | 23.04 | 23.04
2025-02-02 05:00:00 | 23.1 | 0 | 0 | 0 | 325 | 23.1 | 23.1
2025-02-02 06:00:00 | 23.1 | 0 | 0 | 0 | 325 | 23.1 | 23.1
2025-02-02 07:00:00 | 24.24 | 1.6652 | 0 | 0 | 325 | 22.5748 | 22.5748
2025-02-02 08:00:00 | 28.26 | 6.2058 | 0 | 0 | 325 | 22.0542 | 22.0542
2025-02-02 09:00:00 | 27.06 | 9.9131 | 0 | 0 | 325 | 17.1469 | 17.1469
2025-02-02 10:00:00 | 25.92 | 12.5346 | 0 | 0 | 325 | 13.3854 | 13.3854
2025-02-02 11:00:00 | 25.56 | 13.8916 | 0 | 0 | 325 | 11.6684 | 11.6684
2025-02-02 12:00:00 | 24.12 | 13.8916 | 0 | 0 | 325 | 10.2284 | 10.2284
2025-02-02 13:00:00 | 24.84 | 12.5346 | 0 | 0 | 325 | 12.3054 | 12.3054
2025-02-02 14:00:00 | 23.88 | 9.9131 | 0 | 0 | 325 | 13.9669 | 13.9669
2025-02-02 15:00:00 | 22.62 | 6.2058 | 0 | 0 | 325 | 16.4142 | 16.4142
2025-02-02 16:00:00 | 31.8 | 1.6652 | 0 | 0 | 325 | 30.1348 | 30.1348
2025-02-02 17:00:00 | 30.9 | 0 | 0 | 0 | 325 | 30.9 | 30.9
2025-02-02 18:00:00 | 30.96 | 0 | 0 | 0 | 325 | 30.96 | 30.96
2025-02-02 19:00:00 | 29.82 | 0 | 0 | 0 | 325 | 29.82 | 29.82
2025-02-02 20:00:00 | 34.8 | 0 | 0 | 0 | 325 | 34.8 | 34.8
2025-02-02 21:00:00 | 33.36 | 0 | 0 | 0 | 325 | 33.36 | 33.36
2025-02-02 22:00:00 | 28.74 | 0 | 0 | 0 | 325 | 28.74 | 28.74
2025-02-02 23:00:00 | 25.5 | 0 | 0 | 0 | 325 | 25.5 | 25.5
2025-02-03 00:00:00 | 25.5 | 0 | 0 | 0 | 325 | 25.5 | 25.5
2025-02-03 01:00:00 | 15.4282 | 0 | 0 | 0 | 325 | 15.4282 | 15.4282
2025-02-03 02:00:00 | 6.2564 | 0 | 0 | 0 | 325 | 6.2564 | 6.2564
2025-02-03 03:00:00 | 6.2564 | 0 | 0 | 0 | 325 | 6.2564 | 6.2564
2025-02-03 04:00:00 | 6.2564 | 0 | 0 | 0 | 325 | 6.2564 | 6.2564
2025-02-03 05:00:00 | 6.2564 | 0 | 0 | 0 | 325 | 6.2564 | 6.2564
2025-02-03 06:00:00 | 6.2564 | 0 | 0 | 0 | 325 | 6.2564 | 6.2564
2025-02-03 07:00:00 | 6.2564 | 1.7701 | 0 | 4.4863 | 320.5137 | -4.4409e-15 | 4.4863
2025-02-03 08:00:00 | 6.2564 | 6.3174 | 0 | 0 | 320.5137 | -0.061023 | -0.061023
2025-02-03 09:00:00 | 6.2564 | 10.0303 | 0 | 0 | 320.5137 | -3.7739 | -3.7739
2025-02-03 10:00:00 | 6.2564 | 12.6557 | 0 | 0 | 320.5137 | -6.3993 | -6.3993
2025-02-03 11:00:00 | 6.2564 | 14.0147 | 0 | 0 | 320.5137 | -7.7583 | -7.7583
2025-02-03 12:00:00 | 6.2564 | 14.0147 | 0 | 0 | 320.5137 | -7.7583 | -7.7583
2025-02-03 13:00:00 | 6.2564 | 12.6557 | 0 | 0 | 320.5137 | -6.3993 | -6.3993
2025-02-03 14:00:00 | 6.2564 | 10.0303 | 0 | 0 | 320.5137 | -3.7739 | -3.7739
2025-02-03 15:00:00 | 6.2564 | 6.3174 | 0 | 0 | 320.5137 | -0.061023 | -0.061023
2025-02-03 16:00:00 | 6.2564 | 1.7701 | 0 | 4.4863 | 316.0275 | -4.4409e-15 | 4.4863
2025-02-03 17:00:00 | 6.2564 | 0 | 0 | 6.2564 | 309.7711 | 0 | 6.2564
2025-02-03 18:00:00 | 6.2564 | 0 | 0 | 6.2564 | 303.5147 | 0 | 6.2564
2025-02-03 19:00:00 | 6.2564 | 0 | 0 | 0 | 303.5147 | 6.2564 | 6.2564
2025-02-03 20:00:00 | 6.2564 | 0 | 0 | 0 | 303.5147 | 6.2564 | 6.2564
2025-02-03 21:00:00 | 6.2564 | 0 | 0 | 0 | 303.5147 | 6.2564 | 6.2564
2025-02-03 22:00:00 | 6.2564 | 0 | 0 | 0 | 303.5147 | 6.2564 | 6.2564
2025-02-03 23:00:00 | 6.2564 | 0 | 0 | 0 | 303.5147 | 6.2564 | 6.2564
2025-02-04 00:00:00 | 47.42 | 0 | 62.26 | 0 | 358.3035 | 109.68 | 47.42
2025-02-04 01:00:00 | 47.42 | 0 | 62.26 | 0 | 413.0923 | 109.68 | 47.42
2025-02-04 02:00:00 | 47.42 | 0 | 0 | 0 | 413.0923 | 47.42 | 47.42
2025-02-04 03:00:00 | 47.42 | 0 | 0 | 0 | 413.0923 | 47.42 | 47.42
2025-02-04 04:00:00 | 47.42 | 0 | 62.26 | 0 | 467.8811 | 109.68 | 47.42
2025-02-04 05:00:00 | 47.42 | 0 | 27.6307 | 0 | 492.1961 | 75.0507 | 47.42
2025-02-04 06:00:00 | 47.42 | 0 | 62.26 | 0 | 546.9849 | 109.68 | 47.42
2025-02-04 07:00:00 | 47.42 | 1.8769 | 0 | 45.5431 | 501.4418 | -2.8422e-14 | 45.5431
2025-02-04 08:00:00 | 47.42 | 6.431 | 0 | 40.989 | 460.4528 | 2.1316e-14 | 40.989
2025-02-04 09:00:00 | 47.42 | 10.1493 | 0 | 37.2707 | 423.1821 | -3.5527e-14 | 37.2707
2025-02-04 10:00:00 | 47.42 | 12.7786 | 0 | 34.6414 | 388.5407 | -4.9738e-14 | 34.6414
2025-02-04 11:00:00 | 47.42 | 14.1396 | 0 | 33.2804 | 355.2604 | 1.4211e-14 | 33.2804
2025-02-04 12:00:00 | 47.42 | 14.1396 | 0 | 33.2804 | 321.98 | 1.4211e-14 | 33.2804
2025-02-04 13:00:00 | 47.42 | 12.7786 | 0 | 34.6414 | 287.3386 | -4.9738e-14 | 34.6414
2025-02-04 14:00:00 | 47.42 | 10.1493 | 0 | 37.2707 | 250.068 | -3.5527e-14 | 37.2707
2025-02-04 15:00:00 | 47.42 | 6.431 | 0 | 40.989 | 209.0789 | 2.1316e-14 | 40.989
2025-02-04 16:00:00 | 47.42 | 1.8769 | 0 | 45.5431 | 163.5359 | -2.8422e-14 | 45.5431
2025-02-04 17:00:00 | 47.42 | 0 | 0 | 47.42 | 116.1159 | 0 | 47.42
2025-02-04 18:00:00 | 47.42 | 0 | 0 | 47.42 | 68.6959 | 0 | 47.42
2025-02-04 19:00:00 | 47.42 | 0 | 0 | 0 | 68.6959 | 47.42 | 47.42
2025-02-04 20:00:00 | 47.42 | 0 | 0 | 0 | 68.6959 | 47.42 | 47.42
2025-02-04 21:00:00 | 47.42 | 0 | 0 | 0 | 68.6959 | 47.42 | 47.42
2025-02-04 22:00:00 | 47.42 | 0 | 0 | 0 | 68.6959 | 47.42 | 47.42
2025-02-04 23:00:00 | 47.42 | 0 | 0 | 0 | 68.6959 | 47.42 | 47.42
2025-02-05 00:00:00 | 24.84 | 0 | 0 | 0 | 68.6959 | 24.84 | 24.84
2025-02-05 01:00:00 | 22.32 | 0 | 0 | 0 | 68.6959 | 22.32 | 22.32
2025-02-05 02:00:00 | 23.76 | 0 | 0 | 0 | 68.6959 | 23.76 | 23.76
2025-02-05 03:00:00 | 22.56 | 0 | 75 | 0 | 134.6959 | 97.56 | 22.56
2025-02-05 04:00:00 | 23.4 | 0 | 75 | 0 | 200.6959 | 98.4 | 23.4
2025-02-05 05:00:00 | 23.28 | 0 | 75 | 0 | 266.6959 | 98.28 | 23.28
2025-02-05 06:00:00 | 22.56 | 0 | 75 | 0 | 332.6959 | 97.56 | 22.56
2025-02-05 07:00:00 | 23.4 | 1.9856 | 0 | 21.4144 | 311.2814 | 1.0658e-14 | 21.4144
2025-02-05 08:00:00 | 24.48 | 6.5464 | 0 | 17.9336 | 293.3478 | 3.908e-14 | 17.9336
2025-02-05 09:00:00 | 23.64 | 10.2702 | 0 | 13.3698 | 279.978 | -1.5987e-14 | 13.3698
2025-02-05 10:00:00 | 22.08 | 12.9034 | 0 | 9.1766 | 270.8015 | -1.7764e-15 | 9.1766
2025-02-05 11:00:00 | 22.56 | 14.2665 | 0 | 8.2935 | 262.5079 | -3.5527e-15 | 8.2935
2025-02-05 12:00:00 | 22.68 | 14.2665 | 0 | 8.4135 | 254.0944 | -3.5527e-15 | 8.4135
2025-02-05 13:00:00 | 22.2 | 12.9034 | 0 | 9.2966 | 244.7978 | 0 | 9.2966
2025-02-05 14:00:00 | 22.68 | 10.2702 | 0 | 12.4098 | 232.3881 | -1.5987e-14 | 12.4098
2025-02-05 15:00:00 | 33.96 | 6.5464 | 0 | 27.4136 | 204.9744 | 3.908e-14 | 27.4136
2025-02-05 16:00:00 | 48 | 1.9856 | 0 | 46.0144 | 158.96 | 1.4211e-14 | 46.0144
2025-02-05 17:00:00 | 47.52 | 0 | 0 | 47.52 | 111.44 | 0 | 47.52
2025-02-05 18:00:00 | 46.44 | 0 | 0 | 46.44 | 65 | 0 | 46.44
2025-02-05 19:00:00 | 37.44 | 0 | 0 | 0 | 65 | 37.44 | 37.44
2025-02-05 20:00:00 | 30.48 | 0 | 0 | 0 | 65 | 30.48 | 30.48
2025-02-05 21:00:00 | 32.88 | 0 | 0 | 0 | 65 | 32.88 | 32.88
2025-02-05 22:00:00 | 32.16 | 0 | 0 | 0 | 65 | 32.16 | 32.16
2025-02-05 23:00:00 | 26.04 | 0 | 0 | 0 | 65 | 26.04 | 26.04
2025-02-06 00:00:00 | 25.32 | 0 | 0 | 0 | 65 | 25.32 | 25.32
2025-02-06 01:00:00 | 23.52 | 0 | 0 | 0 | 65 | 23.52 | 23.52
2025-02-06 02:00:00 | 23.04 | 0 | 53.1418 | 0 | 111.7648 | 76.1818 | 23.04
2025-02-06 03:00:00 | 22.32 | 0 | 75 | 0 | 177.7648 | 97.32 | 22.32
2025-02-06 04:00:00 | 22.68 | 0 | 75 | 0 | 243.7648 | 97.68 | 22.68
2025-02-06 05:00:00 | 23.04 | 0 | 75 | 0 | 309.7648 | 98.04 | 23.04
2025-02-06 06:00:00 | 23.64 | 0 | 75 | 0 | 375.7648 | 98.64 | 23.64
2025-02-06 07:00:00 | 23.64 | 2.096 | 0 | 21.544 | 354.2208 | -4.2633e-14 | 21.544
2025-02-06 08:00:00 | 23.64 | 6.6635 | 0 | 16.9765 | 337.2443 | 2.4869e-14 | 16.9765
2025-02-06 09:00:00 | 21.96 | 10.3929 | 0 | 11.5671 | 325.6773 | -3.5527e-14 | 11.5671
2025-02-06 10:00:00 | 22.32 | 13.03 | 0 | 9.29 | 316.3873 | 3.5527e-15 | 9.29
2025-02-06 11:00:00 | 21.84 | 14.3951 | 0 | 7.4449 | 308.9424 | -3.5527e-15 | 7.4449
2025-02-06 12:00:00 | 23.04 | 14.3951 | 0 | 8.6449 | 300.2975 | -5.3291e-15 | 8.6449
2025-02-06 13:00:00 | 22.2 | 13.03 | 0 | 9.17 | 291.1275 | 3.5527e-15 | 9.17
2025-02-06 14:00:00 | 33.84 | 10.3929 | 0 | 23.4471 | 267.6805 | -3.1974e-14 | 23.4471
2025-02-06 15:00:00 | 49.08 | 6.6635 | 0 | 42.4165 | 225.264 | 2.8422e-14 | 42.4165
2025-02-06 16:00:00 | 55.2 | 2.096 | 0 | 53.104 | 172.16 | -4.2633e-14 | 53.104
2025-02-06 17:00:00 | 55.32 | 0 | 0 | 55.32 | 116.84 | 0 | 55.32
2025-02-06 18:00:00 | 51.84 | 0 | 0 | 51.84 | 65 | 0 | 51.84
2025-02-06 19:00:00 | 45.84 | 0 | 0 | 0 | 65 | 45.84 | 45.84
2025-02-06 20:00:00 | 28.56 | 0 | 0 | 0 | 65 | 28.56 | 28.56
2025-02-06 21:00:00 | 25.44 | 0 | 0 | 0 | 65 | 25.44 | 25.44
2025-02-06 22:00:00 | 22.8 | 0 | 0 | 0 | 65 | 22.8 | 22.8
2025-02-06 23:00:00 | 23.52 | 0 | 0 | 0 | 65 | 23.52 | 23.52
2025-02-07 00:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-02-07 01:00:00 | 23.4 | 0 | 0 | 0 | 65 | 23.4 | 23.4
2025-02-07 02:00:00 | 23.4 | 0 | 0 | 0 | 65 | 23.4 | 23.4
2025-02-07 03:00:00 | 22.56 | 0 | 64.0185 | 0 | 121.3363 | 86.5785 | 22.56
2025-02-07 04:00:00 | 22.92 | 0 | 75 | 0 | 187.3363 | 97.92 | 22.92
2025-02-07 05:00:00 | 23.4 | 0 | 75 | 0 | 253.3363 | 98.4 | 23.4
2025-02-07 06:00:00 | 23.4 | 0 | 75 | 0 | 319.3363 | 98.4 | 23.4
2025-02-07 07:00:00 | 22.68 | 2.2082 | 0 | 20.4718 | 298.8645 | 2.4869e-14 | 20.4718
2025-02-07 08:00:00 | 23.4 | 6.7825 | 0 | 16.6175 | 282.247 | -7.1054e-15 | 16.6175
2025-02-07 09:00:00 | 22.92 | 10.5174 | 0 | 12.4026 | 269.8443 | -4.6185e-14 | 12.4026
2025-02-07 10:00:00 | 28.44 | 13.1584 | 0 | 15.2816 | 254.5627 | 2.1316e-14 | 15.2816
2025-02-07 11:00:00 | 31.92 | 14.5254 | 0 | 17.3946 | 237.1682 | 2.8422e-14 | 17.3946
2025-02-07 12:00:00 | 31.68 | 14.5254 | 0 | 17.1546 | 220.0136 | 2.4869e-14 | 17.1546
2025-02-07 13:00:00 | 32.04 | 13.1584 | 0 | 18.8816 | 201.132 | 2.1316e-14 | 18.8816
2025-02-07 14:00:00 | 31.56 | 10.5174 | 0 | 21.0426 | 180.0894 | -4.9738e-14 | 21.0426
2025-02-07 15:00:00 | 35.4 | 6.7825 | 0 | 28.6175 | 151.4718 | -7.1054e-15 | 28.6175
2025-02-07 16:00:00 | 32.88 | 2.2082 | 0 | 30.6718 | 120.8 | 2.8422e-14 | 30.6718
2025-02-07 17:00:00 | 27 | 0 | 0 | 27 | 93.8 | 0 | 27
2025-02-07 18:00:00 | 28.8 | 0 | 0 | 28.8 | 65 | 0 | 28.8
2025-02-07 19:00:00 | 37.92 | 0 | 0 | 0 | 65 | 37.92 | 37.92
2025-02-07 20:00:00 | 33.6 | 0 | 0 | 0 | 65 | 33.6 | 33.6
2025-02-07 21:00:00 | 33.12 | 0 | 0 | 0 | 65 | 33.12 | 33.12
2025-02-07 22:00:00 | 33.24 | 0 | 0 | 0 | 65 | 33.24 | 33.24
2025-02-07 23:00:00 | 29.64 | 0 | 0 | 0 | 65 | 29.64 | 29.64
2025-02-08 00:00:00 | 24.72 | 0 | 0 | 0 | 65 | 24.72 | 24.72
2025-02-08 01:00:00 | 26.16 | 0 | 0 | 0 | 65 | 26.16 | 26.16
2025-02-08 02:00:00 | 24.6 | 0 | 0 | 0 | 65 | 24.6 | 24.6
2025-02-08 03:00:00 | 25.44 | 0 | 0 | 0 | 65 | 25.44 | 25.44
2025-02-08 04:00:00 | 24.6 | 0 | 0 | 0 | 65 | 24.6 | 24.6
2025-02-08 05:00:00 | 24.36 | 0 | 0 | 0 | 65 | 24.36 | 24.36
2025-02-08 06:00:00 | 25.32 | 0 | 0 | 0 | 65 | 25.32 | 25.32
2025-02-08 07:00:00 | 24.84 | 2.3221 | 0 | 0 | 65 | 22.5179 | 22.5179
2025-02-08 08:00:00 | 24.12 | 6.9031 | 0 | 0 | 65 | 17.2169 | 17.2169
2025-02-08 09:00:00 | 29.16 | 10.6435 | 0 | 0 | 65 | 18.5165 | 18.5165
2025-02-08 10:00:00 | 32.88 | 13.2884 | 0 | 0 | 65 | 19.5916 | 19.5916
2025-02-08 11:00:00 | 30.72 | 14.6575 | 0 | 0 | 65 | 16.0625 | 16.0625
2025-02-08 12:00:00 | 27.12 | 14.6575 | 0 | 0 | 65 | 12.4625 | 12.4625
2025-02-08 13:00:00 | 26.76 | 13.2884 | 0 | 0 | 65 | 13.4716 | 13.4716
2025-02-08 14:00:00 | 24 | 10.6435 | 0 | 0 | 65 | 13.3565 | 13.3565
2025-02-08 15:00:00 | 24.84 | 6.9031 | 0 | 0 | 65 | 17.9369 | 17.9369
2025-02-08 16:00:00 | 24.24 | 2.3221 | 0 | 0 | 65 | 21.9179 | 21.9179
2025-02-08 17:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-02-08 18:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-02-08 19:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-02-08 20:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-02-08 21:00:00 | 22.8 | 0 | 0 | 0 | 65 | 22.8 | 22.8
2025-02-08 22:00:00 | 24.12 | 0 | 0 | 0 | 65 | 24.12 | 24.12
2025-02-08 23:00:00 | 22.92 | 0 | 0 | 0 | 65 | 22.92 | 22.92
2025-02-09 00:00:00 | 22.92 | 0 | 0 | 0 | 65 | 22.92 | 22.92
2025-02-09 01:00:00 | 23.04 | 0 | 0 | 0 | 65 | 23.04 | 23.04
2025-02-09 02:00:00 | 23.76 | 0 | 0 | 0 | 65 | 23.76 | 23.76
2025-02-09 03:00:00 | 23.04 | 0 | 0 | 0 | 65 | 23.04 | 23.04
2025-02-09 04:00:00 | 23.28 | 0 | 0 | 0 | 65 | 23.28 | 23.28
2025-02-09 05:00:00 | 23.76 | 0 | 0 | 0 | 65 | 23.76 | 23.76
2025-02-09 06:00:00 | 22.92 | 0 | 0 | 0 | 65 | 22.92 | 22.92
2025-02-09 07:00:00 | 23.28 | 2.4376 | 0 | 0 | 65 | 20.8424 | 20.8424
2025-02-09 08:00:00 | 24.24 | 7.0254 | 0 | 0 | 65 | 17.2146 | 17.2146
2025-02-09 09:00:00 | 22.68 | 10.7713 | 0 | 0 | 65 | 11.9087 | 11.9087
2025-02-09 10:00:00 | 22.68 | 13.42 | 0 | 0 | 65 | 9.26 | 9.26
2025-02-09 11:00:00 | 23.4 | 14.7911 | 0 | 0 | 65 | 8.6089 | 8.6089
2025-02-09 12:00:00 | 22.68 | 14.7911 | 0 | 0 | 65 | 7.8889 | 7.8889
2025-02-09 13:00:00 | 22.8 | 13.42 | 0 | 0 | 65 | 9.38 | 9.38
2025-02-09 14:00:00 | 22.32 | 10.7713 | 0 | 0 | 65 | 11.5487 | 11.5487
2025-02-09 15:00:00 | 22.92 | 7.0254 | 0 | 0 | 65 | 15.8946 | 15.8946
2025-02-09 16:00:00 | 22.68 | 2.4376 | 0 | 0 | 65 | 20.2424 | 20.2424
2025-02-09 17:00:00 | 22.56 | 0 | 0 | 0 | 65 | 22.56 | 22.56
2025-02-09 18:00:00 | 36.36 | 0 | 0 | 0 | 65 | 36.36 | 36.36
2025-02-09 19:00:00 | 33 | 0 | 0 | 0 | 65 | 33 | 33
2025-02-09 20:00:00 | 40.68 | 0 | 0 | 0 | 65 | 40.68 | 40.68
2025-02-09 21:00:00 | 40.68 | 0 | 0 | 0 | 65 | 40.68 | 40.68
2025-02-09 22:00:00 | 32.64 | 0 | 0 | 0 | 65 | 32.64 | 32.64
2025-02-09 23:00:00 | 25.92 | 0 | 0 | 0 | 65 | 25.92 | 25.92
2025-02-10 00:00:00 | 25.8 | 0 | 0 | 0 | 65 | 25.8 | 25.8
2025-02-10 01:00:00 | 23.4 | 0 | 0 | 0 | 65 | 23.4 | 23.4
2025-02-10 02:00:00 | 23.04 | 0 | 29.3086 | 0 | 90.7916 | 52.3486 | 23.04
2025-02-10 03:00:00 | 22.8 | 0 | 75 | 0 | 156.7916 | 97.8 | 22.8
2025-02-10 04:00:00 | 23.04 | 0 | 75 | 0 | 222.7916 | 98.04 | 23.04
2025-02-10 05:00:00 | 22.68 | 0 | 75 | 0 | 288.7916 | 97.68 | 22.68
2025-02-10 06:00:00 | 22.8 | 0 | 75 | 0 | 354.7916 | 97.8 | 22.8
2025-02-10 07:00:00 | 23.16 | 2.5549 | 0 | 20.6051 | 334.1864 | 1.7764e-14 | 20.6051
2025-02-10 08:00:00 | 22.32 | 7.1493 | 0 | 15.1707 | 319.0157 | -5.3291e-15 | 15.1707
2025-02-10 09:00:00 | 28.56 | 10.9006 | 0 | 17.6594 | 301.3563 | -2.1316e-14 | 17.6594
2025-02-10 10:00:00 | 26.76 | 13.5532 | 0 | 13.2068 | 288.1495 | -2.8422e-14 | 13.2068
2025-02-10 11:00:00 | 24.72 | 14.9263 | 0 | 9.7937 | 278.3558 | 0 | 9.7937
2025-02-10 12:00:00 | 26.04 | 14.9263 | 0 | 11.1137 | 267.2421 | 1.0658e-14 | 11.1137
2025-02-10 13:00:00 | 25.08 | 13.5532 | 0 | 11.5268 | 255.7153 | -3.1974e-14 | 11.5268
2025-02-10 14:00:00 | 28.68 | 10.9006 | 0 | 17.7794 | 237.9359 | -2.4869e-14 | 17.7794
2025-02-10 15:00:00 | 43.8 | 7.1493 | 0 | 36.6507 | 201.2851 | -1.4211e-14 | 36.6507
2025-02-10 16:00:00 | 46.92 | 2.5549 | 0 | 44.3651 | 156.92 | 2.1316e-14 | 44.3651
2025-02-10 17:00:00 | 47.04 | 0 | 0 | 47.04 | 109.88 | 0 | 47.04
2025-02-10 18:00:00 | 44.88 | 0 | 0 | 44.88 | 65 | 0 | 44.88
2025-02-10 19:00:00 | 42 | 0 | 0 | 0 | 65 | 42 | 42
2025-02-10 20:00:00 | 45.36 | 0 | 0 | 0 | 65 | 45.36 | 45.36
2025-02-10 21:00:00 | 48.84 | 0 | 0 | 0 | 65 | 48.84 | 48.84
2025-02-10 22:00:00 | 46.92 | 0 | 0 | 0 | 65 | 46.92 | 46.92
2025-02-10 23:00:00 | 32.52 | 0 | 0 | 0 | 65 | 32.52 | 32.52
2025-02-11 00:00:00 | 25.68 | 0 | 0 | 0 | 65 | 25.68 | 25.68
2025-02-11 01:00:00 | 23.28 | 0 | 0 | 0 | 65 | 23.28 | 23.28
2025-02-11 02:00:00 | 22.92 | 0 | 70.9358 | 0 | 127.4235 | 93.8558 | 22.92
2025-02-11 03:00:00 | 34.8 | 0 | 74.88 | 0 | 193.3179 | 109.68 | 34.8
2025-02-11 04:00:00 | 39.6 | 0 | 70.08 | 0 | 254.9883 | 109.68 | 39.6
2025-02-11 05:00:00 | 38.4 | 0 | 71.28 | 0 | 317.7147 | 109.68 | 38.4
2025-02-11 06:00:00 | 35.88 | 0 | 73.8 | 0 | 382.6587 | 109.68 | 35.88
2025-02-11 07:00:00 | 22.92 | 2.6737 | 0 | 20.2463 | 362.4124 | -1.7764e-14 | 20.2463
2025-02-11 08:00:00 | 30.84 | 7.2747 | 0 | 23.5653 | 338.8471 | -3.5527e-15 | 23.5653
2025-02-11 09:00:00 | 45.24 | 11.0315 | 0 | 34.2085 | 304.6385 | -3.5527e-14 | 34.2085
2025-02-11 10:00:00 | 53.4 | 13.6879 | 0 | 39.7121 | 264.9264 | -2.8422e-14 | 39.7121
2025-02-11 11:00:00 | 46.8 | 15.0629 | 0 | 31.7371 | 233.1893 | 3.908e-14 | 31.7371
2025-02-11 12:00:00 | 43.56 | 15.0629 | 0 | 28.4971 | 204.6923 | 4.2633e-14 | 28.4971
2025-02-11 13:00:00 | 40.68 | 13.6879 | 0 | 26.9921 | 177.7001 | -2.4869e-14 | 26.9921
2025-02-11 14:00:00 | 39.6 | 11.0315 | 0 | 28.5685 | 149.1316 | -3.908e-14 | 28.5685
2025-02-11 15:00:00 | 26.88 | 7.2747 | 0 | 19.6053 | 129.5263 | -3.5527e-15 | 19.6053
2025-02-11 16:00:00 | 22.32 | 2.6737 | 0 | 19.6463 | 109.88 | -2.1316e-14 | 19.6463
2025-02-11 17:00:00 | 22.44 | 0 | 0 | 22.44 | 87.44 | 0 | 22.44
2025-02-11 18:00:00 | 22.44 | 0 | 0 | 22.44 | 65 | 0 | 22.44
2025-02-11 19:00:00 | 24.24 | 0 | 0 | 0 | 65 | 24.24 | 24.24
2025-02-11 20:00:00 | 48.36 | 0 | 0 | 0 | 65 | 48.36 | 48.36
2025-02-11 21:00:00 | 48.72 | 0 | 0 | 0 | 65 | 48.72 | 48.72
2025-02-11 22:00:00 | 47.16 | 0 | 0 | 0 | 65 | 47.16 | 47.16
2025-02-11 23:00:00 | 31.68 | 0 | 0 | 0 | 65 | 31.68 | 31.68
2025-02-12 00:00:00 | 23.64 | 0 | 0 | 0 | 65 | 23.64 | 23.64
2025-02-12 01:00:00 | 23.16 | 0 | 0 | 0 | 65 | 23.16 | 23.16
2025-02-12 02:00:00 | 22.08 | 0 | 26.7625 | 0 | 88.551 | 48.8425 | 22.08
2025-02-12 03:00:00 | 22.8 | 0 | 75 | 0 | 154.551 | 97.8 | 22.8
2025-02-12 04:00:00 | 22.32 | 0 | 75 | 0 | 220.551 | 97.32 | 22.32
2025-02-12 05:00:00 | 22.44 | 0 | 75 | 0 | 286.551 | 97.44 | 22.44
2025-02-12 06:00:00 | 22.68 | 0 | 75 | 0 | 352.551 | 97.68 | 22.68
2025-02-12 07:00:00 | 22.32 | 2.794 | 0 | 19.526 | 333.0251 | 7.1054e-15 | 19.526
2025-02-12 08:00:00 | 22.44 | 7.4017 | 0 | 15.0383 | 317.9867 | -1.0658e-14 | 15.0383
2025-02-12 09:00:00 | 22.92 | 11.1638 | 0 | 11.7562 | 306.2305 | 4.7962e-14 | 11.7562
2025-02-12 10:00:00 | 24.84 | 13.824 | 0 | 11.016 | 295.2145 | 2.6645e-14 | 11.016
2025-02-12 11:00:00 | 21.72 | 15.201 | 0 | 6.519 | 288.6955 | -1.7764e-15 | 6.519
2025-02-12 12:00:00 | 22.92 | 15.201 | 0 | 7.719 | 280.9765 | 8.8818e-16 | 7.719
2025-02-12 13:00:00 | 36.6 | 13.824 | 0 | 22.776 | 258.2005 | 2.8422e-14 | 22.776
2025-02-12 14:00:00 | 39.36 | 11.1638 | 0 | 28.1962 | 230.0043 | 4.6185e-14 | 28.1962
2025-02-12 15:00:00 | 39.72 | 7.4017 | 0 | 32.3183 | 197.686 | -7.1054e-15 | 32.3183
2025-02-12 16:00:00 | 46.8 | 2.794 | 0 | 44.006 | 153.68 | 7.1054e-15 | 44.006
2025-02-12 17:00:00 | 45.12 | 0 | 0 | 45.12 | 108.56 | 0 | 45.12
2025-02-12 18:00:00 | 43.56 | 0 | 0 | 43.56 | 65 | 0 | 43.56
2025-02-12 19:00:00 | 42 | 0 | 0 | 0 | 65 | 42 | 42
2025-02-12 20:00:00 | 41.52 | 0 | 0 | 0 | 65 | 41.52 | 41.52
2025-02-12 21:00:00 | 32.64 | 0 | 0 | 0 | 65 | 32.64 | 32.64
2025-02-12 22:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-02-12 23:00:00 | 23.04 | 0 | 0 | 0 | 65 | 23.04 | 23.04
2025-02-13 00:00:00 | 22.92 | 0 | 0 | 0 | 65 | 22.92 | 22.92
2025-02-13 01:00:00 | 22.2 | 0 | 0 | 0 | 65 | 22.2 | 22.2
2025-02-13 02:00:00 | 23.64 | 0 | 38.215 | 0 | 98.6292 | 61.855 | 23.64
2025-02-13 03:00:00 | 23.88 | 0 | 75 | 0 | 164.6292 | 98.88 | 23.88
2025-02-13 04:00:00 | 22.32 | 0 | 75 | 0 | 230.6292 | 97.32 | 22.32
2025-02-13 05:00:00 | 22.68 | 0 | 75 | 0 | 296.6292 | 97.68 | 22.68
2025-02-13 06:00:00 | 22.2 | 0 | 75 | 0 | 362.6292 | 97.2 | 22.2
2025-02-13 07:00:00 | 22.92 | 2.9159 | 0 | 20.0041 | 342.6251 | -3.5527e-15 | 20.0041
2025-02-13 08:00:00 | 22.8 | 7.5301 | 0 | 15.2699 | 327.3551 | 1.4211e-14 | 15.2699
2025-02-13 09:00:00 | 24 | 11.2975 | 0 | 12.7025 | 314.6526 | 3.1974e-14 | 12.7025
2025-02-13 10:00:00 | 22.92 | 13.9615 | 0 | 8.9585 | 305.6941 | 3.5527e-15 | 8.9585
2025-02-13 11:00:00 | 22.56 | 15.3405 | 0 | 7.2195 | 298.4746 | -4.4409e-15 | 7.2195
2025-02-13 12:00:00 | 22.8 | 15.3405 | 0 | 7.4595 | 291.015 | -1.7764e-15 | 7.4595
2025-02-13 13:00:00 | 29.28 | 13.9615 | 0 | 15.3185 | 275.6965 | -4.7962e-14 | 15.3185
2025-02-13 14:00:00 | 42.24 | 11.2975 | 0 | 30.9425 | 244.754 | 3.1974e-14 | 30.9425
2025-02-13 15:00:00 | 46.44 | 7.5301 | 0 | 38.9099 | 205.8441 | 1.4211e-14 | 38.9099
2025-02-13 16:00:00 | 50.28 | 2.9159 | 0 | 47.3641 | 158.48 | -7.1054e-15 | 47.3641
2025-02-13 17:00:00 | 50.16 | 0 | 0 | 50.16 | 108.32 | 0 | 50.16
2025-02-13 18:00:00 | 43.32 | 0 | 0 | 43.32 | 65 | 0 | 43.32
2025-02-13 19:00:00 | 41.4 | 0 | 0 | 0 | 65 | 41.4 | 41.4
2025-02-13 20:00:00 | 40.44 | 0 | 0 | 0 | 65 | 40.44 | 40.44
2025-02-13 21:00:00 | 31.08 | 0 | 0 | 0 | 65 | 31.08 | 31.08
2025-02-13 22:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-02-13 23:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-02-14 00:00:00 | 22.56 | 0 | 0 | 0 | 65 | 22.56 | 22.56
2025-02-14 01:00:00 | 22.44 | 0 | 38.3773 | 0 | 98.7721 | 60.8173 | 22.44
2025-02-14 02:00:00 | 34.8 | 0 | 74.88 | 0 | 164.6665 | 109.68 | 34.8
2025-02-14 03:00:00 | 38.76 | 0 | 70.92 | 0 | 227.0761 | 109.68 | 38.76
2025-02-14 04:00:00 | 38.16 | 0 | 71.52 | 0 | 290.0137 | 109.68 | 38.16
2025-02-14 05:00:00 | 28.2 | 0 | 75 | 0 | 356.0137 | 103.2 | 28.2
2025-02-14 06:00:00 | 22.32 | 0 | 75 | 0 | 422.0137 | 97.32 | 22.32
2025-02-14 07:00:00 | 21.96 | 3.0393 | 0 | 18.9207 | 403.0929 | 4.9738e-14 | 18.9207
2025-02-14 08:00:00 | 21.96 | 7.6599 | 0 | 14.3001 | 388.7928 | -1.0658e-14 | 14.3001
2025-02-14 09:00:00 | 27.12 | 11.4326 | 0 | 15.6874 | 373.1054 | -2.8422e-14 | 15.6874
2025-02-14 10:00:00 | 39.48 | 14.1003 | 0 | 25.3797 | 347.7256 | 4.2633e-14 | 25.3797
2025-02-14 11:00:00 | 39.96 | 15.4812 | 0 | 24.4788 | 323.2468 | -4.6185e-14 | 24.4788
2025-02-14 12:00:00 | 44.16 | 15.4812 | 0 | 28.6788 | 294.568 | 4.9738e-14 | 28.6788
2025-02-14 13:00:00 | 44.88 | 14.1003 | 0 | 30.7797 | 263.7883 | 4.6185e-14 | 30.7797
2025-02-14 14:00:00 | 41.28 | 11.4326 | 0 | 29.8474 | 233.9409 | -2.8422e-14 | 29.8474
2025-02-14 15:00:00 | 48.36 | 7.6599 | 0 | 40.7001 | 193.2407 | -7.1054e-15 | 40.7001
2025-02-14 16:00:00 | 49.56 | 3.0393 | 0 | 46.5207 | 146.72 | -4.9738e-14 | 46.5207
2025-02-14 17:00:00 | 41.16 | 0 | 0 | 41.16 | 105.56 | 0 | 41.16
2025-02-14 18:00:00 | 40.56 | 0 | 0 | 40.56 | 65 | 0 | 40.56
2025-02-14 19:00:00 | 40.56 | 0 | 0 | 0 | 65 | 40.56 | 40.56
2025-02-14 20:00:00 | 39.12 | 0 | 0 | 0 | 65 | 39.12 | 39.12
2025-02-14 21:00:00 | 36.84 | 0 | 0 | 0 | 65 | 36.84 | 36.84
2025-02-14 22:00:00 | 22.2 | 0 | 0 | 0 | 65 | 22.2 | 22.2
2025-02-14 23:00:00 | 22.92 | 0 | 0 | 0 | 65 | 22.92 | 22.92
2025-02-15 00:00:00 | 22.44 | 0 | 0 | 0 | 65 | 22.44 | 22.44
2025-02-15 01:00:00 | 21.96 | 0 | 0 | 0 | 65 | 21.96 | 21.96
2025-02-15 02:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-02-15 03:00:00 | 22.44 | 0 | 0 | 0 | 65 | 22.44 | 22.44
2025-02-15 04:00:00 | 22.2 | 0 | 0 | 0 | 65 | 22.2 | 22.2
2025-02-15 05:00:00 | 22.92 | 0 | 0 | 0 | 65 | 22.92 | 22.92
2025-02-15 06:00:00 | 27.24 | 0 | 0 | 0 | 65 | 27.24 | 27.24
2025-02-15 07:00:00 | 39.12 | 3.164 | 0 | 0 | 65 | 35.956 | 35.956
2025-02-15 08:00:00 | 49.08 | 7.791 | 0 | 0 | 65 | 41.289 | 41.289
2025-02-15 09:00:00 | 50.28 | 11.5689 | 0 | 0 | 65 | 38.7111 | 38.7111
2025-02-15 10:00:00 | 53.76 | 14.2403 | 0 | 0 | 65 | 39.5197 | 39.5197
2025-02-15 11:00:00 | 45.72 | 15.6231 | 0 | 0 | 65 | 30.0969 | 30.0969
2025-02-15 12:00:00 | 42.24 | 15.6231 | 0 | 0 | 65 | 26.6169 | 26.6169
2025-02-15 13:00:00 | 41.16 | 14.2403 | 0 | 0 | 65 | 26.9197 | 26.9197
2025-02-15 14:00:00 | 39.72 | 11.5689 | 0 | 0 | 65 | 28.1511 | 28.1511
2025-02-15 15:00:00 | 38.76 | 7.791 | 0 | 0 | 65 | 30.969 | 30.969
2025-02-15 16:00:00 | 38.16 | 3.164 | 0 | 0 | 65 | 34.996 | 34.996
2025-02-15 17:00:00 | 39.72 | 0 | 0 | 0 | 65 | 39.72 | 39.72
2025-02-15 18:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-02-15 19:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-02-15 20:00:00 | 38.64 | 0 | 0 | 0 | 65 | 38.64 | 38.64
2025-02-15 21:00:00 | 38.76 | 0 | 0 | 0 | 65 | 38.76 | 38.76
2025-02-15 22:00:00 | 26.76 | 0 | 0 | 0 | 65 | 26.76 | 26.76
2025-02-15 23:00:00 | 22.56 | 0 | 0 | 0 | 65 | 22.56 | 22.56
2025-02-16 00:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-02-16 01:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-02-16 02:00:00 | 23.4 | 0 | 0 | 0 | 65 | 23.4 | 23.4
2025-02-16 03:00:00 | 39.12 | 0 | 0 | 0 | 65 | 39.12 | 39.12
2025-02-16 04:00:00 | 38.88 | 0 | 0 | 0 | 65 | 38.88 | 38.88
2025-02-16 05:00:00 | 38.28 | 0 | 0 | 0 | 65 | 38.28 | 38.28
2025-02-16 06:00:00 | 26.64 | 0 | 0 | 0 | 65 | 26.64 | 26.64
2025-02-16 07:00:00 | 22.32 | 3.2902 | 0 | 0 | 65 | 19.0298 | 19.0298
2025-02-16 08:00:00 | 21.96 | 7.9235 | 0 | 0 | 65 | 14.0365 | 14.0365
2025-02-16 09:00:00 | 24 | 11.7065 | 0 | 0 | 65 | 12.2935 | 12.2935
2025-02-16 10:00:00 | 37.68 | 14.3816 | 0 | 0 | 65 | 23.2984 | 23.2984
2025-02-16 11:00:00 | 38.4 | 15.7663 | 0 | 0 | 65 | 22.6337 | 22.6337
2025-02-16 12:00:00 | 37.2 | 15.7663 | 0 | 0 | 65 | 21.4337 | 21.4337
2025-02-16 13:00:00 | 37.68 | 14.3816 | 0 | 0 | 65 | 23.2984 | 23.2984
2025-02-16 14:00:00 | 37.92 | 11.7065 | 0 | 0 | 65 | 26.2135 | 26.2135
2025-02-16 15:00:00 | 39.6 | 7.9235 | 0 | 0 | 65 | 31.6765 | 31.6765
2025-02-16 16:00:00 | 43.56 | 3.2902 | 0 | 0 | 65 | 40.2698 | 40.2698
2025-02-16 17:00:00 | 40.56 | 0 | 0 | 0 | 65 | 40.56 | 40.56
2025-02-16 18:00:00 | 42.72 | 0 | 0 | 0 | 65 | 42.72 | 42.72
2025-02-16 19:00:00 | 57 | 0 | 0 | 0 | 65 | 57 | 57
2025-02-16 20:00:00 | 60.24 | 0 | 0 | 0 | 65 | 60.24 | 60.24
2025-02-16 21:00:00 | 53.52 | 0 | 0 | 0 | 65 | 53.52 | 53.52
2025-02-16 22:00:00 | 45.12 | 0 | 0 | 0 | 65 | 45.12 | 45.12
2025-02-16 23:00:00 | 42 | 0 | 0 | 0 | 65 | 42 | 42
2025-02-17 00:00:00 | 41.4 | 0 | 0 | 0 | 65 | 41.4 | 41.4
2025-02-17 01:00:00 | 39.96 | 0 | 0 | 0 | 65 | 39.96 | 39.96
2025-02-17 02:00:00 | 39.36 | 0 | 0 | 0 | 65 | 39.36 | 39.36
2025-02-17 03:00:00 | 38.28 | 0 | 0 | 0 | 65 | 38.28 | 38.28
2025-02-17 04:00:00 | 38.76 | 0 | 0 | 0 | 65 | 38.76 | 38.76
2025-02-17 05:00:00 | 39 | 0 | 0 | 0 | 65 | 39 | 39
2025-02-17 06:00:00 | 37.92 | 0 | 0 | 0 | 65 | 37.92 | 37.92
2025-02-17 07:00:00 | 38.4 | 3.4177 | 0 | 0 | 65 | 34.9823 | 34.9823
2025-02-17 08:00:00 | 38.04 | 8.0572 | 0 | 0 | 65 | 29.9828 | 29.9828
2025-02-17 09:00:00 | 43.68 | 11.8453 | 0 | 0 | 65 | 31.8347 | 31.8347
2025-02-17 10:00:00 | 41.88 | 14.5239 | 0 | 0 | 65 | 27.3561 | 27.3561
2025-02-17 11:00:00 | 39.24 | 15.9105 | 0 | 0 | 65 | 23.3295 | 23.3295
2025-02-17 12:00:00 | 37.92 | 15.9105 | 0 | 0 | 65 | 22.0095 | 22.0095
2025-02-17 13:00:00 | 38.16 | 14.5239 | 0 | 0 | 65 | 23.6361 | 23.6361
2025-02-17 14:00:00 | 38.64 | 11.8453 | 0 | 0 | 65 | 26.7947 | 26.7947
2025-02-17 15:00:00 | 43.8 | 8.0572 | 0 | 0 | 65 | 35.7428 | 35.7428
2025-02-17 16:00:00 | 58.08 | 3.4177 | 0 | 0 | 65 | 54.6623 | 54.6623
2025-02-17 17:00:00 | 62.76 | 0 | 0 | 0 | 65 | 62.76 | 62.76
2025-02-17 18:00:00 | 61.2 | 0 | 0 | 0 | 65 | 61.2 | 61.2
2025-02-17 19:00:00 | 55.68 | 0 | 0 | 0 | 65 | 55.68 | 55.68
2025-02-17 20:00:00 | 51.48 | 0 | 0 | 0 | 65 | 51.48 | 51.48
2025-02-17 21:00:00 | 48 | 0 | 0 | 0 | 65 | 48 | 48
2025-02-17 22:00:00 | 48 | 0 | 0 | 0 | 65 | 48 | 48
2025-02-17 23:00:00 | 41.52 | 0 | 0 | 0 | 65 | 41.52 | 41.52
2025-02-18 00:00:00 | 41.64 | 0 | 0 | 0 | 65 | 41.64 | 41.64
2025-02-18 01:00:00 | 38.76 | 0 | 29.732 | 0 | 91.1641 | 68.492 | 38.76
2025-02-18 02:00:00 | 38.28 | 0 | 71.4 | 0 | 153.9961 | 109.68 | 38.28
2025-02-18 03:00:00 | 38.04 | 0 | 71.64 | 0 | 217.0393 | 109.68 | 38.04
2025-02-18 04:00:00 | 38.28 | 0 | 71.4 | 0 | 279.8713 | 109.68 | 38.28
2025-02-18 05:00:00 | 37.8 | 0 | 71.88 | 0 | 343.1257 | 109.68 | 37.8
2025-02-18 06:00:00 | 38.52 | 0 | 71.16 | 0 | 405.7465 | 109.68 | 38.52
2025-02-18 07:00:00 | 28.8 | 3.5464 | 0 | 25.2536 | 380.493 | -4.6185e-14 | 25.2536
2025-02-18 08:00:00 | 21.96 | 8.1921 | 0 | 13.7679 | 366.725 | 1.4211e-14 | 13.7679
2025-02-18 09:00:00 | 24.72 | 11.9852 | 0 | 12.7348 | 353.9902 | -7.1054e-15 | 12.7348
2025-02-18 10:00:00 | 32.04 | 14.6673 | 0 | 17.3727 | 336.6176 | 2.4869e-14 | 17.3727
2025-02-18 11:00:00 | 39.12 | 16.0557 | 0 | 23.0643 | 313.5533 | 3.908e-14 | 23.0643
2025-02-18 12:00:00 | 38.4 | 16.0557 | 0 | 22.3443 | 291.209 | 3.908e-14 | 22.3443
2025-02-18 13:00:00 | 38.04 | 14.6673 | 0 | 23.3727 | 267.8363 | 2.4869e-14 | 23.3727
2025-02-18 14:00:00 | 38.52 | 11.9852 | 0 | 26.5348 | 241.3015 | -3.5527e-15 | 26.5348
2025-02-18 15:00:00 | 44.28 | 8.1921 | 0 | 36.0879 | 205.2136 | 1.4211e-14 | 36.0879
2025-02-18 16:00:00 | 50.4 | 3.5464 | 0 | 46.8536 | 158.36 | 4.9738e-14 | 46.8536
2025-02-18 17:00:00 | 47.16 | 0 | 0 | 47.16 | 111.2 | 0 | 47.16
2025-02-18 18:00:00 | 46.2 | 0 | 0 | 46.2 | 65 | 0 | 46.2
2025-02-18 19:00:00 | 44.28 | 0 | 0 | 0 | 65 | 44.28 | 44.28
2025-02-18 20:00:00 | 40.08 | 0 | 0 | 0 | 65 | 40.08 | 40.08
2025-02-18 21:00:00 | 23.04 | 0 | 0 | 0 | 65 | 23.04 | 23.04
2025-02-18 22:00:00 | 22.44 | 0 | 0 | 0 | 65 | 22.44 | 22.44
2025-02-18 23:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-02-19 00:00:00 | 21.96 | 0 | 0 | 0 | 65 | 21.96 | 21.96
2025-02-19 01:00:00 | 33.36 | 0 | 0 | 0 | 65 | 33.36 | 33.36
2025-02-19 02:00:00 | 39 | 0 | 55.6484 | 0 | 113.9706 | 94.6484 | 39
2025-02-19 03:00:00 | 38.52 | 0 | 71.16 | 0 | 176.5914 | 109.68 | 38.52
2025-02-19 04:00:00 | 29.28 | 0 | 75 | 0 | 242.5914 | 104.28 | 29.28
2025-02-19 05:00:00 | 22.68 | 0 | 75 | 0 | 308.5914 | 97.68 | 22.68
2025-02-19 06:00:00 | 22.32 | 0 | 75 | 0 | 374.5914 | 97.32 | 22.32
2025-02-19 07:00:00 | 21.84 | 3.6764 | 0 | 18.1636 | 356.4278 | 4.2633e-14 | 18.1636
2025-02-19 08:00:00 | 21.72 | 8.3281 | 0 | 13.3919 | 343.0359 | 3.908e-14 | 13.3919
2025-02-19 09:00:00 | 32.04 | 12.1261 | 0 | 19.9139 | 323.122 | 1.4211e-14 | 19.9139
2025-02-19 10:00:00 | 39.96 | 14.8117 | 0 | 25.1483 | 297.9738 | -2.1316e-14 | 25.1483
2025-02-19 11:00:00 | 37.92 | 16.2019 | 0 | 21.7181 | 276.2557 | -4.2633e-14 | 21.7181
2025-02-19 12:00:00 | 38.52 | 16.2019 | 0 | 22.3181 | 253.9376 | -3.908e-14 | 22.3181
2025-02-19 13:00:00 | 37.44 | 14.8117 | 0 | 22.6283 | 231.3094 | -2.4869e-14 | 22.6283
2025-02-19 14:00:00 | 38.04 | 12.1261 | 0 | 25.9139 | 205.3955 | 1.4211e-14 | 25.9139
2025-02-19 15:00:00 | 37.68 | 8.3281 | 0 | 29.3519 | 176.0436 | 4.2633e-14 | 29.3519
2025-02-19 16:00:00 | 38.04 | 3.6764 | 0 | 34.3636 | 141.68 | 4.2633e-14 | 34.3636
2025-02-19 17:00:00 | 38.28 | 0 | 0 | 38.28 | 103.4 | 0 | 38.28
2025-02-19 18:00:00 | 38.4 | 0 | 0 | 38.4 | 65 | 0 | 38.4
2025-02-19 19:00:00 | 38.16 | 0 | 0 | 0 | 65 | 38.16 | 38.16
2025-02-19 20:00:00 | 36.72 | 0 | 0 | 0 | 65 | 36.72 | 36.72
2025-02-19 21:00:00 | 21.96 | 0 | 0 | 0 | 65 | 21.96 | 21.96
2025-02-19 22:00:00 | 21.84 | 0 | 0 | 0 | 65 | 21.84 | 21.84
2025-02-19 23:00:00 | 22.2 | 0 | 0 | 0 | 65 | 22.2 | 22.2
2025-02-20 00:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-02-20 01:00:00 | 38.04 | 0 | 65.4604 | 0 | 122.6051 | 103.5004 | 38.04
2025-02-20 02:00:00 | 38.4 | 0 | 71.28 | 0 | 185.3315 | 109.68 | 38.4
2025-02-20 03:00:00 | 38.04 | 0 | 71.64 | 0 | 248.3747 | 109.68 | 38.04
2025-02-20 04:00:00 | 38.64 | 0 | 71.04 | 0 | 310.8899 | 109.68 | 38.64
2025-02-20 05:00:00 | 38.28 | 0 | 71.4 | 0 | 373.7219 | 109.68 | 38.28
2025-02-20 06:00:00 | 26.52 | 0 | 75 | 0 | 439.7219 | 101.52 | 26.52
2025-02-20 07:00:00 | 21.72 | 3.8076 | 0 | 17.9124 | 421.8096 | -3.1974e-14 | 17.9124
2025-02-20 08:00:00 | 21.6 | 8.4652 | 0 | 13.1348 | 408.6748 | 4.0856e-14 | 13.1348
2025-02-20 09:00:00 | 36.48 | 12.268 | 0 | 24.212 | 384.4628 | 4.2633e-14 | 24.212
2025-02-20 10:00:00 | 40.8 | 14.9571 | 0 | 25.8429 | 358.6199 | 1.0658e-14 | 25.8429
2025-02-20 11:00:00 | 38.52 | 16.349 | 0 | 22.171 | 336.4489 | -2.8422e-14 | 22.171
2025-02-20 12:00:00 | 38.52 | 16.349 | 0 | 22.171 | 314.2779 | -2.8422e-14 | 22.171
2025-02-20 13:00:00 | 38.04 | 14.9571 | 0 | 23.0829 | 291.195 | 1.4211e-14 | 23.0829
2025-02-20 14:00:00 | 39.6 | 12.268 | 0 | 27.332 | 263.8631 | 4.6185e-14 | 27.332
2025-02-20 15:00:00 | 50.4 | 8.4652 | 0 | 41.9348 | 221.9282 | 3.5527e-14 | 41.9348
2025-02-20 16:00:00 | 53.04 | 3.8076 | 0 | 49.2324 | 172.6959 | -2.8422e-14 | 49.2324
2025-02-20 17:00:00 | 52.56 | 0 | 0 | 52.56 | 120.1359 | 0 | 52.56
2025-02-20 18:00:00 | 48.6 | 0 | 0 | 48.6 | 71.5359 | 0 | 48.6
2025-02-20 19:00:00 | 42.12 | 0 | 0 | 0 | 71.5359 | 42.12 | 42.12
2025-02-20 20:00:00 | 41.76 | 0 | 0 | 0 | 71.5359 | 41.76 | 41.76
2025-02-20 21:00:00 | 40.56 | 0 | 0 | 0 | 71.5359 | 40.56 | 40.56
2025-02-20 22:00:00 | 31.68 | 0 | 0 | 0 | 71.5359 | 31.68 | 31.68
2025-02-20 23:00:00 | 21.72 | 0 | 0 | 0 | 71.5359 | 21.72 | 21.72
2025-02-21 00:00:00 | 23.16 | 0 | 75 | 0 | 137.5359 | 98.16 | 23.16
2025-02-21 01:00:00 | 25.8 | 0 | 0 | 0 | 137.5359 | 25.8 | 25.8
2025-02-21 02:00:00 | 38.88 | 0 | 70.8 | 0 | 199.8399 | 109.68 | 38.88
2025-02-21 03:00:00 | 38.16 | 0 | 71.52 | 0 | 262.7775 | 109.68 | 38.16
2025-02-21 04:00:00 | 39 | 0 | 70.68 | 0 | 324.9759 | 109.68 | 39
2025-02-21 05:00:00 | 38.64 | 0 | 71.04 | 0 | 387.4911 | 109.68 | 38.64
2025-02-21 06:00:00 | 34.68 | 0 | 75 | 0 | 453.4911 | 109.68 | 34.68
2025-02-21 07:00:00 | 22.08 | 3.94 | 0 | 18.14 | 435.3511 | 2.1316e-14 | 18.14
2025-02-21 08:00:00 | 24.12 | 8.6033 | 0 | 15.5167 | 419.8344 | -4.4409e-14 | 15.5167
2025-02-21 09:00:00 | 25.8 | 12.4109 | 0 | 13.3891 | 406.4453 | 1.2434e-14 | 13.3891
2025-02-21 10:00:00 | 40.92 | 15.1033 | 0 | 25.8167 | 380.6286 | 1.0658e-14 | 25.8167
2025-02-21 11:00:00 | 44.76 | 16.497 | 0 | 28.263 | 352.3655 | 3.908e-14 | 28.263
2025-02-21 12:00:00 | 48.12 | 16.497 | 0 | 31.623 | 320.7425 | 3.908e-14 | 31.623
2025-02-21 13:00:00 | 48.36 | 15.1033 | 0 | 33.2567 | 287.4858 | 7.1054e-15 | 33.2567
2025-02-21 14:00:00 | 48.12 | 12.4109 | 0 | 35.7091 | 251.7767 | 7.1054e-15 | 35.7091
2025-02-21 15:00:00 | 54.24 | 8.6033 | 0 | 45.6367 | 206.14 | -4.2633e-14 | 45.6367
2025-02-21 16:00:00 | 53.4 | 3.94 | 0 | 49.46 | 156.68 | 2.1316e-14 | 49.46
2025-02-21 17:00:00 | 48.72 | 0 | 0 | 48.72 | 107.96 | 0 | 48.72
2025-02-21 18:00:00 | 42.96 | 0 | 0 | 42.96 | 65 | 0 | 42.96
2025-02-21 19:00:00 | 40.8 | 0 | 0 | 0 | 65 | 40.8 | 40.8
2025-02-21 20:00:00 | 39.72 | 0 | 0 | 0 | 65 | 39.72 | 39.72
2025-02-21 21:00:00 | 39 | 0 | 0 | 0 | 65 | 39 | 39
2025-02-21 22:00:00 | 38.28 | 0 | 0 | 0 | 65 | 38.28 | 38.28
2025-02-21 23:00:00 | 24 | 0 | 0 | 0 | 65 | 24 | 24
2025-02-22 00:00:00 | 22.56 | 0 | 0 | 0 | 65 | 22.56 | 22.56
2025-02-22 01:00:00 | 21.6 | 0 | 0 | 0 | 65 | 21.6 | 21.6
2025-02-22 02:00:00 | 26.76 | 0 | 0 | 0 | 65 | 26.76 | 26.76
2025-02-22 03:00:00 | 38.64 | 0 | 0 | 0 | 65 | 38.64 | 38.64
2025-02-22 04:00:00 | 37.68 | 0 | 0 | 0 | 65 | 37.68 | 37.68
2025-02-22 05:00:00 | 37.68 | 0 | 0 | 0 | 65 | 37.68 | 37.68
2025-02-22 06:00:00 | 37.8 | 0 | 0 | 0 | 65 | 37.8 | 37.8
2025-02-22 07:00:00 | 37.92 | 4.0734 | 0 | 0 | 65 | 33.8466 | 33.8466
2025-02-22 08:00:00 | 30.96 | 8.7424 | 0 | 0 | 65 | 22.2176 | 22.2176
2025-02-22 09:00:00 | 21.84 | 12.5546 | 0 | 0 | 65 | 9.2854 | 9.2854
2025-02-22 10:00:00 | 21.96 | 15.2503 | 0 | 0 | 65 | 6.7097 | 6.7097
2025-02-22 11:00:00 | 30.6 | 16.6456 | 0 | 0 | 65 | 13.9544 | 13.9544
2025-02-22 12:00:00 | 37.2 | 16.6456 | 0 | 0 | 65 | 20.5544 | 20.5544
2025-02-22 13:00:00 | 37.08 | 15.2503 | 0 | 0 | 65 | 21.8297 | 21.8297
2025-02-22 14:00:00 | 37.92 | 12.5546 | 0 | 0 | 65 | 25.3654 | 25.3654
2025-02-22 15:00:00 | 36.96 | 8.7424 | 0 | 0 | 65 | 28.2176 | 28.2176
2025-02-22 16:00:00 | 37.44 | 4.0734 | 0 | 0 | 65 | 33.3666 | 33.3666
2025-02-22 17:00:00 | 38.28 | 0 | 0 | 0 | 65 | 38.28 | 38.28
2025-02-22 18:00:00 | 38.52 | 0 | 0 | 0 | 65 | 38.52 | 38.52
2025-02-22 19:00:00 | 38.04 | 0 | 0 | 0 | 65 | 38.04 | 38.04
2025-02-22 20:00:00 | 38.52 | 0 | 0 | 0 | 65 | 38.52 | 38.52
2025-02-22 21:00:00 | 37.8 | 0 | 0 | 0 | 65 | 37.8 | 37.8
2025-02-22 22:00:00 | 38.64 | 0 | 0 | 0 | 65 | 38.64 | 38.64
2025-02-22 23:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-02-23 00:00:00 | 26.04 | 0 | 0 | 0 | 65 | 26.04 | 26.04
2025-02-23 01:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-02-23 02:00:00 | 21.84 | 0 | 0 | 0 | 65 | 21.84 | 21.84
2025-02-23 03:00:00 | 22.56 | 0 | 0 | 0 | 65 | 22.56 | 22.56
2025-02-23 04:00:00 | 34.2 | 0 | 0 | 0 | 65 | 34.2 | 34.2
2025-02-23 05:00:00 | 39.24 | 0 | 0 | 0 | 65 | 39.24 | 39.24
2025-02-23 06:00:00 | 38.88 | 0 | 0 | 0 | 65 | 38.88 | 38.88
2025-02-23 07:00:00 | 37.92 | 4.2079 | 0 | 0 | 65 | 33.7121 | 33.7121
2025-02-23 08:00:00 | 26.76 | 8.8824 | 0 | 0 | 65 | 17.8776 | 17.8776
2025-02-23 09:00:00 | 25.68 | 12.6992 | 0 | 0 | 65 | 12.9808 | 12.9808
2025-02-23 10:00:00 | 24.72 | 15.398 | 0 | 0 | 65 | 9.322 | 9.322
2025-02-23 11:00:00 | 22.92 | 16.795 | 0 | 0 | 65 | 6.125 | 6.125
2025-02-23 12:00:00 | 29.76 | 16.795 | 0 | 0 | 65 | 12.965 | 12.965
2025-02-23 13:00:00 | 39.84 | 15.398 | 0 | 0 | 65 | 24.442 | 24.442
2025-02-23 14:00:00 | 39.72 | 12.6992 | 0 | 0 | 65 | 27.0208 | 27.0208
2025-02-23 15:00:00 | 45.24 | 8.8824 | 0 | 0 | 65 | 36.3576 | 36.3576
2025-02-23 16:00:00 | 47.76 | 4.2079 | 0 | 0 | 65 | 43.5521 | 43.5521
2025-02-23 17:00:00 | 47.52 | 0 | 0 | 0 | 65 | 47.52 | 47.52
2025-02-23 18:00:00 | 32.16 | 0 | 0 | 0 | 65 | 32.16 | 32.16
2025-02-23 19:00:00 | 29.28 | 0 | 0 | 0 | 65 | 29.28 | 29.28
2025-02-23 20:00:00 | 33.84 | 0 | 0 | 0 | 65 | 33.84 | 33.84
2025-02-23 21:00:00 | 32.52 | 0 | 0 | 0 | 65 | 32.52 | 32.52
2025-02-23 22:00:00 | 25.44 | 0 | 0 | 0 | 65 | 25.44 | 25.44
2025-02-23 23:00:00 | 25.56 | 0 | 0 | 0 | 65 | 25.56 | 25.56
2025-02-24 00:00:00 | 24.12 | 0 | 0 | 0 | 65 | 24.12 | 24.12
2025-02-24 01:00:00 | 24.12 | 0 | 0 | 0 | 65 | 24.12 | 24.12
2025-02-24 02:00:00 | 23.64 | 0 | 0 | 0 | 65 | 23.64 | 23.64
2025-02-24 03:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-02-24 04:00:00 | 22.44 | 0 | 58.8576 | 0 | 116.7947 | 81.2976 | 22.44
2025-02-24 05:00:00 | 22.92 | 0 | 75 | 0 | 182.7947 | 97.92 | 22.92
2025-02-24 06:00:00 | 23.28 | 0 | 75 | 0 | 248.7947 | 98.28 | 23.28
2025-02-24 07:00:00 | 22.56 | 4.3434 | 0 | 18.2166 | 230.5781 | 2.1316e-14 | 18.2166
2025-02-24 08:00:00 | 22.44 | 9.0233 | 0 | 13.4167 | 217.1614 | -4.0856e-14 | 13.4167
2025-02-24 09:00:00 | 22.44 | 12.8445 | 0 | 9.5955 | 207.5659 | 1.7764e-15 | 9.5955
2025-02-24 10:00:00 | 22.32 | 15.5464 | 0 | 6.7736 | 200.7923 | 1.7764e-15 | 6.7736
2025-02-24 11:00:00 | 22.32 | 16.945 | 0 | 5.375 | 195.4173 | 0 | 5.375
2025-02-24 12:00:00 | 22.68 | 16.945 | 0 | 5.735 | 189.6824 | 0 | 5.735
2025-02-24 13:00:00 | 22.08 | 15.5464 | 0 | 6.5336 | 183.1488 | 0 | 6.5336
2025-02-24 14:00:00 | 22.44 | 12.8445 | 0 | 9.5955 | 173.5532 | 1.7764e-15 | 9.5955
2025-02-24 15:00:00 | 21.96 | 9.0233 | 0 | 12.9367 | 160.6166 | -4.0856e-14 | 12.9367
2025-02-24 16:00:00 | 21.72 | 4.3434 | 0 | 17.3766 | 143.24 | 2.4869e-14 | 17.3766
2025-02-24 17:00:00 | 31.08 | 0 | 0 | 31.08 | 112.16 | 0 | 31.08
2025-02-24 18:00:00 | 47.16 | 0 | 0 | 47.16 | 65 | 0 | 47.16
2025-02-24 19:00:00 | 47.64 | 0 | 0 | 0 | 65 | 47.64 | 47.64
2025-02-24 20:00:00 | 54.84 | 0 | 0 | 0 | 65 | 54.84 | 54.84
2025-02-24 21:00:00 | 53.4 | 0 | 0 | 0 | 65 | 53.4 | 53.4
2025-02-24 22:00:00 | 48.72 | 0 | 0 | 0 | 65 | 48.72 | 48.72
2025-02-24 23:00:00 | 30.48 | 0 | 0 | 0 | 65 | 30.48 | 30.48
2025-02-25 00:00:00 | 25.68 | 0 | 0 | 0 | 65 | 25.68 | 25.68
2025-02-25 01:00:00 | 24.6 | 0 | 0 | 0 | 65 | 24.6 | 24.6
2025-02-25 02:00:00 | 23.04 | 0 | 64.8493 | 0 | 122.0674 | 87.8893 | 23.04
2025-02-25 03:00:00 | 22.44 | 0 | 75 | 0 | 188.0674 | 97.44 | 22.44
2025-02-25 04:00:00 | 22.56 | 0 | 75 | 0 | 254.0674 | 97.56 | 22.56
2025-02-25 05:00:00 | 22.2 | 0 | 75 | 0 | 320.0674 | 97.2 | 22.2
2025-02-25 06:00:00 | 22.44 | 0 | 75 | 0 | 386.0674 | 97.44 | 22.44
2025-02-25 07:00:00 | 35.4 | 4.4799 | 0 | 30.9201 | 355.1472 | -2.8422e-14 | 30.9201
2025-02-25 08:00:00 | 39.72 | 9.165 | 0 | 30.555 | 324.5922 | -1.4211e-14 | 30.555
2025-02-25 09:00:00 | 38.4 | 12.9904 | 0 | 25.4096 | 299.1827 | 2.4869e-14 | 25.4096
2025-02-25 10:00:00 | 38.04 | 15.6954 | 0 | 22.3446 | 276.8381 | -2.4869e-14 | 22.3446
2025-02-25 11:00:00 | 40.8 | 17.0956 | 0 | 23.7044 | 253.1337 | -2.8422e-14 | 23.7044
2025-02-25 12:00:00 | 27.72 | 17.0956 | 0 | 10.6244 | 242.5093 | -2.8422e-14 | 10.6244
2025-02-25 13:00:00 | 21.84 | 15.6954 | 0 | 6.1446 | 236.3647 | -3.5527e-15 | 6.1446
2025-02-25 14:00:00 | 22.08 | 12.9904 | 0 | 9.0896 | 227.2751 | -3.5527e-15 | 9.0896
2025-02-25 15:00:00 | 34.08 | 9.165 | 0 | 24.915 | 202.3601 | -1.4211e-14 | 24.915
2025-02-25 16:00:00 | 47.04 | 4.4799 | 0 | 42.5601 | 159.8 | -3.5527e-14 | 42.5601
2025-02-25 17:00:00 | 47.64 | 0 | 0 | 47.64 | 112.16 | 0 | 47.64
2025-02-25 18:00:00 | 47.16 | 0 | 0 | 47.16 | 65 | 0 | 47.16
2025-02-25 19:00:00 | 46.56 | 0 | 0 | 0 | 65 | 46.56 | 46.56
2025-02-25 20:00:00 | 52.68 | 0 | 0 | 0 | 65 | 52.68 | 52.68
2025-02-25 21:00:00 | 42.6 | 0 | 0 | 0 | 65 | 42.6 | 42.6
2025-02-25 22:00:00 | 27.6 | 0 | 0 | 0 | 65 | 27.6 | 27.6
2025-02-25 23:00:00 | 25.8 | 0 | 0 | 0 | 65 | 25.8 | 25.8
2025-02-26 00:00:00 | 25.08 | 0 | 0 | 0 | 65 | 25.08 | 25.08
2025-02-26 01:00:00 | 23.16 | 0 | 0 | 0 | 65 | 23.16 | 23.16
2025-02-26 02:00:00 | 22.92 | 0 | 22.5607 | 0 | 84.8534 | 45.4807 | 22.92
2025-02-26 03:00:00 | 23.04 | 0 | 75 | 0 | 150.8534 | 98.04 | 23.04
2025-02-26 04:00:00 | 22.44 | 0 | 75 | 0 | 216.8534 | 97.44 | 22.44
2025-02-26 05:00:00 | 23.4 | 0 | 75 | 0 | 282.8534 | 98.4 | 23.4
2025-02-26 06:00:00 | 23.04 | 0 | 75 | 0 | 348.8534 | 98.04 | 23.04
2025-02-26 07:00:00 | 22.68 | 4.6172 | 0 | 18.0628 | 330.7906 | -2.1316e-14 | 18.0628
2025-02-26 08:00:00 | 22.92 | 9.3075 | 0 | 13.6125 | 317.1781 | -3.5527e-14 | 13.6125
2025-02-26 09:00:00 | 22.2 | 13.137 | 0 | 9.063 | 308.1151 | 0 | 9.063
2025-02-26 10:00:00 | 22.44 | 15.8449 | 0 | 6.5951 | 301.5201 | 0 | 6.5951
2025-02-26 11:00:00 | 23.04 | 17.2467 | 0 | 5.7933 | 295.7267 | 8.8818e-16 | 5.7933
2025-02-26 12:00:00 | 25.08 | 17.2467 | 0 | 7.8333 | 287.8934 | 0 | 7.8333
2025-02-26 13:00:00 | 39.12 | 15.8449 | 0 | 23.2751 | 264.6183 | 4.6185e-14 | 23.2751
2025-02-26 14:00:00 | 41.28 | 13.137 | 0 | 28.143 | 236.4754 | -2.8422e-14 | 28.143
2025-02-26 15:00:00 | 41.4 | 9.3075 | 0 | 32.0925 | 204.3828 | -3.5527e-14 | 32.0925
2025-02-26 16:00:00 | 49.32 | 4.6172 | 0 | 44.7028 | 159.68 | -2.1316e-14 | 44.7028
2025-02-26 17:00:00 | 46.92 | 0 | 0 | 46.92 | 112.76 | 0 | 46.92
2025-02-26 18:00:00 | 47.76 | 0 | 0 | 47.76 | 65 | 0 | 47.76
2025-02-26 19:00:00 | 47.4 | 0 | 0 | 0 | 65 | 47.4 | 47.4
2025-02-26 20:00:00 | 45.24 | 0 | 0 | 0 | 65 | 45.24 | 45.24
2025-02-26 21:00:00 | 28.68 | 0 | 0 | 0 | 65 | 28.68 | 28.68
2025-02-26 22:00:00 | 25.2 | 0 | 0 | 0 | 65 | 25.2 | 25.2
2025-02-26 23:00:00 | 24.36 | 0 | 0 | 0 | 65 | 24.36 | 24.36
2025-02-27 00:00:00 | 21.96 | 0 | 0 | 0 | 65 | 21.96 | 21.96
2025-02-27 01:00:00 | 22.56 | 0 | 62.0836 | 0 | 119.6335 | 84.6436 | 22.56
2025-02-27 02:00:00 | 22.44 | 0 | 75 | 0 | 185.6335 | 97.44 | 22.44
2025-02-27 03:00:00 | 22.68 | 0 | 75 | 0 | 251.6335 | 97.68 | 22.68
2025-02-27 04:00:00 | 22.08 | 0 | 75 | 0 | 317.6335 | 97.08 | 22.08
2025-02-27 05:00:00 | 22.56 | 0 | 75 | 0 | 383.6335 | 97.56 | 22.56
2025-02-27 06:00:00 | 22.32 | 0 | 75 | 0 | 449.6335 | 97.32 | 22.32
2025-02-27 07:00:00 | 21.96 | 4.7554 | 0 | 17.2046 | 432.4289 | -4.9738e-14 | 17.2046
2025-02-27 08:00:00 | 22.56 | 9.4506 | 0 | 13.1094 | 419.3195 | -1.2434e-14 | 13.1094
2025-02-27 09:00:00 | 22.44 | 13.2842 | 0 | 9.1558 | 410.1637 | 0 | 9.1558
2025-02-27 10:00:00 | 25.92 | 15.9949 | 0 | 9.9251 | 400.2386 | 1.7764e-15 | 9.9251
2025-02-27 11:00:00 | 36.96 | 17.3981 | 0 | 19.5619 | 380.6768 | 0 | 19.5619
2025-02-27 12:00:00 | 38.04 | 17.3981 | 0 | 20.6419 | 360.0349 | 0 | 20.6419
2025-02-27 13:00:00 | 37.8 | 15.9949 | 0 | 21.8051 | 338.2299 | 1.7764e-14 | 21.8051
2025-02-27 14:00:00 | 46.8 | 13.2842 | 0 | 33.5158 | 304.714 | -1.4211e-14 | 33.5158
2025-02-27 15:00:00 | 60.84 | 9.4506 | 0 | 51.3894 | 253.3246 | -7.1054e-15 | 51.3894
2025-02-27 16:00:00 | 67.8 | 4.7554 | 0 | 63.0446 | 190.28 | 4.9738e-14 | 63.0446
2025-02-27 17:00:00 | 67.08 | 0 | 0 | 67.08 | 123.2 | 0 | 67.08
2025-02-27 18:00:00 | 58.2 | 0 | 0 | 58.2 | 65 | 0 | 58.2
2025-02-27 19:00:00 | 46.56 | 0 | 0 | 0 | 65 | 46.56 | 46.56
2025-02-27 20:00:00 | 41.76 | 0 | 0 | 0 | 65 | 41.76 | 41.76
2025-02-27 21:00:00 | 40.8 | 0 | 0 | 0 | 65 | 40.8 | 40.8
2025-02-27 22:00:00 | 39.48 | 0 | 0 | 0 | 65 | 39.48 | 39.48
2025-02-27 23:00:00 | 39 | 0 | 0 | 0 | 65 | 39 | 39
2025-02-28 00:00:00 | 39 | 0 | 0 | 0 | 65 | 39 | 39
2025-02-28 01:00:00 | 38.4 | 0 | 40.6548 | 0 | 100.7763 | 79.0548 | 38.4
2025-02-28 02:00:00 | 38.64 | 0 | 71.04 | 0 | 163.2915 | 109.68 | 38.64
2025-02-28 03:00:00 | 38.16 | 0 | 71.52 | 0 | 226.2291 | 109.68 | 38.16
2025-02-28 04:00:00 | 37.8 | 0 | 71.88 | 0 | 289.4835 | 109.68 | 37.8
2025-02-28 05:00:00 | 39.36 | 0 | 70.32 | 0 | 351.3651 | 109.68 | 39.36
2025-02-28 06:00:00 | 37.8 | 0 | 71.88 | 0 | 414.6195 | 109.68 | 37.8
2025-02-28 07:00:00 | 37.68 | 4.8944 | 0 | 32.7856 | 381.8338 | -7.1054e-15 | 32.7856
2025-02-28 08:00:00 | 38.04 | 9.5943 | 0 | 28.4457 | 353.3881 | 2.8422e-14 | 28.4457
2025-02-28 09:00:00 | 23.4 | 13.4318 | 0 | 9.9682 | 343.42 | 0 | 9.9682
2025-02-28 10:00:00 | 21.36 | 16.1454 | 0 | 5.2146 | 338.2053 | 8.8818e-16 | 5.2146
2025-02-28 11:00:00 | 32.64 | 17.55 | 0 | 15.09 | 323.1153 | 1.5987e-14 | 15.09
2025-02-28 12:00:00 | 37.92 | 17.55 | 0 | 20.37 | 302.7453 | 1.7764e-14 | 20.37
2025-02-28 13:00:00 | 42.48 | 16.1454 | 0 | 26.3346 | 276.4107 | 3.908e-14 | 26.3346
2025-02-28 14:00:00 | 46.92 | 13.4318 | 0 | 33.4882 | 242.9225 | 7.1054e-15 | 33.4882
2025-02-28 15:00:00 | 53.28 | 9.5943 | 0 | 43.6857 | 199.2368 | 2.8422e-14 | 43.6857
2025-02-28 16:00:00 | 50.52 | 4.8944 | 0 | 45.6256 | 153.6112 | -7.1054e-15 | 45.6256
2025-02-28 17:00:00 | 44.76 | 0 | 0 | 44.76 | 108.8512 | 0 | 44.76
2025-02-28 18:00:00 | 42.36 | 0 | 0 | 42.36 | 66.4912 | 0 | 42.36
2025-02-28 19:00:00 | 40.92 | 0 | 68.76 | 0 | 127 | 109.68 | 40.92
2025-02-28 20:00:00 | 32.04 | 0 | 75 | 0 | 193 | 107.04 | 32.04
2025-02-28 21:00:00 | 21.96 | 0 | 75 | 0 | 259 | 96.96 | 21.96
2025-02-28 22:00:00 | 22.2 | 0 | 75 | 0 | 325 | 97.2 | 22.2
2025-02-28 23:00:00 | 22.32 | 0 | 0 | 0 | 325 | 22.32 | 22.32
2025-03-01 00:00:00 | 21.84 | 0 | 0 | 0 | 325 | 21.84 | 21.84
2025-03-01 01:00:00 | 22.08 | 0 | 0 | 0 | 325 | 22.08 | 22.08
2025-03-01 02:00:00 | 22.8 | 0 | 0 | 0 | 325 | 22.8 | 22.8
2025-03-01 03:00:00 | 21.96 | 0 | 0 | 0 | 325 | 21.96 | 21.96
2025-03-01 04:00:00 | 22.2 | 0 | 0 | 0 | 325 | 22.2 | 22.2
2025-03-01 05:00:00 | 22.56 | 0 | 0 | 0 | 325 | 22.56 | 22.56
2025-03-01 06:00:00 | 22.56 | 0 | 0 | 0 | 325 | 22.56 | 22.56
2025-03-01 07:00:00 | 22.68 | 7.1452 | 0 | 0 | 325 | 15.5348 | 15.5348
2025-03-01 08:00:00 | 27.6 | 13.8226 | 0 | 0 | 325 | 13.7774 | 13.7774
2025-03-01 09:00:00 | 34.8 | 19.2747 | 0 | 0 | 325 | 15.5253 | 15.5253
2025-03-01 10:00:00 | 39.24 | 23.13 | 0 | 0 | 325 | 16.11 | 16.11
2025-03-01 11:00:00 | 32.04 | 25.1256 | 0 | 0 | 325 | 6.9144 | 6.9144
2025-03-01 12:00:00 | 28.92 | 25.1256 | 0 | 0 | 325 | 3.7944 | 3.7944
2025-03-01 13:00:00 | 33.6 | 23.13 | 0 | 0 | 325 | 10.47 | 10.47
2025-03-01 14:00:00 | 42.48 | 19.2747 | 0 | 0 | 325 | 23.2053 | 23.2053
2025-03-01 15:00:00 | 42 | 13.8226 | 0 | 0 | 325 | 28.1774 | 28.1774
2025-03-01 16:00:00 | 39.36 | 7.1452 | 0 | 0 | 325 | 32.2148 | 32.2148
2025-03-01 17:00:00 | 40.68 | 0 | 0 | 0 | 325 | 40.68 | 40.68
2025-03-01 18:00:00 | 39.12 | 0 | 0 | 0 | 325 | 39.12 | 39.12
2025-03-01 19:00:00 | 35.88 | 0 | 0 | 0 | 325 | 35.88 | 35.88
2025-03-01 20:00:00 | 23.04 | 0 | 0 | 0 | 325 | 23.04 | 23.04
2025-03-01 21:00:00 | 22.92 | 0 | 0 | 0 | 325 | 22.92 | 22.92
2025-03-01 22:00:00 | 22.08 | 0 | 0 | 0 | 325 | 22.08 | 22.08
2025-03-01 23:00:00 | 22.8 | 0 | 0 | 0 | 325 | 22.8 | 22.8
2025-03-02 00:00:00 | 22.8 | 0 | 0 | 0 | 325 | 22.8 | 22.8
2025-03-02 01:00:00 | 22.56 | 0 | 0 | 0 | 325 | 22.56 | 22.56
2025-03-02 02:00:00 | 22.92 | 0 | 0 | 0 | 325 | 22.92 | 22.92
2025-03-02 03:00:00 | 22.92 | 0 | 0 | 0 | 325 | 22.92 | 22.92
2025-03-02 04:00:00 | 22.8 | 0 | 0 | 0 | 325 | 22.8 | 22.8
2025-03-02 05:00:00 | 23.4 | 0 | 0 | 0 | 325 | 23.4 | 23.4
2025-03-02 06:00:00 | 22.68 | 0 | 0 | 0 | 325 | 22.68 | 22.68
2025-03-02 07:00:00 | 22.2 | 7.3445 | 0 | 0 | 325 | 14.8555 | 14.8555
2025-03-02 08:00:00 | 22.56 | 14.0282 | 0 | 0 | 325 | 8.5318 | 8.5318
2025-03-02 09:00:00 | 23.4 | 19.4855 | 0 | 0 | 325 | 3.9145 | 3.9145
2025-03-02 10:00:00 | 25.68 | 23.3443 | 0 | 0 | 325 | 2.3357 | 2.3357
2025-03-02 11:00:00 | 25.32 | 25.3418 | 0 | 0 | 325 | -0.021819 | -0.021819
2025-03-02 12:00:00 | 24.24 | 25.3418 | 0 | 0 | 325 | -1.1018 | -1.1018
2025-03-02 13:00:00 | 24.36 | 23.3443 | 0 | 0 | 325 | 1.0157 | 1.0157
2025-03-02 14:00:00 | 21.84 | 19.4855 | 0 | 0 | 325 | 2.3545 | 2.3545
2025-03-02 15:00:00 | 23.88 | 14.0282 | 0 | 0 | 325 | 9.8518 | 9.8518
2025-03-02 16:00:00 | 32.4 | 7.3445 | 0 | 0 | 325 | 25.0555 | 25.0555
2025-03-02 17:00:00 | 46.8 | 0 | 0 | 0 | 325 | 46.8 | 46.8
2025-03-02 18:00:00 | 45.48 | 0 | 0 | 0 | 325 | 45.48 | 45.48
2025-03-02 19:00:00 | 43.92 | 0 | 0 | 0 | 325 | 43.92 | 43.92
2025-03-02 20:00:00 | 46.8 | 0 | 0 | 0 | 325 | 46.8 | 46.8
2025-03-02 21:00:00 | 31.68 | 0 | 0 | 0 | 325 | 31.68 | 31.68
2025-03-02 22:00:00 | 25.32 | 0 | 0 | 0 | 325 | 25.32 | 25.32
2025-03-02 23:00:00 | 23.88 | 0 | 0 | 0 | 325 | 23.88 | 23.88
2025-03-03 00:00:00 | 23.28 | 0 | 0 | 0 | 325 | 23.28 | 23.28
2025-03-03 01:00:00 | 21.6 | 0 | 0 | 0 | 325 | 21.6 | 21.6
2025-03-03 02:00:00 | 21.12 | 0 | 0 | 0 | 325 | 21.12 | 21.12
2025-03-03 03:00:00 | 22.32 | 0 | 0 | 0 | 325 | 22.32 | 22.32
2025-03-03 04:00:00 | 21 | 0 | 0 | 0 | 325 | 21 | 21
2025-03-03 05:00:00 | 21.6 | 0 | 15.4201 | 0 | 338.5697 | 37.0201 | 21.6
2025-03-03 06:00:00 | 21.12 | 0.0832 | 0 | 0 | 338.5697 | 21.0368 | 21.0368
2025-03-03 07:00:00 | 21.12 | 7.5447 | 0 | 13.5753 | 324.9944 | -8.8818e-15 | 13.5753
2025-03-03 08:00:00 | 26.4 | 14.2345 | 0 | 12.1655 | 312.8289 | 2.6645e-14 | 12.1655
2025-03-03 09:00:00 | 22.08 | 19.6966 | 0 | 2.3834 | 310.4455 | -1.3323e-15 | 2.3834
2025-03-03 10:00:00 | 21.12 | 23.559 | 0 | 0 | 310.4455 | -2.439 | -2.439
2025-03-03 11:00:00 | 26.88 | 25.5583 | 0 | 1.3217 | 309.1238 | 2.2204e-16 | 1.3217
2025-03-03 12:00:00 | 36.36 | 25.5583 | 0 | 10.8017 | 298.322 | 1.0658e-14 | 10.8017
2025-03-03 13:00:00 | 40.2 | 23.559 | 0 | 16.641 | 281.681 | 3.908e-14 | 16.641
2025-03-03 14:00:00 | 45 | 19.6966 | 0 | 25.3034 | 256.3777 | 3.1974e-14 | 25.3034
2025-03-03 15:00:00 | 48.48 | 14.2345 | 0 | 34.2455 | 222.1321 | 2.1316e-14 | 34.2455
2025-03-03 16:00:00 | 51.24 | 7.5447 | 0 | 43.6953 | 178.4368 | -7.1054e-15 | 43.6953
2025-03-03 17:00:00 | 57.12 | 0.0832 | 0 | 57.0368 | 121.4 | 0 | 57.0368
2025-03-03 18:00:00 | 56.4 | 0 | 0 | 56.4 | 65 | 0 | 56.4
2025-03-03 19:00:00 | 51.84 | 0 | 40.6755 | 0 | 100.7944 | 92.5155 | 51.84
2025-03-03 20:00:00 | 54.72 | 0 | 0 | 0 | 100.7944 | 54.72 | 54.72
2025-03-03 21:00:00 | 51.6 | 0 | 0 | 0 | 100.7944 | 51.6 | 51.6
2025-03-03 22:00:00 | 49.2 | 0 | 0 | 0 | 100.7944 | 49.2 | 49.2
2025-03-03 23:00:00 | 45.36 | 0 | 0 | 0 | 100.7944 | 45.36 | 45.36
2025-03-04 00:00:00 | 28.92 | 0 | 0 | 0 | 100.7944 | 28.92 | 28.92
2025-03-04 01:00:00 | 22.2 | 0 | 0 | 0 | 100.7944 | 22.2 | 22.2
2025-03-04 02:00:00 | 22.32 | 0 | 75 | 0 | 166.7944 | 97.32 | 22.32
2025-03-04 03:00:00 | 22.92 | 0 | 75 | 0 | 232.7944 | 97.92 | 22.92
2025-03-04 04:00:00 | 22.56 | 0 | 75 | 0 | 298.7944 | 97.56 | 22.56
2025-03-04 05:00:00 | 27 | 0 | 75 | 0 | 364.7944 | 102 | 27
2025-03-04 06:00:00 | 38.76 | 0.27781 | 75 | 0 | 430.7944 | 113.4822 | 38.4822
2025-03-04 07:00:00 | 39.36 | 7.7457 | 0 | 31.6143 | 399.1802 | 1.7764e-14 | 31.6143
2025-03-04 08:00:00 | 39.72 | 14.4413 | 0 | 25.2787 | 373.9014 | 1.7764e-14 | 25.2787
2025-03-04 09:00:00 | 39.36 | 19.9082 | 0 | 19.4518 | 354.4496 | 1.4211e-14 | 19.4518
2025-03-04 10:00:00 | 24.84 | 23.7738 | 0 | 1.0662 | 353.3834 | -3.3307e-15 | 1.0662
2025-03-04 11:00:00 | 27.96 | 25.7749 | 0 | 2.1851 | 351.1983 | -4.4409e-15 | 2.1851
2025-03-04 12:00:00 | 39.12 | 25.7749 | 0 | 13.3451 | 337.8532 | -2.8422e-14 | 13.3451
2025-03-04 13:00:00 | 48.12 | 23.7738 | 0 | 24.3462 | 313.507 | 1.4211e-14 | 24.3462
2025-03-04 14:00:00 | 51.48 | 19.9082 | 0 | 31.5718 | 281.9352 | 1.4211e-14 | 31.5718
2025-03-04 15:00:00 | 54 | 14.4413 | 0 | 39.5587 | 242.3765 | 1.4211e-14 | 39.5587
2025-03-04 16:00:00 | 64.32 | 7.7457 | 0 | 56.5743 | 185.8022 | 1.4211e-14 | 56.5743
2025-03-04 17:00:00 | 61.92 | 0.27781 | 0 | 61.6422 | 124.16 | -3.5527e-14 | 61.6422
2025-03-04 18:00:00 | 59.16 | 0 | 0 | 59.16 | 65 | 0 | 59.16
2025-03-04 19:00:00 | 51 | 0 | 52.9247 | 0 | 111.5737 | 103.9247 | 51
2025-03-04 20:00:00 | 53.88 | 0 | 0 | 0 | 111.5737 | 53.88 | 53.88
2025-03-04 21:00:00 | 54.72 | 0 | 0 | 0 | 111.5737 | 54.72 | 54.72
2025-03-04 22:00:00 | 46.92 | 0 | 0 | 0 | 111.5737 | 46.92 | 46.92
2025-03-04 23:00:00 | 45.48 | 0 | 0 | 0 | 111.5737 | 45.48 | 45.48
2025-03-05 00:00:00 | 43.68 | 0 | 0 | 0 | 111.5737 | 43.68 | 43.68
2025-03-05 01:00:00 | 34.68 | 0 | 0 | 0 | 111.5737 | 34.68 | 34.68
2025-03-05 02:00:00 | 22.08 | 0 | 0 | 0 | 111.5737 | 22.08 | 22.08
2025-03-05 03:00:00 | 22.56 | 0 | 75 | 0 | 177.5737 | 97.56 | 22.56
2025-03-05 04:00:00 | 28.8 | 0 | 75 | 0 | 243.5737 | 103.8 | 28.8
2025-03-05 05:00:00 | 37.32 | 0 | 75 | 0 | 309.5737 | 112.32 | 37.32
2025-03-05 06:00:00 | 37.8 | 0.47349 | 75 | 0 | 375.5737 | 112.3265 | 37.3265
2025-03-05 07:00:00 | 37.68 | 7.9475 | 0 | 29.7325 | 345.8412 | 2.8422e-14 | 29.7325
2025-03-05 08:00:00 | 38.04 | 14.6486 | 0 | 23.3914 | 322.4498 | 1.0658e-14 | 23.3914
2025-03-05 09:00:00 | 39 | 20.12 | 0 | 18.88 | 303.5698 | 4.2633e-14 | 18.88
2025-03-05 10:00:00 | 38.52 | 23.9888 | 0 | 14.5312 | 289.0386 | -1.7764e-15 | 14.5312
2025-03-05 11:00:00 | 37.2 | 25.9915 | 0 | 11.2085 | 277.8301 | 1.2434e-14 | 11.2085
2025-03-05 12:00:00 | 37.56 | 25.9915 | 0 | 11.5685 | 266.2616 | 1.2434e-14 | 11.5685
2025-03-05 13:00:00 | 38.16 | 23.9888 | 0 | 14.1712 | 252.0904 | -8.8818e-15 | 14.1712
2025-03-05 14:00:00 | 40.2 | 20.12 | 0 | 20.08 | 232.0104 | 4.6185e-14 | 20.08
2025-03-05 15:00:00 | 49.2 | 14.6486 | 0 | 34.5514 | 197.459 | 1.4211e-14 | 34.5514
2025-03-05 16:00:00 | 48.12 | 7.9475 | 0 | 40.1725 | 157.2865 | 2.8422e-14 | 40.1725
2025-03-05 17:00:00 | 47.4 | 0.47349 | 0 | 46.9265 | 110.36 | -2.1316e-14 | 46.9265
2025-03-05 18:00:00 | 45.36 | 0 | 0 | 45.36 | 65 | 0 | 45.36
2025-03-05 19:00:00 | 46.44 | 0 | 61.3517 | 0 | 118.9895 | 107.7917 | 46.44
2025-03-05 20:00:00 | 46.92 | 0 | 0 | 0 | 118.9895 | 46.92 | 46.92
2025-03-05 21:00:00 | 50.04 | 0 | 0 | 0 | 118.9895 | 50.04 | 50.04
2025-03-05 22:00:00 | 49.68 | 0 | 0 | 0 | 118.9895 | 49.68 | 49.68
2025-03-05 23:00:00 | 47.4 | 0 | 0 | 0 | 118.9895 | 47.4 | 47.4
2025-03-06 00:00:00 | 39.6 | 0 | 0 | 0 | 118.9895 | 39.6 | 39.6
2025-03-06 01:00:00 | 37.92 | 0 | 0 | 0 | 118.9895 | 37.92 | 37.92
2025-03-06 02:00:00 | 38.16 | 0 | 0 | 0 | 118.9895 | 38.16 | 38.16
2025-03-06 03:00:00 | 37.92 | 0 | 75 | 0 | 184.9895 | 112.92 | 37.92
2025-03-06 04:00:00 | 30.36 | 0 | 75 | 0 | 250.9895 | 105.36 | 30.36
2025-03-06 05:00:00 | 21.84 | 0 | 75 | 0 | 316.9895 | 96.84 | 21.84
2025-03-06 06:00:00 | 21.96 | 0.67016 | 75 | 0 | 382.9895 | 96.2898 | 21.2898
2025-03-06 07:00:00 | 25.68 | 8.15 | 0 | 17.53 | 365.4595 | -1.4211e-14 | 17.53
2025-03-06 08:00:00 | 39.24 | 14.8563 | 0 | 24.3837 | 341.0758 | -3.5527e-15 | 24.3837
2025-03-06 09:00:00 | 39.36 | 20.332 | 0 | 19.028 | 322.0478 | 7.1054e-15 | 19.028
2025-03-06 10:00:00 | 39.6 | 24.2038 | 0 | 15.3962 | 306.6516 | -3.0198e-14 | 15.3962
2025-03-06 11:00:00 | 41.04 | 26.208 | 0 | 14.832 | 291.8197 | 1.4211e-14 | 14.832
2025-03-06 12:00:00 | 41.52 | 26.208 | 0 | 15.312 | 276.5077 | 1.7764e-14 | 15.312
2025-03-06 13:00:00 | 38.88 | 24.2038 | 0 | 14.6762 | 261.8315 | -2.8422e-14 | 14.6762
2025-03-06 14:00:00 | 43.56 | 20.332 | 0 | 23.228 | 238.6035 | 1.0658e-14 | 23.228
2025-03-06 15:00:00 | 47.16 | 14.8563 | 0 | 32.3037 | 206.2998 | -7.1054e-15 | 32.3037
2025-03-06 16:00:00 | 53.52 | 8.15 | 0 | 45.37 | 160.9298 | -7.1054e-15 | 45.37
2025-03-06 17:00:00 | 51.12 | 0.67016 | 0 | 50.4498 | 110.48 | 2.1316e-14 | 50.4498
2025-03-06 18:00:00 | 45.48 | 0 | 0 | 45.48 | 65 | 0 | 45.48
2025-03-06 19:00:00 | 42.36 | 0 | 75 | 0 | 131 | 117.36 | 42.36
2025-03-06 20:00:00 | 41.52 | 0 | 73.1849 | 0 | 195.4027 | 114.7049 | 41.52
2025-03-06 21:00:00 | 40.68 | 0 | 0 | 0 | 195.4027 | 40.68 | 40.68
2025-03-06 22:00:00 | 38.64 | 0 | 0 | 0 | 195.4027 | 38.64 | 38.64
2025-03-06 23:00:00 | 38.28 | 0 | 0 | 0 | 195.4027 | 38.28 | 38.28
2025-03-07 00:00:00 | 39.12 | 0 | 0 | 0 | 195.4027 | 39.12 | 39.12
2025-03-07 01:00:00 | 38.28 | 0 | 0 | 0 | 195.4027 | 38.28 | 38.28
2025-03-07 02:00:00 | 38.64 | 0 | 75 | 0 | 261.4027 | 113.64 | 38.64
2025-03-07 03:00:00 | 38.52 | 0 | 75 | 0 | 327.4027 | 113.52 | 38.52
2025-03-07 04:00:00 | 38.88 | 0 | 75 | 0 | 393.4027 | 113.88 | 38.88
2025-03-07 05:00:00 | 39 | 0 | 75 | 0 | 459.4027 | 114 | 39
2025-03-07 06:00:00 | 39 | 0.86777 | 75 | 0 | 525.4027 | 113.1322 | 38.1322
2025-03-07 07:00:00 | 38.16 | 8.3531 | 0 | 29.8069 | 495.5959 | -3.1974e-14 | 29.8069
2025-03-07 08:00:00 | 38.4 | 15.0644 | 0 | 23.3356 | 472.2602 | 1.0658e-14 | 23.3356
2025-03-07 09:00:00 | 40.8 | 20.544 | 0 | 20.256 | 452.0043 | 4.6185e-14 | 20.256
2025-03-07 10:00:00 | 55.56 | 24.4188 | 0 | 31.1412 | 420.863 | -2.4869e-14 | 31.1412
2025-03-07 11:00:00 | 62.52 | 26.4245 | 0 | 36.0955 | 384.7675 | -3.5527e-14 | 36.0955
2025-03-07 12:00:00 | 62.16 | 26.4245 | 0 | 35.7355 | 349.0319 | -4.9738e-14 | 35.7355
2025-03-07 13:00:00 | 58.92 | 24.4188 | 0 | 34.5012 | 314.5307 | -2.8422e-14 | 34.5012
2025-03-07 14:00:00 | 56.28 | 20.544 | 0 | 35.736 | 278.7947 | 4.2633e-14 | 35.736
2025-03-07 15:00:00 | 61.2 | 15.0644 | 0 | 46.1356 | 232.6591 | 1.4211e-14 | 46.1356
2025-03-07 16:00:00 | 63.24 | 8.3531 | 0 | 54.8869 | 177.7722 | -2.1316e-14 | 54.8869
2025-03-07 17:00:00 | 57.84 | 0.86777 | 0 | 56.9722 | 120.8 | -4.2633e-14 | 56.9722
2025-03-07 18:00:00 | 55.8 | 0 | 0 | 55.8 | 65 | 0 | 55.8
2025-03-07 19:00:00 | 55.56 | 0 | 0 | 0 | 65 | 55.56 | 55.56
2025-03-07 20:00:00 | 52.92 | 0 | 0 | 0 | 65 | 52.92 | 52.92
2025-03-07 21:00:00 | 50.04 | 0 | 0 | 0 | 65 | 50.04 | 50.04
2025-03-07 22:00:00 | 44.88 | 0 | 0 | 0 | 65 | 44.88 | 44.88
2025-03-07 23:00:00 | 47.88 | 0 | 0 | 0 | 65 | 47.88 | 47.88
2025-03-08 00:00:00 | 42.36 | 0 | 0 | 0 | 65 | 42.36 | 42.36
2025-03-08 01:00:00 | 42.36 | 0 | 0 | 0 | 65 | 42.36 | 42.36
2025-03-08 02:00:00 | 42.12 | 0 | 0 | 0 | 65 | 42.12 | 42.12
2025-03-08 03:00:00 | 42.48 | 0 | 0 | 0 | 65 | 42.48 | 42.48
2025-03-08 04:00:00 | 41.88 | 0 | 0 | 0 | 65 | 41.88 | 41.88
2025-03-08 05:00:00 | 42.48 | 0 | 0 | 0 | 65 | 42.48 | 42.48
2025-03-08 06:00:00 | 43.56 | 1.0662 | 0 | 0 | 65 | 42.4938 | 42.4938
2025-03-08 07:00:00 | 53.28 | 8.5568 | 0 | 0 | 65 | 44.7232 | 44.7232
2025-03-08 08:00:00 | 54.12 | 15.2727 | 0 | 0 | 65 | 38.8473 | 38.8473
2025-03-08 09:00:00 | 58.2 | 20.7561 | 0 | 0 | 65 | 37.4439 | 37.4439
2025-03-08 10:00:00 | 53.88 | 24.6335 | 0 | 0 | 65 | 29.2465 | 29.2465
2025-03-08 11:00:00 | 48.24 | 26.6406 | 0 | 0 | 65 | 21.5994 | 21.5994
2025-03-08 12:00:00 | 45.36 | 26.6406 | 0 | 0 | 65 | 18.7194 | 18.7194
2025-03-08 13:00:00 | 44.4 | 24.6335 | 0 | 0 | 65 | 19.7665 | 19.7665
2025-03-08 14:00:00 | 43.2 | 20.7561 | 0 | 0 | 65 | 22.4439 | 22.4439
2025-03-08 15:00:00 | 44.04 | 15.2727 | 0 | 0 | 65 | 28.7673 | 28.7673
2025-03-08 16:00:00 | 49.56 | 8.5568 | 0 | 0 | 65 | 41.0032 | 41.0032
2025-03-08 17:00:00 | 48.48 | 1.0662 | 0 | 0 | 65 | 47.4138 | 47.4138
2025-03-08 18:00:00 | 46.44 | 0 | 0 | 0 | 65 | 46.44 | 46.44
2025-03-08 19:00:00 | 43.08 | 0 | 0 | 0 | 65 | 43.08 | 43.08
2025-03-08 20:00:00 | 42.12 | 0 | 0 | 0 | 65 | 42.12 | 42.12
2025-03-08 21:00:00 | 42.12 | 0 | 0 | 0 | 65 | 42.12 | 42.12
2025-03-08 22:00:00 | 42.36 | 0 | 0 | 0 | 65 | 42.36 | 42.36
2025-03-08 23:00:00 | 42 | 0 | 0 | 0 | 65 | 42 | 42
2025-03-09 00:00:00 | 42.48 | 0 | 0 | 0 | 65 | 42.48 | 42.48
2025-03-09 01:00:00 | 42.6 | 0 | 0 | 0 | 65 | 42.6 | 42.6
2025-03-09 02:00:00 | 41.4 | 0 | 0 | 0 | 65 | 41.4 | 41.4
2025-03-09 03:00:00 | 42 | 0 | 0 | 0 | 65 | 42 | 42
2025-03-09 04:00:00 | 42.6 | 0 | 0 | 0 | 65 | 42.6 | 42.6
2025-03-09 05:00:00 | 42.24 | 0 | 0 | 0 | 65 | 42.24 | 42.24
2025-03-09 06:00:00 | 41.76 | 1.2655 | 0 | 0 | 65 | 40.4945 | 40.4945
2025-03-09 07:00:00 | 41.88 | 8.7609 | 0 | 0 | 65 | 33.1191 | 33.1191
2025-03-09 08:00:00 | 45.72 | 15.4811 | 0 | 0 | 65 | 30.2389 | 30.2389
2025-03-09 09:00:00 | 44.88 | 20.9681 | 0 | 0 | 65 | 23.9119 | 23.9119
2025-03-09 10:00:00 | 42.24 | 24.8481 | 0 | 0 | 65 | 17.3919 | 17.3919
2025-03-09 11:00:00 | 41.88 | 26.8565 | 0 | 0 | 65 | 15.0235 | 15.0235
2025-03-09 12:00:00 | 41.88 | 26.8565 | 0 | 0 | 65 | 15.0235 | 15.0235
2025-03-09 13:00:00 | 45 | 24.8481 | 0 | 0 | 65 | 20.1519 | 20.1519
2025-03-09 14:00:00 | 55.56 | 20.9681 | 0 | 0 | 65 | 34.5919 | 34.5919
2025-03-09 15:00:00 | 64.08 | 15.4811 | 0 | 0 | 65 | 48.5989 | 48.5989
2025-03-09 16:00:00 | 62.4 | 8.7609 | 75 | 0 | 131 | 128.6391 | 53.6391
2025-03-09 17:00:00 | 79.32 | 1.2655 | 65.9091 | 0 | 189 | 143.9636 | 78.0545
2025-03-09 18:00:00 | 92.88 | 0 | 0 | 0 | 189 | 92.88 | 92.88
2025-03-09 19:00:00 | 92.64 | 0 | 0 | 0 | 189 | 92.64 | 92.64
2025-03-09 20:00:00 | 78.48 | 0 | 0 | 0 | 189 | 78.48 | 78.48
2025-03-09 21:00:00 | 63 | 0 | 0 | 0 | 189 | 63 | 63
2025-03-09 22:00:00 | 61.44 | 0 | 0 | 0 | 189 | 61.44 | 61.44
2025-03-09 23:00:00 | 60 | 0 | 0 | 0 | 189 | 60 | 60
2025-03-10 00:00:00 | 52.68 | 0 | 0 | 0 | 189 | 52.68 | 52.68
2025-03-10 01:00:00 | 48.84 | 0 | 75 | 0 | 255 | 123.84 | 48.84
2025-03-10 02:00:00 | 47.16 | 0 | 75 | 0 | 321 | 122.16 | 47.16
2025-03-10 03:00:00 | 45.72 | 0 | 75 | 0 | 387 | 120.72 | 45.72
2025-03-10 04:00:00 | 45.24 | 0 | 75 | 0 | 453 | 120.24 | 45.24
2025-03-10 05:00:00 | 46.2 | 0 | 75 | 0 | 519 | 121.2 | 46.2
2025-03-10 06:00:00 | 44.64 | 1.4655 | 75 | 0 | 585 | 118.1745 | 43.1745
2025-03-10 07:00:00 | 46.92 | 8.9654 | 0 | 37.9546 | 547.0454 | -2.8422e-14 | 37.9546
2025-03-10 08:00:00 | 49.68 | 15.6897 | 0 | 33.9903 | 513.0551 | -1.4211e-14 | 33.9903
2025-03-10 09:00:00 | 50.28 | 21.18 | 0 | 29.1 | 483.9551 | -7.1054e-15 | 29.1
2025-03-10 10:00:00 | 54.48 | 25.0623 | 0 | 29.4177 | 454.5373 | -1.0658e-14 | 29.4177
2025-03-10 11:00:00 | 59.16 | 27.0719 | 0 | 32.0881 | 422.4492 | 2.8422e-14 | 32.0881
2025-03-10 12:00:00 | 57.36 | 27.0719 | 0 | 30.2881 | 392.1611 | 3.1974e-14 | 30.2881
2025-03-10 13:00:00 | 59.28 | 25.0623 | 0 | 34.2177 | 357.9433 | -7.1054e-15 | 34.2177
2025-03-10 14:00:00 | 56.88 | 21.18 | 0 | 35.7 | 322.2433 | -7.1054e-15 | 35.7
2025-03-10 15:00:00 | 69.48 | 15.6897 | 0 | 53.7903 | 268.453 | 0 | 53.7903
2025-03-10 16:00:00 | 78.12 | 8.9654 | 0 | 62.9585 | 205.4945 | 6.1961 | 69.1546
2025-03-10 17:00:00 | 72.36 | 1.4655 | 0 | 70.8945 | 134.6 | 1.4211e-14 | 70.8945
2025-03-10 18:00:00 | 69.6 | 0 | 0 | 69.6 | 65 | 0 | 69.6
2025-03-10 19:00:00 | 67.44 | 0 | 75 | 0 | 131 | 142.44 | 67.44
2025-03-10 20:00:00 | 64.08 | 0 | 4.8729 | 0 | 135.2882 | 68.9529 | 64.08
2025-03-10 21:00:00 | 60.96 | 0 | 0 | 0 | 135.2882 | 60.96 | 60.96
2025-03-10 22:00:00 | 53.52 | 0 | 0 | 0 | 135.2882 | 53.52 | 53.52
2025-03-10 23:00:00 | 49.8 | 0 | 0 | 0 | 135.2882 | 49.8 | 49.8
2025-03-11 00:00:00 | 45 | 0 | 0 | 0 | 135.2882 | 45 | 45
2025-03-11 01:00:00 | 43.56 | 0 | 0 | 0 | 135.2882 | 43.56 | 43.56
2025-03-11 02:00:00 | 42.24 | 0 | 75 | 0 | 201.2882 | 117.24 | 42.24
2025-03-11 03:00:00 | 41.4 | 0 | 75 | 0 | 267.2882 | 116.4 | 41.4
2025-03-11 04:00:00 | 42.24 | 0 | 75 | 0 | 333.2882 | 117.24 | 42.24
2025-03-11 05:00:00 | 41.4 | 0 | 75 | 0 | 399.2882 | 116.4 | 41.4
2025-03-11 06:00:00 | 41.64 | 1.6661 | 75 | 0 | 465.2882 | 114.9739 | 39.9739
2025-03-11 07:00:00 | 52.8 | 9.1702 | 0 | 43.6298 | 421.6584 | 3.5527e-14 | 43.6298
2025-03-11 08:00:00 | 51.24 | 15.8982 | 0 | 35.3418 | 386.3166 | 2.1316e-14 | 35.3418
2025-03-11 09:00:00 | 51.72 | 21.3916 | 0 | 30.3284 | 355.9882 | 2.8422e-14 | 30.3284
2025-03-11 10:00:00 | 48.72 | 25.276 | 0 | 23.444 | 332.5443 | -4.2633e-14 | 23.444
2025-03-11 11:00:00 | 46.2 | 27.2868 | 0 | 18.9132 | 313.631 | -4.6185e-14 | 18.9132
2025-03-11 12:00:00 | 43.44 | 27.2868 | 0 | 16.1532 | 297.4778 | -4.9738e-14 | 16.1532
2025-03-11 13:00:00 | 42.12 | 25.276 | 0 | 16.844 | 280.6339 | -4.6185e-14 | 16.844
2025-03-11 14:00:00 | 42 | 21.3916 | 0 | 20.6084 | 260.0255 | 3.1974e-14 | 20.6084
2025-03-11 15:00:00 | 48.12 | 15.8982 | 0 | 32.2218 | 227.8037 | 2.1316e-14 | 32.2218
2025-03-11 16:00:00 | 57.24 | 9.1702 | 0 | 48.0698 | 179.7339 | 4.2633e-14 | 48.0698
2025-03-11 17:00:00 | 59.28 | 1.6661 | 0 | 57.6139 | 122.12 | 3.5527e-14 | 57.6139
2025-03-11 18:00:00 | 57.12 | 0 | 0 | 57.12 | 65 | 0 | 57.12
2025-03-11 19:00:00 | 59.88 | 0 | 19.4343 | 0 | 82.1022 | 79.3143 | 59.88
2025-03-11 20:00:00 | 58.32 | 0 | 0 | 0 | 82.1022 | 58.32 | 58.32
2025-03-11 21:00:00 | 47.16 | 0 | 0 | 0 | 82.1022 | 47.16 | 47.16
2025-03-11 22:00:00 | 44.64 | 0 | 0 | 0 | 82.1022 | 44.64 | 44.64
2025-03-11 23:00:00 | 42.84 | 0 | 0 | 0 | 82.1022 | 42.84 | 42.84
2025-03-12 00:00:00 | 41.76 | 0 | 0 | 0 | 82.1022 | 41.76 | 41.76
2025-03-12 01:00:00 | 42.24 | 0 | 0 | 0 | 82.1022 | 42.24 | 42.24
2025-03-12 02:00:00 | 41.4 | 0 | 0 | 0 | 82.1022 | 41.4 | 41.4
2025-03-12 03:00:00 | 42.12 | 0 | 75 | 0 | 148.1022 | 117.12 | 42.12
2025-03-12 04:00:00 | 41.16 | 0 | 75 | 0 | 214.1022 | 116.16 | 41.16
2025-03-12 05:00:00 | 31.8 | 0 | 75 | 0 | 280.1022 | 106.8 | 31.8
2025-03-12 06:00:00 | 22.2 | 1.8673 | 75 | 0 | 346.1022 | 95.3327 | 20.3327
2025-03-12 07:00:00 | 23.64 | 9.3753 | 0 | 14.2647 | 331.8374 | 1.954e-14 | 14.2647
2025-03-12 08:00:00 | 44.28 | 16.1067 | 0 | 28.1733 | 303.6641 | -2.8422e-14 | 28.1733
2025-03-12 09:00:00 | 47.88 | 21.6029 | 0 | 26.2771 | 277.387 | 4.2633e-14 | 26.2771
2025-03-12 10:00:00 | 46.68 | 25.4893 | 0 | 21.1907 | 256.1964 | 3.908e-14 | 21.1907
2025-03-12 11:00:00 | 44.4 | 27.5011 | 0 | 16.8989 | 239.2974 | -3.1974e-14 | 16.8989
2025-03-12 12:00:00 | 40.2 | 27.5011 | 0 | 12.6989 | 226.5985 | -2.6645e-14 | 12.6989
2025-03-12 13:00:00 | 43.56 | 25.4893 | 0 | 18.0707 | 208.5278 | 4.2633e-14 | 18.0707
2025-03-12 14:00:00 | 44.64 | 21.6029 | 0 | 23.0371 | 185.4907 | 3.908e-14 | 23.0371
2025-03-12 15:00:00 | 42 | 16.1067 | 0 | 25.8933 | 159.5975 | -2.8422e-14 | 25.8933
2025-03-12 16:00:00 | 34.8 | 9.3753 | 0 | 25.4247 | 134.1727 | 1.7764e-14 | 25.4247
2025-03-12 17:00:00 | 36.48 | 1.8673 | 0 | 34.6127 | 99.56 | 1.4211e-14 | 34.6127
2025-03-12 18:00:00 | 34.56 | 0 | 0 | 34.56 | 65 | 0 | 34.56
2025-03-12 19:00:00 | 34.8 | 0 | 60.8625 | 0 | 118.559 | 95.6625 | 34.8
2025-03-12 20:00:00 | 35.64 | 0 | 0 | 0 | 118.559 | 35.64 | 35.64
2025-03-12 21:00:00 | 35.16 | 0 | 0 | 0 | 118.559 | 35.16 | 35.16
2025-03-12 22:00:00 | 35.16 | 0 | 0 | 0 | 118.559 | 35.16 | 35.16
2025-03-12 23:00:00 | 34.8 | 0 | 0 | 0 | 118.559 | 34.8 | 34.8
2025-03-13 00:00:00 | 19.92 | 0 | 0 | 0 | 118.559 | 19.92 | 19.92
2025-03-13 01:00:00 | 18.72 | 0 | 0 | 0 | 118.559 | 18.72 | 18.72
2025-03-13 02:00:00 | 18.96 | 0 | 0 | 0 | 118.559 | 18.96 | 18.96
2025-03-13 03:00:00 | 18.96 | 0 | 75 | 0 | 184.559 | 93.96 | 18.96
2025-03-13 04:00:00 | 19.8 | 0 | 75 | 0 | 250.559 | 94.8 | 19.8
2025-03-13 05:00:00 | 18.84 | 0 | 75 | 0 | 316.559 | 93.84 | 18.84
2025-03-13 06:00:00 | 19.08 | 2.069 | 75 | 0 | 382.559 | 92.011 | 17.011
2025-03-13 07:00:00 | 30 | 9.5805 | 0 | 20.4195 | 362.1395 | 1.7764e-14 | 20.4195
2025-03-13 08:00:00 | 38.64 | 16.315 | 0 | 22.325 | 339.8145 | 1.4211e-14 | 22.325
2025-03-13 09:00:00 | 39.96 | 21.8138 | 0 | 18.1462 | 321.6683 | -1.0658e-14 | 18.1462
2025-03-13 10:00:00 | 43.2 | 25.702 | 0 | 17.498 | 304.1703 | 2.4869e-14 | 17.498
2025-03-13 11:00:00 | 46.8 | 27.7147 | 0 | 19.0853 | 285.085 | -3.5527e-14 | 19.0853
2025-03-13 12:00:00 | 45.72 | 27.7147 | 0 | 18.0053 | 267.0797 | -3.1974e-14 | 18.0053
2025-03-13 13:00:00 | 48.24 | 25.702 | 0 | 22.538 | 244.5417 | 2.1316e-14 | 22.538
2025-03-13 14:00:00 | 47.16 | 21.8138 | 0 | 25.3462 | 219.1955 | -1.7764e-14 | 25.3462
2025-03-13 15:00:00 | 48.48 | 16.315 | 0 | 32.165 | 187.0305 | 7.1054e-15 | 32.165
2025-03-13 16:00:00 | 47.88 | 9.5805 | 0 | 38.2995 | 148.731 | 1.4211e-14 | 38.2995
2025-03-13 17:00:00 | 44.4 | 2.069 | 0 | 42.331 | 106.4 | 0 | 42.331
2025-03-13 18:00:00 | 41.4 | 0 | 0 | 41.4 | 65 | 0 | 41.4
2025-03-13 19:00:00 | 40.8 | 0 | 0 | 0 | 65 | 40.8 | 40.8
2025-03-13 20:00:00 | 38.04 | 0 | 0 | 0 | 65 | 38.04 | 38.04
2025-03-13 21:00:00 | 39.24 | 0 | 0 | 0 | 65 | 39.24 | 39.24
2025-03-13 22:00:00 | 38.28 | 0 | 0 | 0 | 65 | 38.28 | 38.28
2025-03-13 23:00:00 | 38.76 | 0 | 0 | 0 | 65 | 38.76 | 38.76
2025-03-14 00:00:00 | 38.04 | 0 | 0 | 0 | 65 | 38.04 | 38.04
2025-03-14 01:00:00 | 38.52 | 0 | 0 | 0 | 65 | 38.52 | 38.52
2025-03-14 02:00:00 | 38.76 | 0 | 0 | 0 | 65 | 38.76 | 38.76
2025-03-14 03:00:00 | 38.64 | 0 | 72.5928 | 0 | 128.8817 | 111.2328 | 38.64
2025-03-14 04:00:00 | 38.16 | 0 | 75 | 0 | 194.8817 | 113.16 | 38.16
2025-03-14 05:00:00 | 38.76 | 0 | 75 | 0 | 260.8817 | 113.76 | 38.76
2025-03-14 06:00:00 | 38.4 | 2.2712 | 75 | 0 | 326.8817 | 111.1288 | 36.1288
2025-03-14 07:00:00 | 40.44 | 9.7858 | 0 | 30.6542 | 296.2274 | 1.0658e-14 | 30.6542
2025-03-14 08:00:00 | 34.56 | 16.5231 | 0 | 18.0369 | 278.1905 | -1.7764e-14 | 18.0369
2025-03-14 09:00:00 | 21.84 | 22.0242 | 0.18419 | 0 | 278.3526 | -8.3267e-17 | -0.18419
2025-03-14 10:00:00 | 28.44 | 25.914 | 0 | 2.526 | 275.8266 | 4.4409e-16 | 2.526
2025-03-14 11:00:00 | 32.76 | 27.9275 | 0 | 4.8325 | 270.9942 | -2.6645e-15 | 4.8325
2025-03-14 12:00:00 | 48.72 | 27.9275 | 0 | 20.7925 | 250.2017 | 2.8422e-14 | 20.7925
2025-03-14 13:00:00 | 46.68 | 25.914 | 0 | 20.766 | 229.4357 | 3.908e-14 | 20.766
2025-03-14 14:00:00 | 51 | 22.0242 | 0 | 28.9758 | 200.4599 | -2.1316e-14 | 28.9758
2025-03-14 15:00:00 | 46.56 | 16.5231 | 0 | 30.0369 | 170.4231 | -1.7764e-14 | 30.0369
2025-03-14 16:00:00 | 41.04 | 9.7858 | 0 | 31.2542 | 139.1688 | 1.4211e-14 | 31.2542
2025-03-14 17:00:00 | 38.88 | 2.2712 | 0 | 36.6088 | 102.56 | 3.5527e-14 | 36.6088
2025-03-14 18:00:00 | 37.56 | 0 | 0 | 37.56 | 65 | 0 | 37.56
2025-03-14 19:00:00 | 38.64 | 0 | 0 | 0 | 65 | 38.64 | 38.64
2025-03-14 20:00:00 | 38.88 | 0 | 0 | 0 | 65 | 38.88 | 38.88
2025-03-14 21:00:00 | 38.52 | 0 | 0 | 0 | 65 | 38.52 | 38.52
2025-03-14 22:00:00 | 39.12 | 0 | 0 | 0 | 65 | 39.12 | 39.12
2025-03-14 23:00:00 | 26.4 | 0 | 0 | 0 | 65 | 26.4 | 26.4
2025-03-15 00:00:00 | 21.48 | 0 | 0 | 0 | 65 | 21.48 | 21.48
2025-03-15 01:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-03-15 02:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-03-15 03:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-03-15 04:00:00 | 26.88 | 0 | 0 | 0 | 65 | 26.88 | 26.88
2025-03-15 05:00:00 | 39 | 0 | 0 | 0 | 65 | 39 | 39
2025-03-15 06:00:00 | 39.24 | 2.4737 | 0 | 0 | 65 | 36.7663 | 36.7663
2025-03-15 07:00:00 | 42.84 | 9.9911 | 0 | 0 | 65 | 32.8489 | 32.8489
2025-03-15 08:00:00 | 53.64 | 16.7309 | 0 | 0 | 65 | 36.9091 | 36.9091
2025-03-15 09:00:00 | 56.76 | 22.234 | 0 | 0 | 65 | 34.526 | 34.526
2025-03-15 10:00:00 | 50.64 | 26.1253 | 0 | 0 | 65 | 24.5147 | 24.5147
2025-03-15 11:00:00 | 46.68 | 28.1395 | 0 | 0 | 65 | 18.5405 | 18.5405
2025-03-15 12:00:00 | 44.28 | 28.1395 | 0 | 0 | 65 | 16.1405 | 16.1405
2025-03-15 13:00:00 | 41.16 | 26.1253 | 0 | 0 | 65 | 15.0347 | 15.0347
2025-03-15 14:00:00 | 40.92 | 22.234 | 0 | 0 | 65 | 18.686 | 18.686
2025-03-15 15:00:00 | 37.8 | 16.7309 | 0 | 0 | 65 | 21.0691 | 21.0691
2025-03-15 16:00:00 | 40.44 | 9.9911 | 0 | 0 | 65 | 30.4489 | 30.4489
2025-03-15 17:00:00 | 37.8 | 2.4737 | 0 | 0 | 65 | 35.3263 | 35.3263
2025-03-15 18:00:00 | 38.76 | 0 | 0 | 0 | 65 | 38.76 | 38.76
2025-03-15 19:00:00 | 38.52 | 0 | 0 | 0 | 65 | 38.52 | 38.52
2025-03-15 20:00:00 | 38.88 | 0 | 0 | 0 | 65 | 38.88 | 38.88
2025-03-15 21:00:00 | 41.76 | 0 | 0 | 0 | 65 | 41.76 | 41.76
2025-03-15 22:00:00 | 43.44 | 0 | 0 | 0 | 65 | 43.44 | 43.44
2025-03-15 23:00:00 | 46.08 | 0 | 0 | 0 | 65 | 46.08 | 46.08
2025-03-16 00:00:00 | 48.12 | 0 | 0 | 0 | 65 | 48.12 | 48.12
2025-03-16 01:00:00 | 49.68 | 0 | 0 | 0 | 65 | 49.68 | 49.68
2025-03-16 02:00:00 | 50.52 | 0 | 0 | 0 | 65 | 50.52 | 50.52
2025-03-16 03:00:00 | 49.2 | 0 | 0 | 0 | 65 | 49.2 | 49.2
2025-03-16 04:00:00 | 50.76 | 0 | 0 | 0 | 65 | 50.76 | 50.76
2025-03-16 05:00:00 | 51.24 | 0 | 0 | 0 | 65 | 51.24 | 51.24
2025-03-16 06:00:00 | 51.12 | 2.6766 | 0 | 0 | 65 | 48.4434 | 48.4434
2025-03-16 07:00:00 | 54 | 10.1963 | 0 | 0 | 65 | 43.8037 | 43.8037
2025-03-16 08:00:00 | 56.88 | 16.9383 | 0 | 0 | 65 | 39.9417 | 39.9417
2025-03-16 09:00:00 | 65.28 | 22.4432 | 0 | 0 | 65 | 42.8368 | 42.8368
2025-03-16 10:00:00 | 61.68 | 26.3357 | 0 | 0 | 65 | 35.3443 | 35.3443
2025-03-16 11:00:00 | 61.68 | 28.3506 | 0 | 0 | 65 | 33.3294 | 33.3294
2025-03-16 12:00:00 | 59.76 | 28.3506 | 0 | 0 | 65 | 31.4094 | 31.4094
2025-03-16 13:00:00 | 52.92 | 26.3357 | 0 | 0 | 65 | 26.5843 | 26.5843
2025-03-16 14:00:00 | 51.24 | 22.4432 | 0 | 0 | 65 | 28.7968 | 28.7968
2025-03-16 15:00:00 | 47.4 | 16.9383 | 0 | 0 | 65 | 30.4617 | 30.4617
2025-03-16 16:00:00 | 47.88 | 10.1963 | 0 | 0 | 65 | 37.6837 | 37.6837
2025-03-16 17:00:00 | 52.08 | 2.6766 | 0 | 0 | 65 | 49.4034 | 49.4034
2025-03-16 18:00:00 | 59.28 | 0 | 0 | 0 | 65 | 59.28 | 59.28
2025-03-16 19:00:00 | 64.68 | 0 | 0 | 0 | 65 | 64.68 | 64.68
2025-03-16 20:00:00 | 58.44 | 0 | 0 | 0 | 65 | 58.44 | 58.44
2025-03-16 21:00:00 | 48.84 | 0 | 0 | 0 | 65 | 48.84 | 48.84
2025-03-16 22:00:00 | 42 | 0 | 0 | 0 | 65 | 42 | 42
2025-03-16 23:00:00 | 41.64 | 0 | 0 | 0 | 65 | 41.64 | 41.64
2025-03-17 00:00:00 | 39.6 | 0 | 0 | 0 | 65 | 39.6 | 39.6
2025-03-17 01:00:00 | 35.64 | 0 | 0 | 0 | 65 | 35.64 | 35.64
2025-03-17 02:00:00 | 21.72 | 0 | 0 | 0 | 65 | 21.72 | 21.72
2025-03-17 03:00:00 | 22.56 | 0 | 0 | 0 | 65 | 22.56 | 22.56
2025-03-17 04:00:00 | 22.56 | 0 | 47.6199 | 0 | 106.9055 | 70.1799 | 22.56
2025-03-17 05:00:00 | 22.56 | 0 | 75 | 0 | 172.9055 | 97.56 | 22.56
2025-03-17 06:00:00 | 21.96 | 2.8796 | 75 | 0 | 238.9055 | 94.0804 | 19.0804
2025-03-17 07:00:00 | 22.08 | 10.4014 | 0 | 11.6786 | 227.2269 | 7.1054e-15 | 11.6786
2025-03-17 08:00:00 | 22.44 | 17.1453 | 0 | 5.2947 | 221.9322 | 4.4409e-15 | 5.2947
2025-03-17 09:00:00 | 22.56 | 22.6516 | 0.091612 | 0 | 222.0128 | -4.1633e-17 | -0.091612
2025-03-17 10:00:00 | 21.84 | 26.5452 | 4.7052 | 0 | 226.1534 | -8.8818e-16 | -4.7052
2025-03-17 11:00:00 | 22.56 | 28.5606 | 6.0006 | 0 | 231.4339 | -8.8818e-16 | -6.0006
2025-03-17 12:00:00 | 22.08 | 28.5606 | 6.4806 | 0 | 237.1369 | -8.8818e-16 | -6.4806
2025-03-17 13:00:00 | 28.08 | 26.5452 | 0 | 1.5348 | 235.602 | -2.4425e-15 | 1.5348
2025-03-17 14:00:00 | 45.6 | 22.6516 | 0 | 22.9484 | 212.6537 | -1.7764e-14 | 22.9484
2025-03-17 15:00:00 | 47.4 | 17.1453 | 0 | 30.2547 | 182.3989 | -4.9738e-14 | 30.2547
2025-03-17 16:00:00 | 45.48 | 10.4014 | 0 | 35.0786 | 147.3204 | 7.1054e-15 | 35.0786
2025-03-17 17:00:00 | 43.8 | 2.8796 | 0 | 40.9204 | 106.4 | 4.2633e-14 | 40.9204
2025-03-17 18:00:00 | 41.4 | 0 | 0 | 41.4 | 65 | 0 | 41.4
2025-03-17 19:00:00 | 37.56 | 0 | 0 | 0 | 65 | 37.56 | 37.56
2025-03-17 20:00:00 | 32.28 | 0 | 23.4909 | 0 | 85.672 | 55.7709 | 32.28
2025-03-17 21:00:00 | 36 | 0 | 0 | 0 | 85.672 | 36 | 36
2025-03-17 22:00:00 | 29.16 | 0 | 0 | 0 | 85.672 | 29.16 | 29.16
2025-03-17 23:00:00 | 25.44 | 0 | 0 | 0 | 85.672 | 25.44 | 25.44
2025-03-18 00:00:00 | 25.68 | 0 | 0 | 0 | 85.672 | 25.68 | 25.68
2025-03-18 01:00:00 | 24.12 | 0 | 0 | 0 | 85.672 | 24.12 | 24.12
2025-03-18 02:00:00 | 22.68 | 0 | 0 | 0 | 85.672 | 22.68 | 22.68
2025-03-18 03:00:00 | 23.4 | 0 | 0 | 0 | 85.672 | 23.4 | 23.4
2025-03-18 04:00:00 | 22.92 | 0 | 75 | 0 | 151.672 | 97.92 | 22.92
2025-03-18 05:00:00 | 23.16 | 0 | 75 | 0 | 217.672 | 98.16 | 23.16
2025-03-18 06:00:00 | 22.68 | 3.0829 | 75 | 0 | 283.672 | 94.5971 | 19.5971
2025-03-18 07:00:00 | 22.92 | 10.6063 | 0 | 12.3137 | 271.3583 | -3.5527e-14 | 12.3137
2025-03-18 08:00:00 | 21.96 | 17.3517 | 0 | 4.6083 | 266.75 | 3.5527e-15 | 4.6083
2025-03-18 09:00:00 | 22.56 | 22.8592 | 0.29924 | 0 | 267.0134 | 1.6653e-16 | -0.29924
2025-03-18 10:00:00 | 40.68 | 26.7537 | 0 | 13.9263 | 253.087 | -3.5527e-15 | 13.9263
2025-03-18 11:00:00 | 40.68 | 28.7696 | 0 | 11.9104 | 241.1766 | -3.908e-14 | 11.9104
2025-03-18 12:00:00 | 39.96 | 28.7696 | 0 | 11.1904 | 229.9862 | -3.7303e-14 | 11.1904
2025-03-18 13:00:00 | 39.36 | 26.7537 | 0 | 12.6063 | 217.3799 | -5.3291e-15 | 12.6063
2025-03-18 14:00:00 | 38.04 | 22.8592 | 0 | 15.1808 | 202.1991 | 4.0856e-14 | 15.1808
2025-03-18 15:00:00 | 38.52 | 17.3517 | 0 | 21.1683 | 181.0308 | 2.4869e-14 | 21.1683
2025-03-18 16:00:00 | 38.16 | 10.6063 | 0 | 27.5537 | 153.4771 | -4.2633e-14 | 27.5537
2025-03-18 17:00:00 | 43.44 | 3.0829 | 0 | 40.3571 | 113.12 | -2.1316e-14 | 40.3571
2025-03-18 18:00:00 | 48.12 | 0 | 0 | 48.12 | 65 | 0 | 48.12
2025-03-18 19:00:00 | 50.76 | 0 | 75 | 0 | 131 | 125.76 | 50.76
2025-03-18 20:00:00 | 45.84 | 0 | 10.3728 | 0 | 140.128 | 56.2128 | 45.84
2025-03-18 21:00:00 | 43.44 | 0 | 0 | 0 | 140.128 | 43.44 | 43.44
2025-03-18 22:00:00 | 39.72 | 0 | 0 | 0 | 140.128 | 39.72 | 39.72
2025-03-18 23:00:00 | 39 | 0 | 0 | 0 | 140.128 | 39 | 39
2025-03-19 00:00:00 | 30.72 | 0 | 0 | 0 | 140.128 | 30.72 | 30.72
2025-03-19 01:00:00 | 22.68 | 0 | 0 | 0 | 140.128 | 22.68 | 22.68
2025-03-19 02:00:00 | 22.44 | 0 | 0 | 0 | 140.128 | 22.44 | 22.44
2025-03-19 03:00:00 | 22.2 | 0 | 75 | 0 | 206.128 | 97.2 | 22.2
2025-03-19 04:00:00 | 36.48 | 0 | 75 | 0 | 272.128 | 111.48 | 36.48
2025-03-19 05:00:00 | 53.04 | 0 | 75 | 0 | 338.128 | 128.04 | 53.04
2025-03-19 06:00:00 | 52.68 | 3.2862 | 75 | 0 | 404.128 | 124.3938 | 49.3938
2025-03-19 07:00:00 | 54.36 | 10.811 | 0 | 43.549 | 360.579 | 3.5527e-14 | 43.549
2025-03-19 08:00:00 | 44.04 | 17.5575 | 0 | 26.4825 | 334.0965 | -1.4211e-14 | 26.4825
2025-03-19 09:00:00 | 37.44 | 23.066 | 0 | 14.374 | 319.7225 | -3.3751e-14 | 14.374
2025-03-19 10:00:00 | 36.96 | 26.9611 | 0 | 9.9989 | 309.7236 | -3.5527e-15 | 9.9989
2025-03-19 11:00:00 | 36.6 | 28.9774 | 0 | 7.6226 | 302.1009 | 0 | 7.6226
2025-03-19 12:00:00 | 37.32 | 28.9774 | 0 | 8.3426 | 293.7583 | -1.7764e-15 | 8.3426
2025-03-19 13:00:00 | 42 | 26.9611 | 0 | 15.0389 | 278.7194 | 1.5987e-14 | 15.0389
2025-03-19 14:00:00 | 54.48 | 23.066 | 0 | 31.414 | 247.3054 | -3.5527e-14 | 31.414
2025-03-19 15:00:00 | 59.52 | 17.5575 | 0 | 41.9625 | 205.3429 | -1.4211e-14 | 41.9625
2025-03-19 16:00:00 | 56.4 | 10.811 | 0 | 45.589 | 159.7538 | 3.5527e-14 | 45.589
2025-03-19 17:00:00 | 52.68 | 3.2862 | 0 | 49.3938 | 110.36 | -1.4211e-14 | 49.3938
2025-03-19 18:00:00 | 45.36 | 0 | 0 | 45.36 | 65 | 0 | 45.36
2025-03-19 19:00:00 | 38.16 | 0 | 62.3509 | 0 | 119.8688 | 100.5109 | 38.16
2025-03-19 20:00:00 | 38.88 | 0 | 0 | 0 | 119.8688 | 38.88 | 38.88
2025-03-19 21:00:00 | 36.72 | 0 | 0 | 0 | 119.8688 | 36.72 | 36.72
2025-03-19 22:00:00 | 37.56 | 0 | 0 | 0 | 119.8688 | 37.56 | 37.56
2025-03-19 23:00:00 | 37.32 | 0 | 0 | 0 | 119.8688 | 37.32 | 37.32
2025-03-20 00:00:00 | 36.84 | 0 | 0 | 0 | 119.8688 | 36.84 | 36.84
2025-03-20 01:00:00 | 37.56 | 0 | 0 | 0 | 119.8688 | 37.56 | 37.56
2025-03-20 02:00:00 | 36.96 | 0 | 0 | 0 | 119.8688 | 36.96 | 36.96
2025-03-20 03:00:00 | 36.84 | 0 | 75 | 0 | 185.8688 | 111.84 | 36.84
2025-03-20 04:00:00 | 37.56 | 0 | 75 | 0 | 251.8688 | 112.56 | 37.56
2025-03-20 05:00:00 | 37.32 | 0 | 75 | 0 | 317.8688 | 112.32 | 37.32
2025-03-20 06:00:00 | 21.96 | 3.4895 | 75 | 0 | 383.8688 | 93.4705 | 18.4705
2025-03-20 07:00:00 | 23.16 | 11.0152 | 0 | 12.1448 | 371.724 | -1.0658e-14 | 12.1448
2025-03-20 08:00:00 | 27.84 | 17.7626 | 0 | 10.0774 | 361.6466 | 4.6185e-14 | 10.0774
2025-03-20 09:00:00 | 36.36 | 23.2718 | 0 | 13.0882 | 348.5584 | 4.9738e-14 | 13.0882
2025-03-20 10:00:00 | 36.24 | 27.1674 | 0 | 9.0726 | 339.4857 | 0 | 9.0726
2025-03-20 11:00:00 | 35.76 | 29.1839 | 0 | 6.5761 | 332.9096 | 8.8818e-16 | 6.5761
2025-03-20 12:00:00 | 40.08 | 29.1839 | 0 | 10.8961 | 322.0135 | 1.0658e-14 | 10.8961
2025-03-20 13:00:00 | 46.2 | 27.1674 | 0 | 19.0326 | 302.9809 | 3.908e-14 | 19.0326
2025-03-20 14:00:00 | 51 | 23.2718 | 0 | 27.7282 | 275.2527 | 4.9738e-14 | 27.7282
2025-03-20 15:00:00 | 64.68 | 17.7626 | 0 | 46.9174 | 228.3352 | 4.9738e-14 | 46.9174
2025-03-20 16:00:00 | 65.76 | 11.0152 | 0 | 54.7448 | 173.5905 | -7.1054e-15 | 54.7448
2025-03-20 17:00:00 | 59.64 | 3.4895 | 0 | 56.1505 | 117.44 | 7.1054e-15 | 56.1505
2025-03-20 18:00:00 | 52.44 | 0 | 0 | 52.44 | 65 | 0 | 52.44
2025-03-20 19:00:00 | 48.36 | 0 | 75 | 0 | 131 | 123.36 | 48.36
2025-03-20 20:00:00 | 46.08 | 0 | 25.0217 | 0 | 153.0191 | 71.1017 | 46.08
2025-03-20 21:00:00 | 44.04 | 0 | 0 | 0 | 153.0191 | 44.04 | 44.04
2025-03-20 22:00:00 | 41.04 | 0 | 0 | 0 | 153.0191 | 41.04 | 41.04
2025-03-20 23:00:00 | 39.96 | 0 | 0 | 0 | 153.0191 | 39.96 | 39.96
2025-03-21 00:00:00 | 39.6 | 0 | 0 | 0 | 153.0191 | 39.6 | 39.6
2025-03-21 01:00:00 | 38.88 | 0 | 0 | 0 | 153.0191 | 38.88 | 38.88
2025-03-21 02:00:00 | 39.36 | 0 | 0 | 0 | 153.0191 | 39.36 | 39.36
2025-03-21 03:00:00 | 39.12 | 0 | 75 | 0 | 219.0191 | 114.12 | 39.12
2025-03-21 04:00:00 | 39.12 | 0 | 75 | 0 | 285.0191 | 114.12 | 39.12
2025-03-21 05:00:00 | 38.76 | 0 | 75 | 0 | 351.0191 | 113.76 | 38.76
2025-03-21 06:00:00 | 39.24 | 3.6928 | 75 | 0 | 417.0191 | 110.5472 | 35.5472
2025-03-21 07:00:00 | 38.16 | 11.2191 | 0 | 26.9409 | 390.0782 | 1.7764e-14 | 26.9409
2025-03-21 08:00:00 | 37.08 | 17.9669 | 0 | 19.1131 | 370.9651 | -4.6185e-14 | 19.1131
2025-03-21 09:00:00 | 42.24 | 23.4765 | 0 | 18.7635 | 352.2016 | 4.6185e-14 | 18.7635
2025-03-21 10:00:00 | 48 | 27.3724 | 0 | 20.6276 | 331.5741 | 2.4869e-14 | 20.6276
2025-03-21 11:00:00 | 51.72 | 29.3891 | 0 | 22.3309 | 309.2431 | -3.908e-14 | 22.3309
2025-03-21 12:00:00 | 52.92 | 29.3891 | 0 | 23.5309 | 285.7122 | -3.5527e-14 | 23.5309
2025-03-21 13:00:00 | 50.52 | 27.3724 | 0 | 23.1476 | 262.5646 | 2.8422e-14 | 23.1476
2025-03-21 14:00:00 | 55.32 | 23.4765 | 0 | 31.8435 | 230.7212 | 4.2633e-14 | 31.8435
2025-03-21 15:00:00 | 57.36 | 17.9669 | 0 | 39.3931 | 191.3281 | -4.2633e-14 | 39.3931
2025-03-21 16:00:00 | 49.44 | 11.2191 | 0 | 38.2209 | 153.1072 | 2.1316e-14 | 38.2209
2025-03-21 17:00:00 | 48.24 | 3.6928 | 0 | 44.5472 | 108.56 | 0 | 44.5472
2025-03-21 18:00:00 | 43.56 | 0 | 0 | 43.56 | 65 | 0 | 43.56
2025-03-21 19:00:00 | 43.08 | 0 | 0 | 0 | 65 | 43.08 | 43.08
2025-03-21 20:00:00 | 41.64 | 0 | 0 | 0 | 65 | 41.64 | 41.64
2025-03-21 21:00:00 | 41.28 | 0 | 0 | 0 | 65 | 41.28 | 41.28
2025-03-21 22:00:00 | 42.12 | 0 | 0 | 0 | 65 | 42.12 | 42.12
2025-03-21 23:00:00 | 41.64 | 0 | 0 | 0 | 65 | 41.64 | 41.64
2025-03-22 00:00:00 | 41.52 | 0 | 0 | 0 | 65 | 41.52 | 41.52
2025-03-22 01:00:00 | 41.52 | 0 | 0 | 0 | 65 | 41.52 | 41.52
2025-03-22 02:00:00 | 41.4 | 0 | 0 | 0 | 65 | 41.4 | 41.4
2025-03-22 03:00:00 | 41.88 | 0 | 0 | 0 | 65 | 41.88 | 41.88
2025-03-22 04:00:00 | 42.36 | 0 | 0 | 0 | 65 | 42.36 | 42.36
2025-03-22 05:00:00 | 25.8 | 0 | 0 | 0 | 65 | 25.8 | 25.8
2025-03-22 06:00:00 | 21.96 | 3.896 | 0 | 0 | 65 | 18.064 | 18.064
2025-03-22 07:00:00 | 32.4 | 11.4224 | 0 | 0 | 65 | 20.9776 | 20.9776
2025-03-22 08:00:00 | 50.4 | 18.1705 | 0 | 0 | 65 | 32.2295 | 32.2295
2025-03-22 09:00:00 | 64.44 | 23.6802 | 0 | 0 | 65 | 40.7598 | 40.7598
2025-03-22 10:00:00 | 61.56 | 27.5762 | 0 | 0 | 65 | 33.9838 | 33.9838
2025-03-22 11:00:00 | 55.08 | 29.5929 | 0 | 0 | 65 | 25.4871 | 25.4871
2025-03-22 12:00:00 | 52.92 | 29.5929 | 0 | 0 | 65 | 23.3271 | 23.3271
2025-03-22 13:00:00 | 51.72 | 27.5762 | 0 | 0 | 65 | 24.1438 | 24.1438
2025-03-22 14:00:00 | 51.96 | 23.6802 | 0 | 0 | 65 | 28.2798 | 28.2798
2025-03-22 15:00:00 | 50.88 | 18.1705 | 0 | 0 | 65 | 32.7095 | 32.7095
2025-03-22 16:00:00 | 47.64 | 11.4224 | 0 | 0 | 65 | 36.2176 | 36.2176
2025-03-22 17:00:00 | 47.88 | 3.896 | 0 | 0 | 65 | 43.984 | 43.984
2025-03-22 18:00:00 | 46.32 | 0 | 0 | 0 | 65 | 46.32 | 46.32
2025-03-22 19:00:00 | 44.28 | 0 | 0 | 0 | 65 | 44.28 | 44.28
2025-03-22 20:00:00 | 40.2 | 0 | 0 | 0 | 65 | 40.2 | 40.2
2025-03-22 21:00:00 | 39.6 | 0 | 0 | 0 | 65 | 39.6 | 39.6
2025-03-22 22:00:00 | 38.16 | 0 | 0 | 0 | 65 | 38.16 | 38.16
2025-03-22 23:00:00 | 39.72 | 0 | 0 | 0 | 65 | 39.72 | 39.72
2025-03-23 00:00:00 | 38.28 | 0 | 0 | 0 | 65 | 38.28 | 38.28
2025-03-23 01:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-03-23 02:00:00 | 38.88 | 0 | 0 | 0 | 65 | 38.88 | 38.88
2025-03-23 03:00:00 | 38.28 | 0 | 0 | 0 | 65 | 38.28 | 38.28
2025-03-23 04:00:00 | 37.8 | 0 | 0 | 0 | 65 | 37.8 | 37.8
2025-03-23 05:00:00 | 39.24 | 0 | 0 | 0 | 65 | 39.24 | 39.24
2025-03-23 06:00:00 | 37.92 | 4.0989 | 0 | 0 | 65 | 33.8211 | 33.8211
2025-03-23 07:00:00 | 41.28 | 11.6252 | 0 | 0 | 65 | 29.6548 | 29.6548
2025-03-23 08:00:00 | 41.88 | 18.3731 | 0 | 0 | 65 | 23.5069 | 23.5069
2025-03-23 09:00:00 | 38.28 | 23.8827 | 0 | 0 | 65 | 14.3973 | 14.3973
2025-03-23 10:00:00 | 38.4 | 27.7786 | 0 | 0 | 65 | 10.6214 | 10.6214
2025-03-23 11:00:00 | 38.04 | 29.7952 | 0 | 0 | 65 | 8.2448 | 8.2448
2025-03-23 12:00:00 | 38.88 | 29.7952 | 0 | 0 | 65 | 9.0848 | 9.0848
2025-03-23 13:00:00 | 42.36 | 27.7786 | 0 | 0 | 65 | 14.5814 | 14.5814
2025-03-23 14:00:00 | 48.84 | 23.8827 | 0 | 0 | 65 | 24.9573 | 24.9573
2025-03-23 15:00:00 | 49.56 | 18.3731 | 0 | 0 | 65 | 31.1869 | 31.1869
2025-03-23 16:00:00 | 47.04 | 11.6252 | 0 | 0 | 65 | 35.4148 | 35.4148
2025-03-23 17:00:00 | 43.92 | 4.0989 | 0 | 0 | 65 | 39.8211 | 39.8211
2025-03-23 18:00:00 | 45.96 | 0 | 0 | 0 | 65 | 45.96 | 45.96
2025-03-23 19:00:00 | 48.24 | 0 | 0 | 0 | 65 | 48.24 | 48.24
2025-03-23 20:00:00 | 46.44 | 0 | 0 | 0 | 65 | 46.44 | 46.44
2025-03-23 21:00:00 | 42.36 | 0 | 0 | 0 | 65 | 42.36 | 42.36
2025-03-23 22:00:00 | 41.88 | 0 | 75 | 0 | 131 | 116.88 | 41.88
2025-03-23 23:00:00 | 41.4 | 0 | 5.6993 | 0 | 136.0154 | 47.0993 | 41.4
2025-03-24 00:00:00 | 34.08 | 0 | 0 | 0 | 136.0154 | 34.08 | 34.08
2025-03-24 01:00:00 | 23.64 | 0 | 0 | 0 | 136.0154 | 23.64 | 23.64
2025-03-24 02:00:00 | 22.08 | 0 | 0 | 0 | 136.0154 | 22.08 | 22.08
2025-03-24 03:00:00 | 22.56 | 0 | 0 | 0 | 136.0154 | 22.56 | 22.56
2025-03-24 04:00:00 | 22.32 | 0 | 75 | 0 | 202.0154 | 97.32 | 22.32
2025-03-24 05:00:00 | 22.68 | 0 | 75 | 0 | 268.0154 | 97.68 | 22.68
2025-03-24 06:00:00 | 21.96 | 4.3017 | 75 | 0 | 334.0154 | 92.6583 | 17.6583
2025-03-24 07:00:00 | 23.28 | 11.8274 | 0 | 11.4526 | 322.5628 | 3.5527e-14 | 11.4526
2025-03-24 08:00:00 | 24.36 | 18.5747 | 0 | 5.7853 | 316.7775 | 8.8818e-16 | 5.7853
2025-03-24 09:00:00 | 26.4 | 24.0839 | 0 | 2.3161 | 314.4614 | 3.1086e-15 | 2.3161
2025-03-24 10:00:00 | 39 | 27.9795 | 0 | 11.0205 | 303.4409 | -1.0658e-14 | 11.0205
2025-03-24 11:00:00 | 38.4 | 29.996 | 0 | 8.404 | 295.0369 | 3.5527e-15 | 8.404
2025-03-24 12:00:00 | 38.04 | 29.996 | 0 | 8.044 | 286.9929 | 3.5527e-15 | 8.044
2025-03-24 13:00:00 | 39.84 | 27.9795 | 0 | 11.8605 | 275.1324 | -7.1054e-15 | 11.8605
2025-03-24 14:00:00 | 42.96 | 24.0839 | 0 | 18.8761 | 256.2563 | -3.5527e-15 | 18.8761
2025-03-24 15:00:00 | 54.96 | 18.5747 | 0 | 36.3853 | 219.871 | -7.1054e-15 | 36.3853
2025-03-24 16:00:00 | 61.2 | 11.8274 | 0 | 49.3726 | 170.4983 | 3.5527e-14 | 49.3726
2025-03-24 17:00:00 | 57 | 4.3017 | 0 | 52.6983 | 117.8 | -4.2633e-14 | 52.6983
2025-03-24 18:00:00 | 52.8 | 0 | 0 | 52.8 | 65 | 0 | 52.8
2025-03-24 19:00:00 | 50.64 | 0 | 75 | 0 | 131 | 125.64 | 50.64
2025-03-24 20:00:00 | 48.36 | 0 | 21.6044 | 0 | 150.0118 | 69.9644 | 48.36
2025-03-24 21:00:00 | 48 | 0 | 0 | 0 | 150.0118 | 48 | 48
2025-03-24 22:00:00 | 42.84 | 0 | 0 | 0 | 150.0118 | 42.84 | 42.84
2025-03-24 23:00:00 | 41.04 | 0 | 0 | 0 | 150.0118 | 41.04 | 41.04
2025-03-25 00:00:00 | 41.04 | 0 | 0 | 0 | 150.0118 | 41.04 | 41.04
2025-03-25 01:00:00 | 38.88 | 0 | 0 | 0 | 150.0118 | 38.88 | 38.88
2025-03-25 02:00:00 | 38.4 | 0 | 0 | 0 | 150.0118 | 38.4 | 38.4
2025-03-25 03:00:00 | 38.76 | 0 | 75 | 0 | 216.0118 | 113.76 | 38.76
2025-03-25 04:00:00 | 38.76 | 0 | 75 | 0 | 282.0118 | 113.76 | 38.76
2025-03-25 05:00:00 | 31.92 | 0 | 75 | 0 | 348.0118 | 106.92 | 31.92
2025-03-25 06:00:00 | 22.56 | 4.504 | 75 | 0 | 414.0118 | 93.056 | 18.056
2025-03-25 07:00:00 | 29.4 | 12.0288 | 0 | 17.3712 | 396.6406 | -4.2633e-14 | 17.3712
2025-03-25 08:00:00 | 42.84 | 18.7753 | 0 | 24.0647 | 372.576 | 1.7764e-14 | 24.0647
2025-03-25 09:00:00 | 47.16 | 24.2838 | 0 | 22.8762 | 349.6998 | -7.1054e-15 | 22.8762
2025-03-25 10:00:00 | 46.8 | 28.1789 | 0 | 18.6211 | 331.0787 | 4.6185e-14 | 18.6211
2025-03-25 11:00:00 | 50.76 | 30.1952 | 0 | 20.5648 | 310.5139 | 1.4211e-14 | 20.5648
2025-03-25 12:00:00 | 53.28 | 30.1952 | 0 | 23.0848 | 287.4291 | 1.7764e-14 | 23.0848
2025-03-25 13:00:00 | 53.28 | 28.1789 | 0 | 25.1011 | 262.328 | 4.9738e-14 | 25.1011
2025-03-25 14:00:00 | 54.12 | 24.2838 | 0 | 29.8362 | 232.4919 | -7.1054e-15 | 29.8362
2025-03-25 15:00:00 | 52.8 | 18.7753 | 0 | 34.0247 | 198.4672 | 1.4211e-14 | 34.0247
2025-03-25 16:00:00 | 52.32 | 12.0288 | 0 | 40.2912 | 158.176 | -4.2633e-14 | 40.2912
2025-03-25 17:00:00 | 50.4 | 4.504 | 0 | 45.896 | 112.28 | 1.4211e-14 | 45.896
2025-03-25 18:00:00 | 47.28 | 0 | 0 | 47.28 | 65 | 0 | 47.28
2025-03-25 19:00:00 | 52.92 | 0 | 75 | 0 | 131 | 127.92 | 52.92
2025-03-25 20:00:00 | 54.6 | 0 | 0 | 0 | 131 | 54.6 | 54.6
2025-03-25 21:00:00 | 47.64 | 0 | 0 | 0 | 131 | 47.64 | 47.64
2025-03-25 22:00:00 | 43.08 | 0 | 0 | 0 | 131 | 43.08 | 43.08
2025-03-25 23:00:00 | 41.4 | 0 | 0 | 0 | 131 | 41.4 | 41.4
2025-03-26 00:00:00 | 41.16 | 0 | 0 | 0 | 131 | 41.16 | 41.16
2025-03-26 01:00:00 | 38.04 | 0 | 0 | 0 | 131 | 38.04 | 38.04
2025-03-26 02:00:00 | 38.88 | 0 | 0 | 0 | 131 | 38.88 | 38.88
2025-03-26 03:00:00 | 37.92 | 0 | 75 | 0 | 197 | 112.92 | 37.92
2025-03-26 04:00:00 | 38.16 | 0 | 75 | 0 | 263 | 113.16 | 38.16
2025-03-26 05:00:00 | 38.76 | 0 | 75 | 0 | 329 | 113.76 | 38.76
2025-03-26 06:00:00 | 38.04 | 4.706 | 75 | 0 | 395 | 108.334 | 33.334
2025-03-26 07:00:00 | 38.52 | 12.2295 | 0 | 26.2905 | 368.7095 | 1.0658e-14 | 26.2905
2025-03-26 08:00:00 | 39.36 | 18.9748 | 0 | 20.3852 | 348.3243 | -3.908e-14 | 20.3852
2025-03-26 09:00:00 | 41.76 | 24.4824 | 0 | 17.2776 | 331.0466 | -1.4211e-14 | 17.2776
2025-03-26 10:00:00 | 40.68 | 28.3768 | 0 | 12.3032 | 318.7434 | 4.6185e-14 | 12.3032
2025-03-26 11:00:00 | 41.88 | 30.3927 | 0 | 11.4873 | 307.2562 | 1.2434e-14 | 11.4873
2025-03-26 12:00:00 | 45.84 | 30.3927 | 0 | 15.4473 | 291.8089 | 1.2434e-14 | 15.4473
2025-03-26 13:00:00 | 48.12 | 28.3768 | 0 | 19.7432 | 272.0657 | 4.6185e-14 | 19.7432
2025-03-26 14:00:00 | 51.6 | 24.4824 | 0 | 27.1176 | 244.948 | -1.0658e-14 | 27.1176
2025-03-26 15:00:00 | 51.84 | 18.9748 | 0 | 32.8652 | 212.0828 | -3.5527e-14 | 32.8652
2025-03-26 16:00:00 | 51.36 | 12.2295 | 0 | 39.1305 | 172.9523 | 7.1054e-15 | 39.1305
2025-03-26 17:00:00 | 50.28 | 4.706 | 0 | 45.574 | 127.3783 | 2.8422e-14 | 45.574
2025-03-26 18:00:00 | 48.36 | 0 | 0 | 48.36 | 79.0183 | 0 | 48.36
2025-03-26 19:00:00 | 49.44 | 0 | 49.1494 | 0 | 122.2698 | 98.5894 | 49.44
2025-03-26 20:00:00 | 49.2 | 0 | 0 | 0 | 122.2698 | 49.2 | 49.2
2025-03-26 21:00:00 | 47.04 | 0 | 0 | 0 | 122.2698 | 47.04 | 47.04
2025-03-26 22:00:00 | 45.12 | 0 | 0 | 0 | 122.2698 | 45.12 | 45.12
2025-03-26 23:00:00 | 43.32 | 0 | 0 | 0 | 122.2698 | 43.32 | 43.32
2025-03-27 00:00:00 | 40.68 | 0 | 0 | 0 | 122.2698 | 40.68 | 40.68
2025-03-27 01:00:00 | 37.92 | 0 | 0 | 0 | 122.2698 | 37.92 | 37.92
2025-03-27 02:00:00 | 38.16 | 0 | 0 | 0 | 122.2698 | 38.16 | 38.16
2025-03-27 03:00:00 | 38.76 | 0 | 0 | 0 | 122.2698 | 38.76 | 38.76
2025-03-27 04:00:00 | 38.28 | 0 | 75 | 0 | 188.2698 | 113.28 | 38.28
2025-03-27 05:00:00 | 38.04 | 0 | 75 | 0 | 254.2698 | 113.04 | 38.04
2025-03-27 06:00:00 | 27.24 | 4.9075 | 75 | 0 | 320.2698 | 97.3325 | 22.3325
2025-03-27 07:00:00 | 22.2 | 12.4293 | 0 | 9.7707 | 310.4991 | 3.5527e-15 | 9.7707
2025-03-27 08:00:00 | 24.24 | 19.1731 | 0 | 5.0669 | 305.4322 | -3.5527e-15 | 5.0669
2025-03-27 09:00:00 | 22.56 | 24.6795 | 2.1195 | 0 | 307.2974 | -1.7764e-15 | -2.1195
2025-03-27 10:00:00 | 22.92 | 28.573 | 5.653 | 0 | 312.272 | 3.5527e-15 | -5.653
2025-03-27 11:00:00 | 29.16 | 30.5885 | 1.4285 | 0 | 313.5291 | -2.2204e-16 | -1.4285
2025-03-27 12:00:00 | 38.52 | 30.5885 | 0 | 7.9315 | 305.5976 | 2.6645e-15 | 7.9315
2025-03-27 13:00:00 | 48 | 28.573 | 0 | 19.427 | 286.1706 | 2.1316e-14 | 19.427
2025-03-27 14:00:00 | 60.36 | 24.6795 | 0 | 35.6805 | 250.4901 | 7.1054e-15 | 35.6805
2025-03-27 15:00:00 | 66.36 | 19.1731 | 0 | 47.1869 | 203.3032 | -2.1316e-14 | 47.1869
2025-03-27 16:00:00 | 62.28 | 12.4293 | 0 | 49.8507 | 153.4525 | 3.5527e-14 | 49.8507
2025-03-27 17:00:00 | 50.64 | 4.9075 | 0 | 45.7325 | 107.72 | -3.5527e-14 | 45.7325
2025-03-27 18:00:00 | 42.72 | 0 | 0 | 42.72 | 65 | 0 | 42.72
2025-03-27 19:00:00 | 40.92 | 0 | 73.5051 | 0 | 129.6845 | 114.4251 | 40.92
2025-03-27 20:00:00 | 41.88 | 0 | 0 | 0 | 129.6845 | 41.88 | 41.88
2025-03-27 21:00:00 | 39.96 | 0 | 0 | 0 | 129.6845 | 39.96 | 39.96
2025-03-27 22:00:00 | 38.16 | 0 | 0 | 0 | 129.6845 | 38.16 | 38.16
2025-03-27 23:00:00 | 38.28 | 0 | 0 | 0 | 129.6845 | 38.28 | 38.28
2025-03-28 00:00:00 | 29.52 | 0 | 0 | 0 | 129.6845 | 29.52 | 29.52
2025-03-28 01:00:00 | 22.32 | 0 | 0 | 0 | 129.6845 | 22.32 | 22.32
2025-03-28 02:00:00 | 21.84 | 0 | 0 | 0 | 129.6845 | 21.84 | 21.84
2025-03-28 03:00:00 | 22.68 | 0 | 75 | 0 | 195.6845 | 97.68 | 22.68
2025-03-28 04:00:00 | 22.08 | 0 | 75 | 0 | 261.6845 | 97.08 | 22.08
2025-03-28 05:00:00 | 21.96 | 0 | 75 | 0 | 327.6845 | 96.96 | 21.96
2025-03-28 06:00:00 | 22.8 | 5.1085 | 75 | 0 | 393.6845 | 92.6915 | 17.6915
2025-03-28 07:00:00 | 26.16 | 12.6282 | 0 | 13.5318 | 380.1527 | 4.7962e-14 | 13.5318
2025-03-28 08:00:00 | 38.88 | 19.3702 | 0 | 19.5098 | 360.6429 | 4.2633e-14 | 19.5098
2025-03-28 09:00:00 | 43.68 | 24.8751 | 0 | 18.8049 | 341.838 | -2.8422e-14 | 18.8049
2025-03-28 10:00:00 | 46.8 | 28.7676 | 0 | 18.0324 | 323.8056 | -3.5527e-14 | 18.0324
2025-03-28 11:00:00 | 46.2 | 30.7825 | 0 | 15.4175 | 308.388 | 1.7764e-15 | 15.4175
2025-03-28 12:00:00 | 52.08 | 30.7825 | 0 | 21.2975 | 287.0905 | -3.5527e-15 | 21.2975
2025-03-28 13:00:00 | 50.64 | 28.7676 | 0 | 21.8724 | 265.2181 | -3.1974e-14 | 21.8724
2025-03-28 14:00:00 | 59.4 | 24.8751 | 0 | 34.5249 | 230.6931 | -2.8422e-14 | 34.5249
2025-03-28 15:00:00 | 59.4 | 19.3702 | 0 | 40.0298 | 190.6634 | 4.2633e-14 | 40.0298
2025-03-28 16:00:00 | 52.08 | 12.6282 | 0 | 39.4518 | 151.2115 | 4.9738e-14 | 39.4518
2025-03-28 17:00:00 | 47.4 | 5.1085 | 0 | 42.2915 | 108.92 | -7.1054e-15 | 42.2915
2025-03-28 18:00:00 | 43.92 | 0 | 0 | 43.92 | 65 | 0 | 43.92
2025-03-28 19:00:00 | 42.96 | 0 | 0 | 0 | 65 | 42.96 | 42.96
2025-03-28 20:00:00 | 38.88 | 0 | 0 | 0 | 65 | 38.88 | 38.88
2025-03-28 21:00:00 | 38.76 | 0 | 0 | 0 | 65 | 38.76 | 38.76
2025-03-28 22:00:00 | 38.04 | 0 | 0 | 0 | 65 | 38.04 | 38.04
2025-03-28 23:00:00 | 38.28 | 0 | 0 | 0 | 65 | 38.28 | 38.28
2025-03-29 00:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-03-29 01:00:00 | 38.52 | 0 | 0 | 0 | 65 | 38.52 | 38.52
2025-03-29 02:00:00 | 38.64 | 0 | 0 | 0 | 65 | 38.64 | 38.64
2025-03-29 03:00:00 | 34.68 | 0 | 0 | 0 | 65 | 34.68 | 34.68
2025-03-29 04:00:00 | 21.84 | 0 | 0 | 0 | 65 | 21.84 | 21.84
2025-03-29 05:00:00 | 22.44 | 0 | 0 | 0 | 65 | 22.44 | 22.44
2025-03-29 06:00:00 | 21.72 | 5.3088 | 0 | 0 | 65 | 16.4112 | 16.4112
2025-03-29 07:00:00 | 36.84 | 12.8261 | 0 | 0 | 65 | 24.0139 | 24.0139
2025-03-29 08:00:00 | 37.08 | 19.566 | 0 | 0 | 65 | 17.514 | 17.514
2025-03-29 09:00:00 | 38.52 | 25.0691 | 0 | 0 | 65 | 13.4509 | 13.4509
2025-03-29 10:00:00 | 37.8 | 28.9603 | 0 | 0 | 65 | 8.8397 | 8.8397
2025-03-29 11:00:00 | 40.32 | 30.9746 | 0 | 0 | 65 | 9.3454 | 9.3454
2025-03-29 12:00:00 | 48.12 | 30.9746 | 0 | 0 | 65 | 17.1454 | 17.1454
2025-03-29 13:00:00 | 53.52 | 28.9603 | 0 | 0 | 65 | 24.5597 | 24.5597
2025-03-29 14:00:00 | 55.2 | 25.0691 | 0 | 0 | 65 | 30.1309 | 30.1309
2025-03-29 15:00:00 | 55.08 | 19.566 | 0 | 0 | 65 | 35.514 | 35.514
2025-03-29 16:00:00 | 54.24 | 12.8261 | 0 | 0 | 65 | 41.4139 | 41.4139
2025-03-29 17:00:00 | 53.64 | 5.3088 | 0 | 0 | 65 | 48.3312 | 48.3312
2025-03-29 18:00:00 | 51.24 | 0 | 0 | 0 | 65 | 51.24 | 51.24
2025-03-29 19:00:00 | 49.56 | 0 | 0 | 0 | 65 | 49.56 | 49.56
2025-03-29 20:00:00 | 45.96 | 0 | 0 | 0 | 65 | 45.96 | 45.96
2025-03-29 21:00:00 | 44.52 | 0 | 0 | 0 | 65 | 44.52 | 44.52
2025-03-29 22:00:00 | 43.56 | 0 | 0 | 0 | 65 | 43.56 | 43.56
2025-03-29 23:00:00 | 39 | 0 | 0 | 0 | 65 | 39 | 39
2025-03-30 00:00:00 | 38.04 | 0 | 0 | 0 | 65 | 38.04 | 38.04
2025-03-30 01:00:00 | 38.04 | 0 | 0 | 0 | 65 | 38.04 | 38.04
2025-03-30 02:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-03-30 03:00:00 | 39 | 0 | 0 | 0 | 65 | 39 | 39
2025-03-30 04:00:00 | 38.52 | 0 | 0 | 0 | 65 | 38.52 | 38.52
2025-03-30 05:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-03-30 06:00:00 | 38.04 | 5.5085 | 0 | 0 | 65 | 32.5315 | 32.5315
2025-03-30 07:00:00 | 41.16 | 13.023 | 0 | 0 | 65 | 28.137 | 28.137
2025-03-30 08:00:00 | 38.52 | 19.7604 | 0 | 0 | 65 | 18.7596 | 18.7596
2025-03-30 09:00:00 | 40.2 | 25.2615 | 0 | 0 | 65 | 14.9385 | 14.9385
2025-03-30 10:00:00 | 48.48 | 29.1513 | 0 | 0 | 65 | 19.3287 | 19.3287
2025-03-30 11:00:00 | 58.08 | 31.1648 | 0 | 0 | 65 | 26.9152 | 26.9152
2025-03-30 12:00:00 | 58.32 | 31.1648 | 0 | 0 | 65 | 27.1552 | 27.1552
2025-03-30 13:00:00 | 57.96 | 29.1513 | 75 | 0 | 131 | 103.8087 | 28.8087
2025-03-30 14:00:00 | 82.2 | 25.2615 | 65.9091 | 0 | 189 | 122.8476 | 56.9385
2025-03-30 15:00:00 | 91.2 | 19.7604 | 0 | 0 | 189 | 71.4396 | 71.4396
2025-03-30 16:00:00 | 93 | 13.023 | 0 | 0 | 189 | 79.977 | 79.977
2025-03-30 17:00:00 | 93.12 | 5.5085 | 0 | 0 | 189 | 87.6115 | 87.6115
2025-03-30 18:00:00 | 109.08 | 0 | 0 | 0 | 189 | 109.08 | 109.08
2025-03-30 19:00:00 | 97.92 | 0 | 0 | 0 | 189 | 97.92 | 97.92
2025-03-30 20:00:00 | 97.2 | 0 | 0 | 0 | 189 | 97.2 | 97.2
2025-03-30 21:00:00 | 91.56 | 0 | 0 | 0 | 189 | 91.56 | 91.56
2025-03-30 22:00:00 | 69.72 | 0 | 0 | 0 | 189 | 69.72 | 69.72
2025-03-30 23:00:00 | 66.6 | 0 | 0 | 0 | 189 | 66.6 | 66.6
2025-03-31 00:00:00 | 65.28 | 0 | 0 | 0 | 189 | 65.28 | 65.28
2025-03-31 01:00:00 | 63.72 | 0 | 75 | 0 | 255 | 138.72 | 63.72
2025-03-31 02:00:00 | 63.36 | 0 | 75 | 0 | 321 | 138.36 | 63.36
2025-03-31 03:00:00 | 64.44 | 0 | 75 | 0 | 387 | 139.44 | 64.44
2025-03-31 04:00:00 | 63.12 | 0 | 75 | 0 | 453 | 138.12 | 63.12
2025-03-31 05:00:00 | 62.76 | 0 | 75 | 0 | 519 | 137.76 | 62.76
2025-03-31 06:00:00 | 61.68 | 5.7074 | 75 | 0 | 585 | 130.9726 | 55.9726
2025-03-31 07:00:00 | 58.68 | 13.2188 | 0 | 45.4612 | 539.5388 | -2.8422e-14 | 45.4612
2025-03-31 08:00:00 | 57.84 | 19.9534 | 0 | 37.8866 | 501.6523 | -2.8422e-14 | 37.8866
2025-03-31 09:00:00 | 55.8 | 25.4522 | 0 | 30.3478 | 471.3044 | 3.5527e-14 | 30.3478
2025-03-31 10:00:00 | 70.2 | 29.3404 | 0 | 40.8596 | 430.4448 | -2.1316e-14 | 40.8596
2025-03-31 11:00:00 | 69.6 | 31.3531 | 0 | 38.2469 | 392.1979 | 7.1054e-15 | 38.2469
2025-03-31 12:00:00 | 75.36 | 31.3531 | 0 | 44.0069 | 348.191 | 1.4211e-14 | 44.0069
2025-03-31 13:00:00 | 83.52 | 29.3404 | 0 | 54.1796 | 294.0113 | -2.8422e-14 | 54.1796
2025-03-31 14:00:00 | 84.48 | 25.4522 | 0 | 59.0278 | 234.9835 | 3.5527e-14 | 59.0278
2025-03-31 15:00:00 | 93.72 | 19.9534 | 0 | 19.9835 | 215 | 53.7831 | 73.7666
2025-03-31 16:00:00 | 93.6 | 13.2188 | 0 | 0 | 215 | 80.3812 | 80.3812
2025-03-31 17:00:00 | 91.92 | 5.7074 | 0 | 75 | 140 | 11.2126 | 86.2126
2025-03-31 18:00:00 | 89.04 | 0 | 0 | 75 | 65 | 14.04 | 89.04
2025-03-31 19:00:00 | 92.88 | 0 | 70.8073 | 0 | 127.3104 | 163.6873 | 92.88
2025-03-31 20:00:00 | 89.04 | 0 | 74.6473 | 0 | 193 | 163.6873 | 89.04
2025-03-31 21:00:00 | 81.36 | 0 | 75 | 0 | 259 | 156.36 | 81.36
2025-03-31 22:00:00 | 66.6 | 0 | 75 | 0 | 325 | 141.6 | 66.6
2025-03-31 23:00:00 | 64.68 | 0 | 0 | 0 | 325 | 64.68 | 64.68
2025-04-01 00:00:00 | 61.2 | 0 | 0 | 0 | 325 | 61.2 | 61.2
2025-04-01 01:00:00 | 61.8 | 0 | 0 | 0 | 325 | 61.8 | 61.8
2025-04-01 02:00:00 | 59.64 | 0 | 0 | 0 | 325 | 59.64 | 59.64
2025-04-01 03:00:00 | 54 | 0 | 75 | 0 | 391 | 129 | 54
2025-04-01 04:00:00 | 50.52 | 0 | 21.8117 | 0 | 410.1943 | 72.3317 | 50.52
2025-04-01 05:00:00 | 49.2 | 0 | 0 | 0 | 410.1943 | 49.2 | 49.2
2025-04-01 06:00:00 | 49.68 | 7.0464 | 75 | 0 | 476.1943 | 117.6336 | 42.6336
2025-04-01 07:00:00 | 54.48 | 16.0047 | 0 | 38.4753 | 437.7191 | -4.2633e-14 | 38.4753
2025-04-01 08:00:00 | 61.68 | 24.0366 | 0 | 37.6434 | 400.0756 | 7.1054e-15 | 37.6434
2025-04-01 09:00:00 | 61.44 | 30.5945 | 0 | 30.8455 | 369.2302 | -4.6185e-14 | 30.8455
2025-04-01 10:00:00 | 59.64 | 35.2317 | 0 | 24.4083 | 344.8219 | -3.1974e-14 | 24.4083
2025-04-01 11:00:00 | 56.4 | 37.6321 | 0 | 18.7679 | 326.054 | -7.816e-14 | 18.7679
2025-04-01 12:00:00 | 50.52 | 37.6321 | 0 | 12.8879 | 313.1661 | 2.6645e-14 | 12.8879
2025-04-01 13:00:00 | 57.84 | 35.2317 | 0 | 22.6083 | 290.5578 | -3.1974e-14 | 22.6083
2025-04-01 14:00:00 | 59.88 | 30.5945 | 0 | 29.2855 | 261.2724 | -3.908e-14 | 29.2855
2025-04-01 15:00:00 | 62.52 | 24.0366 | 0 | 38.4834 | 222.7889 | 1.4211e-14 | 38.4834
2025-04-01 16:00:00 | 63 | 16.0047 | 0 | 46.9953 | 175.7936 | -3.5527e-14 | 46.9953
2025-04-01 17:00:00 | 61.2 | 7.0464 | 0 | 54.1536 | 121.64 | 6.3949e-14 | 54.1536
2025-04-01 18:00:00 | 56.64 | 0 | 0 | 56.64 | 65 | 0 | 56.64
2025-04-01 19:00:00 | 55.2 | 0 | 0 | 0 | 65 | 55.2 | 55.2
2025-04-01 20:00:00 | 56.16 | 0 | 0 | 0 | 65 | 56.16 | 56.16
2025-04-01 21:00:00 | 52.68 | 0 | 0 | 0 | 65 | 52.68 | 52.68
2025-04-01 22:00:00 | 46.68 | 0 | 0 | 0 | 65 | 46.68 | 46.68
2025-04-01 23:00:00 | 44.88 | 0 | 0 | 0 | 65 | 44.88 | 44.88
2025-04-02 00:00:00 | 41.88 | 0 | 0 | 0 | 65 | 41.88 | 41.88
2025-04-02 01:00:00 | 40.08 | 0 | 0 | 0 | 65 | 40.08 | 40.08
2025-04-02 02:00:00 | 39.12 | 0 | 0 | 0 | 65 | 39.12 | 39.12
2025-04-02 03:00:00 | 38.88 | 0 | 75 | 0 | 131 | 113.88 | 38.88
2025-04-02 04:00:00 | 38.28 | 0 | 75 | 0 | 197 | 113.28 | 38.28
2025-04-02 05:00:00 | 38.04 | 0 | 8.9956 | 0 | 204.9161 | 47.0356 | 38.04
2025-04-02 06:00:00 | 37.8 | 7.2817 | 75 | 0 | 270.9161 | 105.5183 | 30.5183
2025-04-02 07:00:00 | 40.44 | 16.2355 | 0 | 24.2045 | 246.7116 | -4.9738e-14 | 24.2045
2025-04-02 08:00:00 | 38.52 | 24.2632 | 0 | 14.2568 | 232.4548 | 3.908e-14 | 14.2568
2025-04-02 09:00:00 | 38.52 | 30.8179 | 0 | 7.7021 | 224.7527 | 1.7764e-15 | 7.7021
2025-04-02 10:00:00 | 40.32 | 35.4527 | 0 | 4.8673 | 219.8854 | 0 | 4.8673
2025-04-02 11:00:00 | 46.44 | 37.8518 | 0 | 8.5882 | 211.2972 | 1.0658e-14 | 8.5882
2025-04-02 12:00:00 | 41.4 | 37.8518 | 0 | 3.5482 | 207.749 | 1.7764e-15 | 3.5482
2025-04-02 13:00:00 | 40.68 | 35.4527 | 0 | 5.2273 | 202.5217 | -8.8818e-16 | 5.2273
2025-04-02 14:00:00 | 43.2 | 30.8179 | 0 | 12.3821 | 190.1396 | 1.0658e-14 | 12.3821
2025-04-02 15:00:00 | 43.32 | 24.2632 | 0 | 19.0568 | 171.0828 | 3.5527e-14 | 19.0568
2025-04-02 16:00:00 | 43.08 | 16.2355 | 0 | 26.8445 | 144.2383 | -4.6185e-14 | 26.8445
2025-04-02 17:00:00 | 43.8 | 7.2817 | 0 | 36.5183 | 107.72 | 4.2633e-14 | 36.5183
2025-04-02 18:00:00 | 42.72 | 0 | 0 | 42.72 | 65 | 0 | 42.72
2025-04-02 19:00:00 | 44.16 | 0 | 0 | 0 | 65 | 44.16 | 44.16
2025-04-02 20:00:00 | 42.48 | 0 | 0 | 0 | 65 | 42.48 | 42.48
2025-04-02 21:00:00 | 43.68 | 0 | 0 | 0 | 65 | 43.68 | 43.68
2025-04-02 22:00:00 | 44.16 | 0 | 0 | 0 | 65 | 44.16 | 44.16
2025-04-02 23:00:00 | 43.56 | 0 | 65.9091 | 0 | 123 | 109.4691 | 43.56
2025-04-03 00:00:00 | 45.12 | 0 | 75 | 0 | 189 | 120.12 | 45.12
2025-04-03 01:00:00 | 47.4 | 0 | 75 | 0 | 255 | 122.4 | 47.4
2025-04-03 02:00:00 | 50.4 | 0 | 75 | 0 | 321 | 125.4 | 50.4
2025-04-03 03:00:00 | 52.08 | 0 | 75 | 0 | 387 | 127.08 | 52.08
2025-04-03 04:00:00 | 54.72 | 0 | 75 | 0 | 453 | 129.72 | 54.72
2025-04-03 05:00:00 | 55.68 | 0 | 75 | 0 | 519 | 130.68 | 55.68
2025-04-03 06:00:00 | 56.4 | 7.5159 | 75 | 0 | 585 | 123.8841 | 48.8841
2025-04-03 07:00:00 | 58.92 | 16.4647 | 0 | 42.4553 | 542.5447 | -2.8422e-14 | 42.4553
2025-04-03 08:00:00 | 73.68 | 24.488 | 0 | 49.192 | 493.3527 | -1.4211e-14 | 49.192
2025-04-03 09:00:00 | 99.36 | 31.039 | 0 | 68.321 | 425.0317 | 4.2633e-14 | 68.321
2025-04-03 10:00:00 | 102.36 | 35.6712 | 0 | 66.6888 | 358.3429 | -1.4211e-14 | 66.6888
2025-04-03 11:00:00 | 107.04 | 38.069 | 0 | 68.971 | 289.3719 | -5.6843e-14 | 68.971
2025-04-03 12:00:00 | 98.16 | 38.069 | 0 | 60.091 | 229.2809 | -7.1054e-14 | 60.091
2025-04-03 13:00:00 | 91.92 | 35.6712 | 0 | 33.9169 | 195.3641 | 22.3319 | 56.2488
2025-04-03 14:00:00 | 88.44 | 31.039 | 0 | 0 | 195.3641 | 57.401 | 57.401
2025-04-03 15:00:00 | 82.68 | 24.488 | 0 | 0 | 195.3641 | 58.192 | 58.192
2025-04-03 16:00:00 | 81.72 | 16.4647 | 0 | 0 | 195.3641 | 65.2553 | 65.2553
2025-04-03 17:00:00 | 65.76 | 7.5159 | 0 | 58.2441 | 137.12 | -2.1316e-14 | 58.2441
2025-04-03 18:00:00 | 72.12 | 0 | 0 | 72.12 | 65 | 0 | 72.12
2025-04-03 19:00:00 | 61.56 | 0 | 0 | 0 | 65 | 61.56 | 61.56
2025-04-03 20:00:00 | 62.04 | 0 | 0 | 0 | 65 | 62.04 | 62.04
2025-04-03 21:00:00 | 67.56 | 0 | 0 | 0 | 65 | 67.56 | 67.56
2025-04-03 22:00:00 | 65.16 | 0 | 0 | 0 | 65 | 65.16 | 65.16
2025-04-03 23:00:00 | 61.68 | 0 | 0 | 0 | 65 | 61.68 | 61.68
2025-04-04 00:00:00 | 59.88 | 0 | 0 | 0 | 65 | 59.88 | 59.88
2025-04-04 01:00:00 | 58.2 | 0 | 0 | 0 | 65 | 58.2 | 58.2
2025-04-04 02:00:00 | 53.88 | 0 | 31.5311 | 0 | 92.7474 | 85.4111 | 53.88
2025-04-04 03:00:00 | 46.68 | 0 | 75 | 0 | 158.7474 | 121.68 | 46.68
2025-04-04 04:00:00 | 42.48 | 0 | 75 | 0 | 224.7474 | 117.48 | 42.48
2025-04-04 05:00:00 | 40.92 | 0 | 75 | 0 | 290.7474 | 115.92 | 40.92
2025-04-04 06:00:00 | 39.48 | 7.7489 | 75 | 0 | 356.7474 | 106.7311 | 31.7311
2025-04-04 07:00:00 | 40.08 | 16.6923 | 0 | 23.3877 | 333.3597 | 7.1054e-15 | 23.3877
2025-04-04 08:00:00 | 40.44 | 24.7108 | 0 | 15.7292 | 317.6305 | -2.4869e-14 | 15.7292
2025-04-04 09:00:00 | 40.44 | 31.2578 | 0 | 9.1822 | 308.4483 | 0 | 9.1822
2025-04-04 10:00:00 | 40.2 | 35.8873 | 0 | 4.3127 | 304.1356 | 4.4409e-15 | 4.3127
2025-04-04 11:00:00 | 41.16 | 38.2836 | 0 | 2.8764 | 301.2592 | 6.6613e-15 | 2.8764
2025-04-04 12:00:00 | 43.44 | 38.2836 | 0 | 5.1564 | 296.1029 | 7.9936e-15 | 5.1564
2025-04-04 13:00:00 | 48.36 | 35.8873 | 0 | 12.4727 | 283.6301 | 2.1316e-14 | 12.4727
2025-04-04 14:00:00 | 63.72 | 31.2578 | 0 | 32.4622 | 251.1679 | 7.1054e-15 | 32.4622
2025-04-04 15:00:00 | 64.2 | 24.7108 | 0 | 39.4892 | 211.6787 | -2.1316e-14 | 39.4892
2025-04-04 16:00:00 | 61.56 | 16.6923 | 0 | 44.8677 | 166.8111 | 1.4211e-14 | 44.8677
2025-04-04 17:00:00 | 57.24 | 7.7489 | 0 | 49.4911 | 117.32 | -2.8422e-14 | 49.4911
2025-04-04 18:00:00 | 52.32 | 0 | 0 | 52.32 | 65 | 0 | 52.32
2025-04-04 19:00:00 | 48.12 | 0 | 0 | 0 | 65 | 48.12 | 48.12
2025-04-04 20:00:00 | 48.6 | 0 | 0 | 0 | 65 | 48.6 | 48.6
2025-04-04 21:00:00 | 48.12 | 0 | 0 | 0 | 65 | 48.12 | 48.12
2025-04-04 22:00:00 | 48 | 0 | 0 | 0 | 65 | 48 | 48
2025-04-04 23:00:00 | 48.72 | 0 | 0 | 0 | 65 | 48.72 | 48.72
2025-04-05 00:00:00 | 50.16 | 0 | 0 | 0 | 65 | 50.16 | 50.16
2025-04-05 01:00:00 | 49.92 | 0 | 0 | 0 | 65 | 49.92 | 49.92
2025-04-05 02:00:00 | 49.32 | 0 | 0 | 0 | 65 | 49.32 | 49.32
2025-04-05 03:00:00 | 48 | 0 | 0 | 0 | 65 | 48 | 48
2025-04-05 04:00:00 | 47.4 | 0 | 0 | 0 | 65 | 47.4 | 47.4
2025-04-05 05:00:00 | 46.44 | 0 | 0 | 0 | 65 | 46.44 | 46.44
2025-04-05 06:00:00 | 44.64 | 7.9807 | 0 | 0 | 65 | 36.6593 | 36.6593
2025-04-05 07:00:00 | 46.08 | 16.9183 | 0 | 0 | 65 | 29.1617 | 29.1617
2025-04-05 08:00:00 | 60.6 | 24.9315 | 0 | 0 | 65 | 35.6685 | 35.6685
2025-04-05 09:00:00 | 69.96 | 31.4743 | 0 | 0 | 65 | 38.4857 | 38.4857
2025-04-05 10:00:00 | 63.24 | 36.1008 | 0 | 0 | 65 | 27.1392 | 27.1392
2025-04-05 11:00:00 | 58.08 | 38.4956 | 0 | 0 | 65 | 19.5844 | 19.5844
2025-04-05 12:00:00 | 54.96 | 38.4956 | 0 | 0 | 65 | 16.4644 | 16.4644
2025-04-05 13:00:00 | 54.48 | 36.1008 | 0 | 0 | 65 | 18.3792 | 18.3792
2025-04-05 14:00:00 | 52.2 | 31.4743 | 0 | 0 | 65 | 20.7257 | 20.7257
2025-04-05 15:00:00 | 48.72 | 24.9315 | 0 | 0 | 65 | 23.7885 | 23.7885
2025-04-05 16:00:00 | 48.72 | 16.9183 | 0 | 0 | 65 | 31.8017 | 31.8017
2025-04-05 17:00:00 | 46.56 | 7.9807 | 0 | 0 | 65 | 38.5793 | 38.5793
2025-04-05 18:00:00 | 45.84 | 0 | 0 | 0 | 65 | 45.84 | 45.84
2025-04-05 19:00:00 | 44.76 | 0 | 0 | 0 | 65 | 44.76 | 44.76
2025-04-05 20:00:00 | 44.04 | 0 | 0 | 0 | 65 | 44.04 | 44.04
2025-04-05 21:00:00 | 42.24 | 0 | 0 | 0 | 65 | 42.24 | 42.24
2025-04-05 22:00:00 | 40.68 | 0 | 0 | 0 | 65 | 40.68 | 40.68
2025-04-05 23:00:00 | 41.16 | 0 | 0 | 0 | 65 | 41.16 | 41.16
2025-04-06 00:00:00 | 41.16 | 0 | 0 | 0 | 65 | 41.16 | 41.16
2025-04-06 01:00:00 | 40.08 | 0 | 0 | 0 | 65 | 40.08 | 40.08
2025-04-06 02:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-04-06 03:00:00 | 39.36 | 0 | 0 | 0 | 65 | 39.36 | 39.36
2025-04-06 04:00:00 | 39.12 | 0 | 0 | 0 | 65 | 39.12 | 39.12
2025-04-06 05:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-04-06 06:00:00 | 38.4 | 8.2111 | 0 | 0 | 65 | 30.1889 | 30.1889
2025-04-06 07:00:00 | 39.24 | 17.1425 | 0 | 0 | 65 | 22.0975 | 22.0975
2025-04-06 08:00:00 | 40.2 | 25.1502 | 0 | 0 | 65 | 15.0498 | 15.0498
2025-04-06 09:00:00 | 38.28 | 31.6885 | 0 | 0 | 65 | 6.5915 | 6.5915
2025-04-06 10:00:00 | 39.96 | 36.3117 | 0 | 0 | 65 | 3.6483 | 3.6483
2025-04-06 11:00:00 | 44.28 | 38.7049 | 0 | 0 | 65 | 5.5751 | 5.5751
2025-04-06 12:00:00 | 49.08 | 38.7049 | 0 | 0 | 65 | 10.3751 | 10.3751
2025-04-06 13:00:00 | 52.68 | 36.3117 | 0 | 0 | 65 | 16.3683 | 16.3683
2025-04-06 14:00:00 | 51.84 | 31.6885 | 0 | 0 | 65 | 20.1515 | 20.1515
2025-04-06 15:00:00 | 50.04 | 25.1502 | 0 | 0 | 65 | 24.8898 | 24.8898
2025-04-06 16:00:00 | 51 | 17.1425 | 0 | 0 | 65 | 33.8575 | 33.8575
2025-04-06 17:00:00 | 61.44 | 8.2111 | 0 | 0 | 65 | 53.2289 | 53.2289
2025-04-06 18:00:00 | 66.24 | 0 | 0 | 0 | 65 | 66.24 | 66.24
2025-04-06 19:00:00 | 67.32 | 0 | 0 | 0 | 65 | 67.32 | 67.32
2025-04-06 20:00:00 | 62.52 | 0 | 0 | 0 | 65 | 62.52 | 62.52
2025-04-06 21:00:00 | 52.08 | 0 | 0 | 0 | 65 | 52.08 | 52.08
2025-04-06 22:00:00 | 45.84 | 0 | 0 | 0 | 65 | 45.84 | 45.84
2025-04-06 23:00:00 | 42.96 | 0 | 0 | 0 | 65 | 42.96 | 42.96
2025-04-07 00:00:00 | 41.76 | 0 | 0 | 0 | 65 | 41.76 | 41.76
2025-04-07 01:00:00 | 37.92 | 0 | 0 | 0 | 65 | 37.92 | 37.92
2025-04-07 02:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-04-07 03:00:00 | 38.04 | 0 | 75 | 0 | 131 | 113.04 | 38.04
2025-04-07 04:00:00 | 38.64 | 0 | 75 | 0 | 197 | 113.64 | 38.64
2025-04-07 05:00:00 | 38.52 | 0 | 0 | 0 | 197 | 38.52 | 38.52
2025-04-07 06:00:00 | 38.88 | 8.4401 | 71.3844 | 0 | 259.8183 | 101.8243 | 30.4399
2025-04-07 07:00:00 | 42 | 17.3649 | 0 | 24.6351 | 235.1832 | -7.1054e-15 | 24.6351
2025-04-07 08:00:00 | 40.68 | 25.3667 | 0 | 15.3133 | 219.8699 | 7.1054e-15 | 15.3133
2025-04-07 09:00:00 | 38.28 | 31.9001 | 0 | 6.3799 | 213.49 | -1.7764e-15 | 6.3799
2025-04-07 10:00:00 | 39.12 | 36.52 | 0 | 2.6 | 210.89 | -3.5527e-15 | 2.6
2025-04-07 11:00:00 | 39 | 38.9114 | 0 | 0.088609 | 210.8014 | -1.0897e-13 | 0.088609
2025-04-07 12:00:00 | 38.04 | 38.9114 | 0.87139 | 0 | 211.5682 | 3.3307e-16 | -0.87139
2025-04-07 13:00:00 | 38.52 | 36.52 | 0 | 2 | 209.5682 | 2.176e-14 | 2
2025-04-07 14:00:00 | 37.8 | 31.9001 | 0 | 5.8999 | 203.6683 | 4.4409e-15 | 5.8999
2025-04-07 15:00:00 | 39.6 | 25.3667 | 0 | 14.2333 | 189.435 | 8.8818e-15 | 14.2333
2025-04-07 16:00:00 | 49.32 | 17.3649 | 0 | 31.9551 | 157.4799 | -7.1054e-15 | 31.9551
2025-04-07 17:00:00 | 51.72 | 8.4401 | 0 | 43.2799 | 114.2 | 1.4211e-14 | 43.2799
2025-04-07 18:00:00 | 49.2 | 0 | 0 | 49.2 | 65 | 9.9476e-14 | 49.2
2025-04-07 19:00:00 | 52.2 | 0 | 0 | 0 | 65 | 52.2 | 52.2
2025-04-07 20:00:00 | 50.4 | 0 | 0 | 0 | 65 | 50.4 | 50.4
2025-04-07 21:00:00 | 51.72 | 0 | 0 | 0 | 65 | 51.72 | 51.72
2025-04-07 22:00:00 | 44.16 | 0 | 0 | 0 | 65 | 44.16 | 44.16
2025-04-07 23:00:00 | 42.48 | 0 | 0 | 0 | 65 | 42.48 | 42.48
2025-04-08 00:00:00 | 42.12 | 0 | 0 | 0 | 65 | 42.12 | 42.12
2025-04-08 01:00:00 | 41.64 | 0 | 0 | 0 | 65 | 41.64 | 41.64
2025-04-08 02:00:00 | 39.24 | 0 | 70.6585 | 0 | 127.1795 | 109.8985 | 39.24
2025-04-08 03:00:00 | 26.88 | 0 | 75 | 0 | 193.1795 | 101.88 | 26.88
2025-04-08 04:00:00 | 22.92 | 0 | 75 | 0 | 259.1795 | 97.92 | 22.92
2025-04-08 05:00:00 | 23.52 | 0 | 75 | 0 | 325.1795 | 98.52 | 23.52
2025-04-08 06:00:00 | 23.04 | 8.6675 | 75 | 0 | 391.1795 | 89.3725 | 14.3725
2025-04-08 07:00:00 | 27.72 | 17.5854 | 0 | 10.1346 | 381.0449 | 4.0856e-14 | 10.1346
2025-04-08 08:00:00 | 40.8 | 25.581 | 0 | 15.219 | 365.8259 | 3.5527e-14 | 15.219
2025-04-08 09:00:00 | 49.8 | 32.1093 | 0 | 17.6907 | 348.1353 | 0 | 17.6907
2025-04-08 10:00:00 | 51.24 | 36.7256 | 0 | 14.5144 | 333.6209 | 2.4869e-14 | 14.5144
2025-04-08 11:00:00 | 51.36 | 39.1151 | 0 | 12.2449 | 321.376 | -6.7502e-14 | 12.2449
2025-04-08 12:00:00 | 53.4 | 39.1151 | 0 | 14.2849 | 307.0911 | 3.1974e-14 | 14.2849
2025-04-08 13:00:00 | 53.04 | 36.7256 | 0 | 16.3144 | 290.7767 | 2.1316e-14 | 16.3144
2025-04-08 14:00:00 | 55.56 | 32.1093 | 0 | 23.4507 | 267.3261 | 3.5527e-15 | 23.4507
2025-04-08 15:00:00 | 61.08 | 25.581 | 0 | 35.499 | 231.8271 | 3.5527e-14 | 35.499
2025-04-08 16:00:00 | 65.28 | 17.5854 | 0 | 47.6946 | 184.1325 | 4.2633e-14 | 47.6946
2025-04-08 17:00:00 | 64.68 | 8.6675 | 0 | 56.0125 | 128.12 | -7.1054e-15 | 56.0125
2025-04-08 18:00:00 | 63.12 | 0 | 0 | 63.12 | 65 | 0 | 63.12
2025-04-08 19:00:00 | 69.48 | 0 | 0 | 0 | 65 | 69.48 | 69.48
2025-04-08 20:00:00 | 66 | 0 | 0 | 0 | 65 | 66 | 66
2025-04-08 21:00:00 | 60.72 | 0 | 0 | 0 | 65 | 60.72 | 60.72
2025-04-08 22:00:00 | 48.84 | 0 | 0 | 0 | 65 | 48.84 | 48.84
2025-04-08 23:00:00 | 44.04 | 0 | 0 | 0 | 65 | 44.04 | 44.04
2025-04-09 00:00:00 | 38.64 | 0 | 38.5813 | 0 | 98.9515 | 77.2213 | 38.64
2025-04-09 01:00:00 | 39.12 | 0 | 75 | 0 | 164.9515 | 114.12 | 39.12
2025-04-09 02:00:00 | 39.36 | 0 | 75 | 0 | 230.9515 | 114.36 | 39.36
2025-04-09 03:00:00 | 40.8 | 0 | 75 | 0 | 296.9515 | 115.8 | 40.8
2025-04-09 04:00:00 | 42.12 | 0 | 75 | 0 | 362.9515 | 117.12 | 42.12
2025-04-09 05:00:00 | 40.56 | 0 | 75 | 0 | 428.9515 | 115.56 | 40.56
2025-04-09 06:00:00 | 45.72 | 8.8934 | 75 | 0 | 494.9515 | 111.8266 | 36.8266
2025-04-09 07:00:00 | 46.56 | 17.804 | 0 | 28.756 | 466.1955 | -3.908e-14 | 28.756
2025-04-09 08:00:00 | 48.36 | 25.793 | 0 | 22.567 | 443.6285 | 3.908e-14 | 22.567
2025-04-09 09:00:00 | 54.96 | 32.316 | 0 | 22.644 | 420.9845 | -4.2633e-14 | 22.644
2025-04-09 10:00:00 | 56.16 | 36.9285 | 0 | 19.2315 | 401.753 | 1.0658e-14 | 19.2315
2025-04-09 11:00:00 | 55.56 | 39.316 | 0 | 16.244 | 385.509 | 0 | 16.244
2025-04-09 12:00:00 | 55.56 | 39.316 | 0 | 16.244 | 369.2651 | 0 | 16.244
2025-04-09 13:00:00 | 54.96 | 36.9285 | 0 | 18.0315 | 351.2335 | 1.7764e-14 | 18.0315
2025-04-09 14:00:00 | 58.2 | 32.316 | 0 | 25.884 | 325.3496 | -4.2633e-14 | 25.884
2025-04-09 15:00:00 | 82.08 | 25.793 | 0 | 56.287 | 269.0626 | 3.5527e-14 | 56.287
2025-04-09 16:00:00 | 82.44 | 17.804 | 0 | 64.636 | 204.4266 | -4.2633e-14 | 64.636
2025-04-09 17:00:00 | 76.92 | 8.8934 | 0 | 68.0266 | 136.4 | -2.8422e-14 | 68.0266
2025-04-09 18:00:00 | 71.4 | 0 | 0 | 71.4 | 65 | 9.9476e-14 | 71.4
2025-04-09 19:00:00 | 65.52 | 0 | 0 | 0 | 65 | 65.52 | 65.52
2025-04-09 20:00:00 | 61.08 | 0 | 0 | 0 | 65 | 61.08 | 61.08
2025-04-09 21:00:00 | 63.48 | 0 | 0 | 0 | 65 | 63.48 | 63.48
2025-04-09 22:00:00 | 58.8 | 0 | 0 | 0 | 65 | 58.8 | 58.8
2025-04-09 23:00:00 | 54.36 | 0 | 0 | 0 | 65 | 54.36 | 54.36
2025-04-10 00:00:00 | 49.2 | 0 | 0 | 0 | 65 | 49.2 | 49.2
2025-04-10 01:00:00 | 46.68 | 0 | 2.0344 | 0 | 66.7903 | 48.7144 | 46.68
2025-04-10 02:00:00 | 45.6 | 0 | 75 | 0 | 132.7903 | 120.6 | 45.6
2025-04-10 03:00:00 | 45 | 0 | 75 | 0 | 198.7903 | 120 | 45
2025-04-10 04:00:00 | 45.24 | 0 | 75 | 0 | 264.7903 | 120.24 | 45.24
2025-04-10 05:00:00 | 44.28 | 0 | 75 | 0 | 330.7903 | 119.28 | 44.28
2025-04-10 06:00:00 | 44.28 | 9.1177 | 75 | 0 | 396.7903 | 110.1623 | 35.1623
2025-04-10 07:00:00 | 44.64 | 18.0206 | 0 | 26.6194 | 370.1708 | 1.7764e-14 | 26.6194
2025-04-10 08:00:00 | 45.6 | 26.0027 | 0 | 19.5973 | 350.5736 | -1.0658e-14 | 19.5973
2025-04-10 09:00:00 | 44.04 | 32.5201 | 0 | 11.5199 | 339.0536 | -3.0198e-14 | 11.5199
2025-04-10 10:00:00 | 45 | 37.1286 | 0 | 7.8714 | 331.1822 | 9.77e-15 | 7.8714
2025-04-10 11:00:00 | 46.08 | 39.5141 | 0 | 6.5659 | 324.6163 | -4.4409e-15 | 6.5659
2025-04-10 12:00:00 | 44.52 | 39.5141 | 0 | 5.0059 | 319.6104 | 0 | 5.0059
2025-04-10 13:00:00 | 50.88 | 37.1286 | 0 | 13.7514 | 305.8589 | -1.7764e-14 | 13.7514
2025-04-10 14:00:00 | 61.44 | 32.5201 | 0 | 28.9199 | 276.939 | -3.1974e-14 | 28.9199
2025-04-10 15:00:00 | 69.6 | 26.0027 | 0 | 43.5973 | 233.3417 | -1.4211e-14 | 43.5973
2025-04-10 16:00:00 | 70.8 | 18.0206 | 0 | 52.7794 | 180.5623 | 1.4211e-14 | 52.7794
2025-04-10 17:00:00 | 63.84 | 9.1177 | 0 | 54.7223 | 125.84 | 0 | 54.7223
2025-04-10 18:00:00 | 60.84 | 0 | 0 | 60.84 | 65 | 0 | 60.84
2025-04-10 19:00:00 | 58.08 | 0 | 0 | 0 | 65 | 58.08 | 58.08
2025-04-10 20:00:00 | 58.92 | 0 | 0 | 0 | 65 | 58.92 | 58.92
2025-04-10 21:00:00 | 57.6 | 0 | 0 | 0 | 65 | 57.6 | 57.6
2025-04-10 22:00:00 | 50.28 | 0 | 0 | 0 | 65 | 50.28 | 50.28
2025-04-10 23:00:00 | 47.16 | 0 | 0 | 0 | 65 | 47.16 | 47.16
2025-04-11 00:00:00 | 45 | 0 | 6.5508 | 0 | 70.7647 | 51.5508 | 45
2025-04-11 01:00:00 | 43.32 | 0 | 75 | 0 | 136.7647 | 118.32 | 43.32
2025-04-11 02:00:00 | 42.36 | 0 | 75 | 0 | 202.7647 | 117.36 | 42.36
2025-04-11 03:00:00 | 39.36 | 0 | 75 | 0 | 268.7647 | 114.36 | 39.36
2025-04-11 04:00:00 | 37.8 | 0 | 75 | 0 | 334.7647 | 112.8 | 37.8
2025-04-11 05:00:00 | 38.04 | 0.13159 | 75 | 0 | 400.7647 | 112.9084 | 37.9084
2025-04-11 06:00:00 | 37.92 | 9.3402 | 75 | 0 | 466.7647 | 103.5798 | 28.5798
2025-04-11 07:00:00 | 37.32 | 18.2351 | 0 | 19.0849 | 447.6798 | -3.908e-14 | 19.0849
2025-04-11 08:00:00 | 38.52 | 26.21 | 0 | 12.31 | 435.3698 | -3.908e-14 | 12.31
2025-04-11 09:00:00 | 42.12 | 32.7215 | 0 | 9.3985 | 425.9714 | 1.7764e-15 | 9.3985
2025-04-11 10:00:00 | 47.4 | 37.3259 | 0 | 10.0741 | 415.8972 | 2.6645e-14 | 10.0741
2025-04-11 11:00:00 | 52.8 | 39.7092 | 0 | 13.0908 | 402.8064 | -1.0658e-14 | 13.0908
2025-04-11 12:00:00 | 57.6 | 39.7092 | 0 | 17.8908 | 384.9157 | -7.1054e-15 | 17.8908
2025-04-11 13:00:00 | 66.36 | 37.3259 | 0 | 29.0341 | 355.8815 | 2.8422e-14 | 29.0341
2025-04-11 14:00:00 | 80.04 | 32.7215 | 0 | 47.3185 | 308.563 | -4.2633e-14 | 47.3185
2025-04-11 15:00:00 | 84.84 | 26.21 | 0 | 58.63 | 249.9331 | -3.5527e-14 | 58.63
2025-04-11 16:00:00 | 74.4 | 18.2351 | 0 | 56.1649 | 193.7682 | -3.5527e-14 | 56.1649
2025-04-11 17:00:00 | 69.24 | 9.3402 | 0 | 59.8998 | 133.8684 | -7.1054e-15 | 59.8998
2025-04-11 18:00:00 | 69 | 0.13159 | 0 | 68.8684 | 65 | -4.2633e-14 | 68.8684
2025-04-11 19:00:00 | 66.6 | 0 | 0 | 0 | 65 | 66.6 | 66.6
2025-04-11 20:00:00 | 56.76 | 0 | 0 | 0 | 65 | 56.76 | 56.76
2025-04-11 21:00:00 | 50.64 | 0 | 0 | 0 | 65 | 50.64 | 50.64
2025-04-11 22:00:00 | 46.2 | 0 | 0 | 0 | 65 | 46.2 | 46.2
2025-04-11 23:00:00 | 43.8 | 0 | 0 | 0 | 65 | 43.8 | 43.8
2025-04-12 00:00:00 | 41.28 | 0 | 0 | 0 | 65 | 41.28 | 41.28
2025-04-12 01:00:00 | 40.56 | 0 | 0 | 0 | 65 | 40.56 | 40.56
2025-04-12 02:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-04-12 03:00:00 | 42.24 | 0 | 0 | 0 | 65 | 42.24 | 42.24
2025-04-12 04:00:00 | 40.92 | 0 | 0 | 0 | 65 | 40.92 | 40.92
2025-04-12 05:00:00 | 41.64 | 0.36103 | 0 | 0 | 65 | 41.279 | 41.279
2025-04-12 06:00:00 | 40.44 | 9.561 | 0 | 0 | 65 | 30.879 | 30.879
2025-04-12 07:00:00 | 48.24 | 18.4475 | 0 | 0 | 65 | 29.7925 | 29.7925
2025-04-12 08:00:00 | 58.56 | 26.4149 | 0 | 0 | 65 | 32.1451 | 32.1451
2025-04-12 09:00:00 | 66.96 | 32.9203 | 0 | 0 | 65 | 34.0397 | 34.0397
2025-04-12 10:00:00 | 66.24 | 37.5203 | 0 | 0 | 65 | 28.7197 | 28.7197
2025-04-12 11:00:00 | 65.16 | 39.9014 | 0 | 0 | 65 | 25.2586 | 25.2586
2025-04-12 12:00:00 | 65.28 | 39.9014 | 0 | 0 | 65 | 25.3786 | 25.3786
2025-04-12 13:00:00 | 64.08 | 37.5203 | 0 | 0 | 65 | 26.5597 | 26.5597
2025-04-12 14:00:00 | 61.08 | 32.9203 | 0 | 0 | 65 | 28.1597 | 28.1597
2025-04-12 15:00:00 | 56.64 | 26.4149 | 0 | 0 | 65 | 30.2251 | 30.2251
2025-04-12 16:00:00 | 54.96 | 18.4475 | 0 | 0 | 65 | 36.5125 | 36.5125
2025-04-12 17:00:00 | 55.68 | 9.561 | 0 | 0 | 65 | 46.119 | 46.119
2025-04-12 18:00:00 | 54.84 | 0.36103 | 0 | 0 | 65 | 54.479 | 54.479
2025-04-12 19:00:00 | 53.16 | 0 | 0 | 0 | 65 | 53.16 | 53.16
2025-04-12 20:00:00 | 51.12 | 0 | 0 | 0 | 65 | 51.12 | 51.12
2025-04-12 21:00:00 | 52.92 | 0 | 0 | 0 | 65 | 52.92 | 52.92
2025-04-12 22:00:00 | 52.32 | 0 | 0 | 0 | 65 | 52.32 | 52.32
2025-04-12 23:00:00 | 24.96 | 0 | 0 | 0 | 65 | 24.96 | 24.96
2025-04-13 00:00:00 | 7.8 | 0 | 0 | 0 | 65 | 7.8 | 7.8
2025-04-13 01:00:00 | 7.68 | 0 | 0 | 0 | 65 | 7.68 | 7.68
2025-04-13 02:00:00 | 8.04 | 0 | 0 | 0 | 65 | 8.04 | 8.04
2025-04-13 03:00:00 | 6.72 | 0 | 0 | 0 | 65 | 6.72 | 6.72
2025-04-13 04:00:00 | 7.56 | 0 | 0 | 0 | 65 | 7.56 | 7.56
2025-04-13 05:00:00 | 7.2 | 0.58896 | 0 | 0 | 65 | 6.611 | 6.611
2025-04-13 06:00:00 | 8.16 | 9.7799 | 0 | 0 | 65 | -1.6199 | -1.6199
2025-04-13 07:00:00 | 6.24 | 18.6577 | 0 | 0 | 65 | -12.4177 | -12.4177
2025-04-13 08:00:00 | 5.64 | 26.6174 | 0 | 0 | 65 | -20.9774 | -20.9774
2025-04-13 09:00:00 | 6.12 | 33.1164 | 0 | 0 | 65 | -26.9964 | -26.9964
2025-04-13 10:00:00 | 5.04 | 37.7118 | 0 | 0 | 65 | -32.6718 | -32.6718
2025-04-13 11:00:00 | 6.6 | 40.0906 | 0 | 0 | 65 | -33.4906 | -33.4906
2025-04-13 12:00:00 | 5.64 | 40.0906 | 0 | 0 | 65 | -34.4506 | -34.4506
2025-04-13 13:00:00 | 5.52 | 37.7118 | 0 | 0 | 65 | -32.1918 | -32.1918
2025-04-13 14:00:00 | 6.84 | 33.1164 | 0 | 0 | 65 | -26.2764 | -26.2764
2025-04-13 15:00:00 | 5.64 | 26.6174 | 0 | 0 | 65 | -20.9774 | -20.9774
2025-04-13 16:00:00 | 15.12 | 18.6577 | 0 | 0 | 65 | -3.5377 | -3.5377
2025-04-13 17:00:00 | 17.52 | 9.7799 | 0 | 0 | 65 | 7.7401 | 7.7401
2025-04-13 18:00:00 | 18.84 | 0.58896 | 0 | 0 | 65 | 18.251 | 18.251
2025-04-13 19:00:00 | 22.2 | 0 | 0 | 0 | 65 | 22.2 | 22.2
2025-04-13 20:00:00 | 14.52 | 0 | 0 | 0 | 65 | 14.52 | 14.52
2025-04-13 21:00:00 | 5.64 | 0 | 0 | 0 | 65 | 5.64 | 5.64
2025-04-13 22:00:00 | 5.4 | 0 | 0 | 0 | 65 | 5.4 | 5.4
2025-04-13 23:00:00 | 6.72 | 0 | 0 | 0 | 65 | 6.72 | 6.72
2025-04-14 00:00:00 | 5.04 | 0 | 0 | 0 | 65 | 5.04 | 5.04
2025-04-14 01:00:00 | 5.76 | 0 | 0 | 0 | 65 | 5.76 | 5.76
2025-04-14 02:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-14 03:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-14 04:00:00 | 5.64 | 0 | 0 | 0 | 65 | 5.64 | 5.64
2025-04-14 05:00:00 | 6.12 | 0.81531 | 0 | 0 | 65 | 5.3047 | 5.3047
2025-04-14 06:00:00 | 5.76 | 9.9969 | 0 | 0 | 65 | -4.2369 | -4.2369
2025-04-14 07:00:00 | 4.92 | 18.8657 | 0 | 0 | 65 | -13.9457 | -13.9457
2025-04-14 08:00:00 | 5.4 | 26.8173 | 0 | 0 | 65 | -21.4173 | -21.4173
2025-04-14 09:00:00 | 5.28 | 33.3097 | 0 | 0 | 65 | -28.0297 | -28.0297
2025-04-14 10:00:00 | 5.64 | 37.9005 | 0 | 0 | 65 | -32.2605 | -32.2605
2025-04-14 11:00:00 | 4.92 | 40.2769 | 0 | 0 | 65 | -35.3569 | -35.3569
2025-04-14 12:00:00 | 2.04 | 40.2769 | 0 | 0 | 65 | -38.2369 | -38.2369
2025-04-14 13:00:00 | 6.12 | 37.9005 | 0 | 0 | 65 | -31.7805 | -31.7805
2025-04-14 14:00:00 | 5.04 | 33.3097 | 0 | 0 | 65 | -28.2697 | -28.2697
2025-04-14 15:00:00 | 5.04 | 26.8173 | 4.8531 | 0 | 69.2707 | -16.9242 | -21.7773
2025-04-14 16:00:00 | 12.96 | 18.8657 | 5.9057 | 0 | 74.4677 | -8.8818e-16 | -5.9057
2025-04-14 17:00:00 | 14.28 | 9.9969 | 0 | 4.2831 | 70.1847 | 4.4409e-15 | 4.2831
2025-04-14 18:00:00 | 6 | 0.81531 | 0 | 5.1847 | 65 | 3.5527e-15 | 5.1847
2025-04-14 19:00:00 | 6.24 | 0 | 0 | 0 | 65 | 6.24 | 6.24
2025-04-14 20:00:00 | 6.84 | 0 | 0 | 0 | 65 | 6.84 | 6.84
2025-04-14 21:00:00 | 6 | 0 | 0 | 0 | 65 | 6 | 6
2025-04-14 22:00:00 | 6.6 | 0 | 0 | 0 | 65 | 6.6 | 6.6
2025-04-14 23:00:00 | 6.24 | 0 | 0 | 0 | 65 | 6.24 | 6.24
2025-04-15 00:00:00 | 6.48 | 0 | 0 | 0 | 65 | 6.48 | 6.48
2025-04-15 01:00:00 | 6.72 | 0 | 0 | 0 | 65 | 6.72 | 6.72
2025-04-15 02:00:00 | 6.24 | 0 | 0 | 0 | 65 | 6.24 | 6.24
2025-04-15 03:00:00 | 6.36 | 0 | 0 | 0 | 65 | 6.36 | 6.36
2025-04-15 04:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-15 05:00:00 | 6 | 1.04 | 0 | 0 | 65 | 4.96 | 4.96
2025-04-15 06:00:00 | 8.88 | 10.212 | 0 | 0 | 65 | -1.332 | -1.332
2025-04-15 07:00:00 | 5.76 | 19.0714 | 0 | 0 | 65 | -13.3114 | -13.3114
2025-04-15 08:00:00 | 5.76 | 27.0146 | 0 | 0 | 65 | -21.2546 | -21.2546
2025-04-15 09:00:00 | 6 | 33.5002 | 0 | 0 | 65 | -27.5002 | -27.5002
2025-04-15 10:00:00 | 5.76 | 38.0862 | 0 | 0 | 65 | -32.3262 | -32.3262
2025-04-15 11:00:00 | 4.92 | 40.46 | 0 | 0 | 65 | -35.54 | -35.54
2025-04-15 12:00:00 | 5.76 | 40.46 | 0 | 0 | 65 | -34.7 | -34.7
2025-04-15 13:00:00 | 6.36 | 38.0862 | 0 | 0 | 65 | -31.7262 | -31.7262
2025-04-15 14:00:00 | 4.92 | 33.5002 | 0 | 0 | 65 | -28.5802 | -28.5802
2025-04-15 15:00:00 | 4.8 | 27.0146 | 0 | 0 | 65 | -22.2146 | -22.2146
2025-04-15 16:00:00 | 5.4 | 19.0714 | 0 | 0 | 65 | -13.6714 | -13.6714
2025-04-15 17:00:00 | 5.04 | 10.212 | 4.9545 | 0 | 69.36 | -0.21744 | -5.172
2025-04-15 18:00:00 | 5.4 | 1.04 | 0 | 4.36 | 65 | 8.8818e-16 | 4.36
2025-04-15 19:00:00 | 4.44 | 0 | 0 | 0 | 65 | 4.44 | 4.44
2025-04-15 20:00:00 | 5.04 | 0 | 0 | 0 | 65 | 5.04 | 5.04
2025-04-15 21:00:00 | 5.28 | 0 | 0 | 0 | 65 | 5.28 | 5.28
2025-04-15 22:00:00 | 5.28 | 0 | 0 | 0 | 65 | 5.28 | 5.28
2025-04-15 23:00:00 | 4.44 | 0 | 0 | 0 | 65 | 4.44 | 4.44
2025-04-16 00:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-16 01:00:00 | 4.68 | 0 | 0 | 0 | 65 | 4.68 | 4.68
2025-04-16 02:00:00 | 5.04 | 0 | 0 | 0 | 65 | 5.04 | 5.04
2025-04-16 03:00:00 | 4.92 | 0 | 0 | 0 | 65 | 4.92 | 4.92
2025-04-16 04:00:00 | 5.28 | 0 | 0 | 0 | 65 | 5.28 | 5.28
2025-04-16 05:00:00 | 4.68 | 1.263 | 0 | 0 | 65 | 3.417 | 3.417
2025-04-16 06:00:00 | 5.52 | 10.425 | 0 | 0 | 65 | -4.905 | -4.905
2025-04-16 07:00:00 | 4.68 | 19.2748 | 0 | 0 | 65 | -14.5948 | -14.5948
2025-04-16 08:00:00 | 4.68 | 27.2093 | 0 | 0 | 65 | -22.5293 | -22.5293
2025-04-16 09:00:00 | 5.16 | 33.6879 | 0 | 0 | 65 | -28.5279 | -28.5279
2025-04-16 10:00:00 | 5.52 | 38.2689 | 0 | 0 | 65 | -32.7489 | -32.7489
2025-04-16 11:00:00 | 4.8 | 40.6402 | 0 | 0 | 65 | -35.8402 | -35.8402
2025-04-16 12:00:00 | 5.04 | 40.6402 | 0 | 0 | 65 | -35.6002 | -35.6002
2025-04-16 13:00:00 | 4.2 | 38.2689 | 0 | 0 | 65 | -34.0689 | -34.0689
2025-04-16 14:00:00 | 4.8 | 33.6879 | 0 | 0 | 65 | -28.8879 | -28.8879
2025-04-16 15:00:00 | 5.4 | 27.2093 | 0 | 0 | 65 | -21.8093 | -21.8093
2025-04-16 16:00:00 | 4.56 | 19.2748 | 0 | 0 | 65 | -14.7148 | -14.7148
2025-04-16 17:00:00 | 4.56 | 10.425 | 4.4285 | 0 | 68.897 | -1.4365 | -5.865
2025-04-16 18:00:00 | 5.16 | 1.263 | 0 | 3.897 | 65 | -3.1086e-15 | 3.897
2025-04-16 19:00:00 | 4.92 | 0 | 0 | 0 | 65 | 4.92 | 4.92
2025-04-16 20:00:00 | 4.68 | 0 | 0 | 0 | 65 | 4.68 | 4.68
2025-04-16 21:00:00 | 5.76 | 0 | 0 | 0 | 65 | 5.76 | 5.76
2025-04-16 22:00:00 | 4.8 | 0 | 0 | 0 | 65 | 4.8 | 4.8
2025-04-16 23:00:00 | 5.16 | 0 | 0 | 0 | 65 | 5.16 | 5.16
2025-04-17 00:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-17 01:00:00 | 4.92 | 0 | 0 | 0 | 65 | 4.92 | 4.92
2025-04-17 02:00:00 | 4.92 | 0 | 0 | 0 | 65 | 4.92 | 4.92
2025-04-17 03:00:00 | 5.88 | 0 | 0 | 0 | 65 | 5.88 | 5.88
2025-04-17 04:00:00 | 5.64 | 0 | 0 | 0 | 65 | 5.64 | 5.64
2025-04-17 05:00:00 | 5.52 | 1.4841 | 0 | 0 | 65 | 4.0359 | 4.0359
2025-04-17 06:00:00 | 5.76 | 10.6359 | 0 | 0 | 65 | -4.8759 | -4.8759
2025-04-17 07:00:00 | 5.28 | 19.4758 | 0 | 0 | 65 | -14.1958 | -14.1958
2025-04-17 08:00:00 | 4.68 | 27.4014 | 0 | 0 | 65 | -22.7214 | -22.7214
2025-04-17 09:00:00 | 5.4 | 33.8727 | 0 | 0 | 65 | -28.4727 | -28.4727
2025-04-17 10:00:00 | 5.04 | 38.4486 | 0 | 0 | 65 | -33.4086 | -33.4086
2025-04-17 11:00:00 | 5.28 | 40.8172 | 0 | 0 | 65 | -35.5372 | -35.5372
2025-04-17 12:00:00 | 5.28 | 40.8172 | 0 | 0 | 65 | -35.5372 | -35.5372
2025-04-17 13:00:00 | 4.68 | 38.4486 | 0 | 0 | 65 | -33.7686 | -33.7686
2025-04-17 14:00:00 | 4.68 | 33.8727 | 0 | 0 | 65 | -29.1927 | -29.1927
2025-04-17 15:00:00 | 4.8 | 27.4014 | 0 | 0 | 65 | -22.6014 | -22.6014
2025-04-17 16:00:00 | 5.16 | 19.4758 | 0 | 0 | 65 | -14.3158 | -14.3158
2025-04-17 17:00:00 | 4.56 | 10.6359 | 4.0408 | 0 | 68.5559 | -2.0351 | -6.0759
2025-04-17 18:00:00 | 5.04 | 1.4841 | 0 | 3.5559 | 65 | -3.9968e-15 | 3.5559
2025-04-17 19:00:00 | 4.92 | 0 | 0 | 0 | 65 | 4.92 | 4.92
2025-04-17 20:00:00 | 4.8 | 0 | 0 | 0 | 65 | 4.8 | 4.8
2025-04-17 21:00:00 | 4.44 | 0 | 0 | 0 | 65 | 4.44 | 4.44
2025-04-17 22:00:00 | 6.12 | 0 | 0 | 0 | 65 | 6.12 | 6.12
2025-04-17 23:00:00 | 5.04 | 0 | 0 | 0 | 65 | 5.04 | 5.04
2025-04-18 00:00:00 | 6 | 0 | 0 | 0 | 65 | 6 | 6
2025-04-18 01:00:00 | 4.92 | 0 | 0 | 0 | 65 | 4.92 | 4.92
2025-04-18 02:00:00 | 6.12 | 0 | 0 | 0 | 65 | 6.12 | 6.12
2025-04-18 03:00:00 | 5.88 | 0 | 0 | 0 | 65 | 5.88 | 5.88
2025-04-18 04:00:00 | 5.64 | 0 | 0 | 0 | 65 | 5.64 | 5.64
2025-04-18 05:00:00 | 5.04 | 1.7034 | 0 | 0 | 65 | 3.3366 | 3.3366
2025-04-18 06:00:00 | 5.64 | 10.8446 | 0 | 0 | 65 | -5.2046 | -5.2046
2025-04-18 07:00:00 | 4.8 | 19.6743 | 0 | 0 | 65 | -14.8743 | -14.8743
2025-04-18 08:00:00 | 5.52 | 27.5908 | 0 | 0 | 65 | -22.0708 | -22.0708
2025-04-18 09:00:00 | 5.04 | 34.0547 | 0 | 0 | 65 | -29.0147 | -29.0147
2025-04-18 10:00:00 | 5.4 | 38.6253 | 0 | 0 | 65 | -33.2253 | -33.2253
2025-04-18 11:00:00 | 4.8 | 40.9912 | 0 | 0 | 65 | -36.1912 | -36.1912
2025-04-18 12:00:00 | 5.28 | 40.9912 | 0 | 0 | 65 | -35.7112 | -35.7112
2025-04-18 13:00:00 | 4.8 | 38.6253 | 0 | 0 | 65 | -33.8253 | -33.8253
2025-04-18 14:00:00 | 4.44 | 34.0547 | 0 | 0 | 65 | -29.6147 | -29.6147
2025-04-18 15:00:00 | 5.28 | 27.5908 | 0 | 0 | 65 | -22.3108 | -22.3108
2025-04-18 16:00:00 | 5.16 | 19.6743 | 0 | 0 | 65 | -14.5143 | -14.5143
2025-04-18 17:00:00 | 5.16 | 10.8446 | 4.7461 | 0 | 69.1766 | -0.93845 | -5.6846
2025-04-18 18:00:00 | 5.88 | 1.7034 | 0 | 4.1766 | 65 | 3.5527e-15 | 4.1766
2025-04-18 19:00:00 | 5.04 | 0 | 0 | 0 | 65 | 5.04 | 5.04
2025-04-18 20:00:00 | 6 | 0 | 0 | 0 | 65 | 6 | 6
2025-04-18 21:00:00 | 6.48 | 0 | 0 | 0 | 65 | 6.48 | 6.48
2025-04-18 22:00:00 | 7.2 | 0 | 0 | 0 | 65 | 7.2 | 7.2
2025-04-18 23:00:00 | 6.84 | 0 | 0 | 0 | 65 | 6.84 | 6.84
2025-04-19 00:00:00 | 6.36 | 0 | 0 | 0 | 65 | 6.36 | 6.36
2025-04-19 01:00:00 | 6.24 | 0 | 0 | 0 | 65 | 6.24 | 6.24
2025-04-19 02:00:00 | 7.8 | 0 | 0 | 0 | 65 | 7.8 | 7.8
2025-04-19 03:00:00 | 6.6 | 0 | 0 | 0 | 65 | 6.6 | 6.6
2025-04-19 04:00:00 | 7.8 | 0 | 0 | 0 | 65 | 7.8 | 7.8
2025-04-19 05:00:00 | 6.24 | 1.9207 | 0 | 0 | 65 | 4.3193 | 4.3193
2025-04-19 06:00:00 | 6.48 | 11.0511 | 0 | 0 | 65 | -4.5711 | -4.5711
2025-04-19 07:00:00 | 6.96 | 19.8704 | 0 | 0 | 65 | -12.9104 | -12.9104
2025-04-19 08:00:00 | 7.2 | 27.7775 | 0 | 0 | 65 | -20.5775 | -20.5775
2025-04-19 09:00:00 | 6.6 | 34.2337 | 0 | 0 | 65 | -27.6337 | -27.6337
2025-04-19 10:00:00 | 7.08 | 38.7989 | 0 | 0 | 65 | -31.7189 | -31.7189
2025-04-19 11:00:00 | 6.96 | 41.162 | 0 | 0 | 65 | -34.202 | -34.202
2025-04-19 12:00:00 | 6.36 | 41.162 | 0 | 0 | 65 | -34.802 | -34.802
2025-04-19 13:00:00 | 6.96 | 38.7989 | 0 | 0 | 65 | -31.8389 | -31.8389
2025-04-19 14:00:00 | 6.96 | 34.2337 | 0 | 0 | 65 | -27.2737 | -27.2737
2025-04-19 15:00:00 | 7.44 | 27.7775 | 0 | 0 | 65 | -20.3375 | -20.3375
2025-04-19 16:00:00 | 6.6 | 19.8704 | 0 | 0 | 65 | -13.2704 | -13.2704
2025-04-19 17:00:00 | 6.96 | 11.0511 | 0 | 0 | 65 | -4.0911 | -4.0911
2025-04-19 18:00:00 | 6.96 | 1.9207 | 0 | 0 | 65 | 5.0393 | 5.0393
2025-04-19 19:00:00 | 6.72 | 0 | 0 | 0 | 65 | 6.72 | 6.72
2025-04-19 20:00:00 | 7.92 | 0 | 0 | 0 | 65 | 7.92 | 7.92
2025-04-19 21:00:00 | 7.92 | 0 | 0 | 0 | 65 | 7.92 | 7.92
2025-04-19 22:00:00 | 7.2 | 0 | 0 | 0 | 65 | 7.2 | 7.2
2025-04-19 23:00:00 | 7.68 | 0 | 0 | 0 | 65 | 7.68 | 7.68
2025-04-20 00:00:00 | 7.08 | 0 | 0 | 0 | 65 | 7.08 | 7.08
2025-04-20 01:00:00 | 7.32 | 0 | 0 | 0 | 65 | 7.32 | 7.32
2025-04-20 02:00:00 | 8.64 | 0 | 0 | 0 | 65 | 8.64 | 8.64
2025-04-20 03:00:00 | 7.8 | 0 | 0 | 0 | 65 | 7.8 | 7.8
2025-04-20 04:00:00 | 7.32 | 0 | 0 | 0 | 65 | 7.32 | 7.32
2025-04-20 05:00:00 | 7.32 | 2.136 | 0 | 0 | 65 | 5.184 | 5.184
2025-04-20 06:00:00 | 7.32 | 11.2553 | 0 | 0 | 65 | -3.9353 | -3.9353
2025-04-20 07:00:00 | 8.04 | 20.0639 | 0 | 0 | 65 | -12.0239 | -12.0239
2025-04-20 08:00:00 | 7.92 | 27.9615 | 0 | 0 | 65 | -20.0415 | -20.0415
2025-04-20 09:00:00 | 7.44 | 34.4098 | 0 | 0 | 65 | -26.9698 | -26.9698
2025-04-20 10:00:00 | 7.68 | 38.9695 | 0 | 0 | 65 | -31.2895 | -31.2895
2025-04-20 11:00:00 | 7.2 | 41.3297 | 0 | 0 | 65 | -34.1297 | -34.1297
2025-04-20 12:00:00 | 7.44 | 41.3297 | 0 | 0 | 65 | -33.8897 | -33.8897
2025-04-20 13:00:00 | 7.2 | 38.9695 | 0 | 0 | 65 | -31.7695 | -31.7695
2025-04-20 14:00:00 | 7.92 | 34.4098 | 0 | 0 | 65 | -26.4898 | -26.4898
2025-04-20 15:00:00 | 7.32 | 27.9615 | 0 | 0 | 65 | -20.6415 | -20.6415
2025-04-20 16:00:00 | 7.68 | 20.0639 | 0 | 0 | 65 | -12.3839 | -12.3839
2025-04-20 17:00:00 | 7.32 | 11.2553 | 0 | 0 | 65 | -3.9353 | -3.9353
2025-04-20 18:00:00 | 9.12 | 2.136 | 0 | 0 | 65 | 6.984 | 6.984
2025-04-20 19:00:00 | 8.88 | 0 | 0 | 0 | 65 | 8.88 | 8.88
2025-04-20 20:00:00 | 7.68 | 0 | 0 | 0 | 65 | 7.68 | 7.68
2025-04-20 21:00:00 | 7.32 | 0 | 0 | 0 | 65 | 7.32 | 7.32
2025-04-20 22:00:00 | 7.32 | 0 | 0 | 0 | 65 | 7.32 | 7.32
2025-04-20 23:00:00 | 7.32 | 0 | 0 | 0 | 65 | 7.32 | 7.32
2025-04-21 00:00:00 | 7.8 | 0 | 0 | 0 | 65 | 7.8 | 7.8
2025-04-21 01:00:00 | 8.04 | 0 | 0 | 0 | 65 | 8.04 | 8.04
2025-04-21 02:00:00 | 7.44 | 0 | 0 | 0 | 65 | 7.44 | 7.44
2025-04-21 03:00:00 | 7.44 | 0 | 0 | 0 | 65 | 7.44 | 7.44
2025-04-21 04:00:00 | 8.16 | 0 | 0 | 0 | 65 | 8.16 | 8.16
2025-04-21 05:00:00 | 7.2 | 2.3492 | 0 | 0 | 65 | 4.8508 | 4.8508
2025-04-21 06:00:00 | 7.2 | 11.4572 | 0 | 0 | 65 | -4.2572 | -4.2572
2025-04-21 07:00:00 | 7.68 | 20.2549 | 0 | 0 | 65 | -12.5749 | -12.5749
2025-04-21 08:00:00 | 7.8 | 28.1426 | 0 | 0 | 65 | -20.3426 | -20.3426
2025-04-21 09:00:00 | 7.2 | 34.583 | 0 | 0 | 65 | -27.383 | -27.383
2025-04-21 10:00:00 | 6.96 | 39.137 | 0 | 0 | 65 | -32.177 | -32.177
2025-04-21 11:00:00 | 6.96 | 41.4943 | 0 | 0 | 65 | -34.5343 | -34.5343
2025-04-21 12:00:00 | 6.36 | 41.4943 | 0 | 0 | 65 | -35.1343 | -35.1343
2025-04-21 13:00:00 | 7.2 | 39.137 | 0 | 0 | 65 | -31.937 | -31.937
2025-04-21 14:00:00 | 6 | 34.583 | 0 | 0 | 65 | -28.583 | -28.583
2025-04-21 15:00:00 | 5.76 | 28.1426 | 0 | 0 | 65 | -22.3826 | -22.3826
2025-04-21 16:00:00 | 5.64 | 20.2549 | 0 | 0 | 65 | -14.6149 | -14.6149
2025-04-21 17:00:00 | 5.64 | 11.4572 | 4.285 | 0 | 68.7708 | -1.5323 | -5.8172
2025-04-21 18:00:00 | 6.12 | 2.3492 | 0 | 3.7708 | 65 | 3.9968e-15 | 3.7708
2025-04-21 19:00:00 | 6.48 | 0 | 0 | 0 | 65 | 6.48 | 6.48
2025-04-21 20:00:00 | 5.64 | 0 | 0 | 0 | 65 | 5.64 | 5.64
2025-04-21 21:00:00 | 5.64 | 0 | 0 | 0 | 65 | 5.64 | 5.64
2025-04-21 22:00:00 | 5.88 | 0 | 0 | 0 | 65 | 5.88 | 5.88
2025-04-21 23:00:00 | 6.84 | 0 | 0 | 0 | 65 | 6.84 | 6.84
2025-04-22 00:00:00 | 7.92 | 0 | 0 | 0 | 65 | 7.92 | 7.92
2025-04-22 01:00:00 | 7.2 | 0 | 0 | 0 | 65 | 7.2 | 7.2
2025-04-22 02:00:00 | 6.84 | 0 | 0 | 0 | 65 | 6.84 | 6.84
2025-04-22 03:00:00 | 6.48 | 0 | 0 | 0 | 65 | 6.48 | 6.48
2025-04-22 04:00:00 | 7.08 | 0 | 0 | 0 | 65 | 7.08 | 7.08
2025-04-22 05:00:00 | 8.16 | 2.5603 | 0 | 0 | 65 | 5.5997 | 5.5997
2025-04-22 06:00:00 | 6.72 | 11.6567 | 0 | 0 | 65 | -4.9367 | -4.9367
2025-04-22 07:00:00 | 6.6 | 20.4432 | 0 | 0 | 65 | -13.8432 | -13.8432
2025-04-22 08:00:00 | 6.24 | 28.321 | 0 | 0 | 65 | -22.081 | -22.081
2025-04-22 09:00:00 | 5.76 | 34.7532 | 0 | 0 | 65 | -28.9932 | -28.9932
2025-04-22 10:00:00 | 5.52 | 39.3014 | 0 | 0 | 65 | -33.7814 | -33.7814
2025-04-22 11:00:00 | 6.36 | 41.6557 | 0 | 0 | 65 | -35.2957 | -35.2957
2025-04-22 12:00:00 | 5.52 | 41.6557 | 0 | 0 | 65 | -36.1357 | -36.1357
2025-04-22 13:00:00 | 5.04 | 39.3014 | 0 | 0 | 65 | -34.2614 | -34.2614
2025-04-22 14:00:00 | 5.28 | 34.7532 | 0 | 0 | 65 | -29.4732 | -29.4732
2025-04-22 15:00:00 | 4.32 | 28.321 | 0 | 0 | 65 | -24.001 | -24.001
2025-04-22 16:00:00 | 4.44 | 20.4432 | 0 | 0 | 65 | -16.0032 | -16.0032
2025-04-22 17:00:00 | 6.12 | 11.6567 | 2.2724 | 0 | 66.9997 | -3.2643 | -5.5367
2025-04-22 18:00:00 | 4.56 | 2.5603 | 0 | 1.9997 | 65 | -1.1102e-15 | 1.9997
2025-04-22 19:00:00 | 4.8 | 0 | 0 | 0 | 65 | 4.8 | 4.8
2025-04-22 20:00:00 | 5.4 | 0 | 0 | 0 | 65 | 5.4 | 5.4
2025-04-22 21:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-22 22:00:00 | 5.4 | 0 | 0 | 0 | 65 | 5.4 | 5.4
2025-04-22 23:00:00 | 5.76 | 0 | 0 | 0 | 65 | 5.76 | 5.76
2025-04-23 00:00:00 | 5.76 | 0 | 0 | 0 | 65 | 5.76 | 5.76
2025-04-23 01:00:00 | 6 | 0 | 0 | 0 | 65 | 6 | 6
2025-04-23 02:00:00 | 5.04 | 0 | 0 | 0 | 65 | 5.04 | 5.04
2025-04-23 03:00:00 | 5.88 | 0 | 0 | 0 | 65 | 5.88 | 5.88
2025-04-23 04:00:00 | 7.08 | 0 | 0 | 0 | 65 | 7.08 | 7.08
2025-04-23 05:00:00 | 5.88 | 2.7691 | 0 | 0 | 65 | 3.1109 | 3.1109
2025-04-23 06:00:00 | 6.24 | 11.8538 | 0 | 0 | 65 | -5.6138 | -5.6138
2025-04-23 07:00:00 | 5.52 | 20.6289 | 0 | 0 | 65 | -15.1089 | -15.1089
2025-04-23 08:00:00 | 5.64 | 28.4965 | 0 | 0 | 65 | -22.8565 | -22.8565
2025-04-23 09:00:00 | 5.04 | 34.9204 | 0 | 0 | 65 | -29.8804 | -29.8804
2025-04-23 10:00:00 | 6.6 | 39.4627 | 0 | 0 | 65 | -32.8627 | -32.8627
2025-04-23 11:00:00 | 5.52 | 41.814 | 0 | 0 | 65 | -36.294 | -36.294
2025-04-23 12:00:00 | 4.8 | 41.814 | 0 | 0 | 65 | -37.014 | -37.014
2025-04-23 13:00:00 | 4.56 | 39.4627 | 0 | 0 | 65 | -34.9027 | -34.9027
2025-04-23 14:00:00 | 4.92 | 34.9204 | 0 | 0 | 65 | -30.0004 | -30.0004
2025-04-23 15:00:00 | 4.56 | 28.4965 | 0 | 0 | 65 | -23.9365 | -23.9365
2025-04-23 16:00:00 | 5.4 | 20.6289 | 0 | 0 | 65 | -15.2289 | -15.2289
2025-04-23 17:00:00 | 5.16 | 11.8538 | 1.4897 | 0 | 66.3109 | -5.2041 | -6.6938
2025-04-23 18:00:00 | 4.08 | 2.7691 | 0 | 1.3109 | 65 | 1.7764e-15 | 1.3109
2025-04-23 19:00:00 | 4.44 | 0 | 0 | 0 | 65 | 4.44 | 4.44
2025-04-23 20:00:00 | 4.92 | 0 | 0 | 0 | 65 | 4.92 | 4.92
2025-04-23 21:00:00 | 4.68 | 0 | 0 | 0 | 65 | 4.68 | 4.68
2025-04-23 22:00:00 | 5.28 | 0 | 0 | 0 | 65 | 5.28 | 5.28
2025-04-23 23:00:00 | 5.76 | 0 | 0 | 0 | 65 | 5.76 | 5.76
2025-04-24 00:00:00 | 5.16 | 0 | 0 | 0 | 65 | 5.16 | 5.16
2025-04-24 01:00:00 | 5.76 | 0 | 0 | 0 | 65 | 5.76 | 5.76
2025-04-24 02:00:00 | 4.8 | 0 | 0 | 0 | 65 | 4.8 | 4.8
2025-04-24 03:00:00 | 5.88 | 0 | 0 | 0 | 65 | 5.88 | 5.88
2025-04-24 04:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-24 05:00:00 | 6.36 | 2.9756 | 0 | 0 | 65 | 3.3844 | 3.3844
2025-04-24 06:00:00 | 5.28 | 12.0483 | 0 | 0 | 65 | -6.7683 | -6.7683
2025-04-24 07:00:00 | 5.88 | 20.8119 | 0 | 0 | 65 | -14.9319 | -14.9319
2025-04-24 08:00:00 | 4.92 | 28.6691 | 0 | 0 | 65 | -23.7491 | -23.7491
2025-04-24 09:00:00 | 5.76 | 35.0845 | 0 | 0 | 65 | -29.3245 | -29.3245
2025-04-24 10:00:00 | 5.52 | 39.6209 | 0 | 0 | 65 | -34.1009 | -34.1009
2025-04-24 11:00:00 | 5.4 | 41.9691 | 0 | 0 | 65 | -36.5691 | -36.5691
2025-04-24 12:00:00 | 6.12 | 41.9691 | 0 | 0 | 65 | -35.8491 | -35.8491
2025-04-24 13:00:00 | 5.64 | 39.6209 | 0 | 0 | 65 | -33.9809 | -33.9809
2025-04-24 14:00:00 | 4.68 | 35.0845 | 0 | 0 | 65 | -30.4045 | -30.4045
2025-04-24 15:00:00 | 5.64 | 28.6691 | 0 | 0 | 65 | -23.0291 | -23.0291
2025-04-24 16:00:00 | 5.4 | 20.8119 | 0 | 0 | 65 | -15.4119 | -15.4119
2025-04-24 17:00:00 | 5.76 | 12.0483 | 2.6186 | 0 | 67.3044 | -3.6697 | -6.2883
2025-04-24 18:00:00 | 5.28 | 2.9756 | 0 | 2.3044 | 65 | 0 | 2.3044
2025-04-24 19:00:00 | 5.28 | 0 | 0 | 0 | 65 | 5.28 | 5.28
2025-04-24 20:00:00 | 6.36 | 0 | 0 | 0 | 65 | 6.36 | 6.36
2025-04-24 21:00:00 | 6 | 0 | 0 | 0 | 65 | 6 | 6
2025-04-24 22:00:00 | 7.2 | 0 | 0 | 0 | 65 | 7.2 | 7.2
2025-04-24 23:00:00 | 7.44 | 0 | 0 | 0 | 65 | 7.44 | 7.44
2025-04-25 00:00:00 | 7.44 | 0 | 0 | 0 | 65 | 7.44 | 7.44
2025-04-25 01:00:00 | 7.2 | 0 | 0 | 0 | 65 | 7.2 | 7.2
2025-04-25 02:00:00 | 6.84 | 0 | 0 | 0 | 65 | 6.84 | 6.84
2025-04-25 03:00:00 | 6.6 | 0 | 0 | 0 | 65 | 6.6 | 6.6
2025-04-25 04:00:00 | 7.08 | 0 | 0 | 0 | 65 | 7.08 | 7.08
2025-04-25 05:00:00 | 7.56 | 3.1798 | 0 | 0 | 65 | 4.3802 | 4.3802
2025-04-25 06:00:00 | 7.44 | 12.2403 | 0 | 0 | 65 | -4.8003 | -4.8003
2025-04-25 07:00:00 | 7.08 | 20.9922 | 0 | 0 | 65 | -13.9122 | -13.9122
2025-04-25 08:00:00 | 7.08 | 28.8389 | 0 | 0 | 65 | -21.7589 | -21.7589
2025-04-25 09:00:00 | 6.48 | 35.2457 | 0 | 0 | 65 | -28.7657 | -28.7657
2025-04-25 10:00:00 | 7.2 | 39.776 | 0 | 0 | 65 | -32.576 | -32.576
2025-04-25 11:00:00 | 7.32 | 42.121 | 0 | 0 | 65 | -34.801 | -34.801
2025-04-25 12:00:00 | 6.6 | 42.121 | 0 | 0 | 65 | -35.521 | -35.521
2025-04-25 13:00:00 | 6.6 | 39.776 | 0 | 0 | 65 | -33.176 | -33.176
2025-04-25 14:00:00 | 6.48 | 35.2457 | 0 | 0 | 65 | -28.7657 | -28.7657
2025-04-25 15:00:00 | 6.48 | 28.8389 | 0 | 0 | 65 | -22.3589 | -22.3589
2025-04-25 16:00:00 | 6.96 | 20.9922 | 0 | 0 | 65 | -14.0322 | -14.0322
2025-04-25 17:00:00 | 6.84 | 12.2403 | 4.4321 | 0 | 68.9002 | -0.96826 | -5.4003
2025-04-25 18:00:00 | 7.08 | 3.1798 | 0 | 3.9002 | 65 | -2.6645e-15 | 3.9002
2025-04-25 19:00:00 | 6.72 | 0 | 0 | 0 | 65 | 6.72 | 6.72
2025-04-25 20:00:00 | 6.84 | 0 | 0 | 0 | 65 | 6.84 | 6.84
2025-04-25 21:00:00 | 6.6 | 0 | 0 | 0 | 65 | 6.6 | 6.6
2025-04-25 22:00:00 | 7.68 | 0 | 0 | 0 | 65 | 7.68 | 7.68
2025-04-25 23:00:00 | 7.56 | 0 | 0 | 0 | 65 | 7.56 | 7.56
2025-04-26 00:00:00 | 6.36 | 0 | 0 | 0 | 65 | 6.36 | 6.36
2025-04-26 01:00:00 | 6.6 | 0 | 0 | 0 | 65 | 6.6 | 6.6
2025-04-26 02:00:00 | 7.2 | 0 | 0 | 0 | 65 | 7.2 | 7.2
2025-04-26 03:00:00 | 7.2 | 0 | 0 | 0 | 65 | 7.2 | 7.2
2025-04-26 04:00:00 | 7.2 | 0 | 0 | 0 | 65 | 7.2 | 7.2
2025-04-26 05:00:00 | 6.96 | 3.3815 | 0 | 0 | 65 | 3.5785 | 3.5785
2025-04-26 06:00:00 | 6.96 | 12.4298 | 0 | 0 | 65 | -5.4698 | -5.4698
2025-04-26 07:00:00 | 6.36 | 21.1697 | 0 | 0 | 65 | -14.8097 | -14.8097
2025-04-26 08:00:00 | 5.52 | 29.0057 | 0 | 0 | 65 | -23.4857 | -23.4857
2025-04-26 09:00:00 | 5.64 | 35.4038 | 0 | 0 | 65 | -29.7638 | -29.7638
2025-04-26 10:00:00 | 5.64 | 39.9279 | 0 | 0 | 65 | -34.2879 | -34.2879
2025-04-26 11:00:00 | 7.32 | 42.2698 | 0 | 0 | 65 | -34.9498 | -34.9498
2025-04-26 12:00:00 | 5.04 | 42.2698 | 0 | 0 | 65 | -37.2298 | -37.2298
2025-04-26 13:00:00 | 5.04 | 39.9279 | 0 | 0 | 65 | -34.8879 | -34.8879
2025-04-26 14:00:00 | 5.28 | 35.4038 | 0 | 0 | 65 | -30.1238 | -30.1238
2025-04-26 15:00:00 | 4.68 | 29.0057 | 0 | 0 | 65 | -24.3257 | -24.3257
2025-04-26 16:00:00 | 5.28 | 21.1697 | 0 | 0 | 65 | -15.8897 | -15.8897
2025-04-26 17:00:00 | 5.52 | 12.4298 | 0 | 0 | 65 | -6.9098 | -6.9098
2025-04-26 18:00:00 | 5.4 | 3.3815 | 0 | 0 | 65 | 2.0185 | 2.0185
2025-04-26 19:00:00 | 5.16 | 0 | 0 | 0 | 65 | 5.16 | 5.16
2025-04-26 20:00:00 | 5.16 | 0 | 0 | 0 | 65 | 5.16 | 5.16
2025-04-26 21:00:00 | 5.04 | 0 | 0 | 0 | 65 | 5.04 | 5.04
2025-04-26 22:00:00 | 6.84 | 0 | 0 | 0 | 65 | 6.84 | 6.84
2025-04-26 23:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-27 00:00:00 | 5.88 | 0 | 0 | 0 | 65 | 5.88 | 5.88
2025-04-27 01:00:00 | 5.4 | 0 | 0 | 0 | 65 | 5.4 | 5.4
2025-04-27 02:00:00 | 5.28 | 0 | 0 | 0 | 65 | 5.28 | 5.28
2025-04-27 03:00:00 | 6 | 0 | 0 | 0 | 65 | 6 | 6
2025-04-27 04:00:00 | 7.8 | 0 | 0 | 0 | 65 | 7.8 | 7.8
2025-04-27 05:00:00 | 5.28 | 3.5807 | 0 | 0 | 65 | 1.6993 | 1.6993
2025-04-27 06:00:00 | 5.28 | 12.6165 | 0 | 0 | 65 | -7.3365 | -7.3365
2025-04-27 07:00:00 | 5.28 | 21.3444 | 0 | 0 | 65 | -16.0644 | -16.0644
2025-04-27 08:00:00 | 5.52 | 29.1696 | 0 | 0 | 65 | -23.6496 | -23.6496
2025-04-27 09:00:00 | 5.88 | 35.5589 | 0 | 0 | 65 | -29.6789 | -29.6789
2025-04-27 10:00:00 | 6.12 | 40.0768 | 0 | 0 | 65 | -33.9568 | -33.9568
2025-04-27 11:00:00 | 5.28 | 42.4154 | 0 | 0 | 65 | -37.1354 | -37.1354
2025-04-27 12:00:00 | 5.88 | 42.4154 | 0 | 0 | 65 | -36.5354 | -36.5354
2025-04-27 13:00:00 | 4.68 | 40.0768 | 0 | 0 | 65 | -35.3968 | -35.3968
2025-04-27 14:00:00 | 4.56 | 35.5589 | 0 | 0 | 65 | -30.9989 | -30.9989
2025-04-27 15:00:00 | 5.52 | 29.1696 | 0 | 0 | 65 | -23.6496 | -23.6496
2025-04-27 16:00:00 | 5.16 | 21.3444 | 0 | 0 | 65 | -16.1844 | -16.1844
2025-04-27 17:00:00 | 5.28 | 12.6165 | 0 | 0 | 65 | -7.3365 | -7.3365
2025-04-27 18:00:00 | 4.56 | 3.5807 | 0 | 0 | 65 | 0.97926 | 0.97926
2025-04-27 19:00:00 | 4.8 | 0 | 0 | 0 | 65 | 4.8 | 4.8
2025-04-27 20:00:00 | 4.68 | 0 | 0 | 0 | 65 | 4.68 | 4.68
2025-04-27 21:00:00 | 5.64 | 0 | 0 | 0 | 65 | 5.64 | 5.64
2025-04-27 22:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-27 23:00:00 | 5.64 | 0 | 0 | 0 | 65 | 5.64 | 5.64
2025-04-28 00:00:00 | 4.92 | 0 | 0 | 0 | 65 | 4.92 | 4.92
2025-04-28 01:00:00 | 5.64 | 0 | 0 | 0 | 65 | 5.64 | 5.64
2025-04-28 02:00:00 | 4.92 | 0 | 0 | 0 | 65 | 4.92 | 4.92
2025-04-28 03:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-28 04:00:00 | 5.16 | 0 | 0 | 0 | 65 | 5.16 | 5.16
2025-04-28 05:00:00 | 6.12 | 3.7774 | 0 | 0 | 65 | 2.3426 | 2.3426
2025-04-28 06:00:00 | 5.4 | 12.8006 | 0 | 0 | 65 | -7.4006 | -7.4006
2025-04-28 07:00:00 | 4.44 | 21.5163 | 0 | 0 | 65 | -17.0763 | -17.0763
2025-04-28 08:00:00 | 5.04 | 29.3306 | 0 | 0 | 65 | -24.2906 | -24.2906
2025-04-28 09:00:00 | 5.76 | 35.7109 | 0 | 0 | 65 | -29.9509 | -29.9509
2025-04-28 10:00:00 | 4.8 | 40.2225 | 0 | 0 | 65 | -35.4225 | -35.4225
2025-04-28 11:00:00 | 5.28 | 42.5578 | 0 | 0 | 65 | -37.2778 | -37.2778
2025-04-28 12:00:00 | 5.4 | 42.5578 | 0 | 0 | 65 | -37.1578 | -37.1578
2025-04-28 13:00:00 | 5.16 | 40.2225 | 0 | 0 | 65 | -35.0625 | -35.0625
2025-04-28 14:00:00 | 5.04 | 35.7109 | 0 | 0 | 65 | -30.6709 | -30.6709
2025-04-28 15:00:00 | 5.16 | 29.3306 | 0 | 0 | 65 | -24.1706 | -24.1706
2025-04-28 16:00:00 | 5.64 | 21.5163 | 0 | 0 | 65 | -15.8763 | -15.8763
2025-04-28 17:00:00 | 4.32 | 12.8006 | 1.7075 | 0 | 66.5026 | -6.7731 | -8.4806
2025-04-28 18:00:00 | 5.28 | 3.7774 | 0 | 1.5026 | 65 | 0 | 1.5026
2025-04-28 19:00:00 | 4.92 | 0 | 0 | 0 | 65 | 4.92 | 4.92
2025-04-28 20:00:00 | 5.04 | 0 | 0 | 0 | 65 | 5.04 | 5.04
2025-04-28 21:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-28 22:00:00 | 5.76 | 0 | 0 | 0 | 65 | 5.76 | 5.76
2025-04-28 23:00:00 | 4.68 | 0 | 0 | 0 | 65 | 4.68 | 4.68
2025-04-29 00:00:00 | 5.28 | 0 | 0 | 0 | 65 | 5.28 | 5.28
2025-04-29 01:00:00 | 6.24 | 0 | 0 | 0 | 65 | 6.24 | 6.24
2025-04-29 02:00:00 | 5.04 | 0 | 0 | 0 | 65 | 5.04 | 5.04
2025-04-29 03:00:00 | 6 | 0 | 0 | 0 | 65 | 6 | 6
2025-04-29 04:00:00 | 5.88 | 0 | 0 | 0 | 65 | 5.88 | 5.88
2025-04-29 05:00:00 | 5.28 | 3.9715 | 0 | 0 | 65 | 1.3085 | 1.3085
2025-04-29 06:00:00 | 5.76 | 12.9819 | 0 | 0 | 65 | -7.2219 | -7.2219
2025-04-29 07:00:00 | 5.16 | 21.6853 | 0 | 0 | 65 | -16.5253 | -16.5253
2025-04-29 08:00:00 | 6.96 | 29.4885 | 0 | 0 | 65 | -22.5285 | -22.5285
2025-04-29 09:00:00 | 4.92 | 35.8599 | 0 | 0 | 65 | -30.9399 | -30.9399
2025-04-29 10:00:00 | 6 | 40.3651 | 0 | 0 | 65 | -34.3651 | -34.3651
2025-04-29 11:00:00 | 5.52 | 42.6971 | 0 | 0 | 65 | -37.1771 | -37.1771
2025-04-29 12:00:00 | 4.8 | 42.6971 | 0 | 0 | 65 | -37.8971 | -37.8971
2025-04-29 13:00:00 | 6 | 40.3651 | 0 | 0 | 65 | -34.3651 | -34.3651
2025-04-29 14:00:00 | 5.88 | 35.8599 | 0 | 0 | 65 | -29.9799 | -29.9799
2025-04-29 15:00:00 | 5.04 | 29.4885 | 0 | 0 | 65 | -24.4485 | -24.4485
2025-04-29 16:00:00 | 6.24 | 21.6853 | 0 | 0 | 65 | -15.4453 | -15.4453
2025-04-29 17:00:00 | 5.16 | 12.9819 | 2.0324 | 0 | 66.7885 | -5.7896 | -7.8219
2025-04-29 18:00:00 | 5.76 | 3.9715 | 0 | 1.7885 | 65 | 6.6613e-16 | 1.7885
2025-04-29 19:00:00 | 5.64 | 0 | 0 | 0 | 65 | 5.64 | 5.64
2025-04-29 20:00:00 | 5.52 | 0 | 0 | 0 | 65 | 5.52 | 5.52
2025-04-29 21:00:00 | 6.24 | 0 | 0 | 0 | 65 | 6.24 | 6.24
2025-04-29 22:00:00 | 6.48 | 0 | 0 | 0 | 65 | 6.48 | 6.48
2025-04-29 23:00:00 | 6.12 | 0 | 0 | 0 | 65 | 6.12 | 6.12
2025-04-30 00:00:00 | 6.48 | 0 | 0 | 0 | 65 | 6.48 | 6.48
2025-04-30 01:00:00 | 7.32 | 0 | 0 | 0 | 65 | 7.32 | 7.32
2025-04-30 02:00:00 | 7.92 | 0 | 0 | 0 | 65 | 7.92 | 7.92
2025-04-30 03:00:00 | 6.96 | 0 | 0 | 0 | 65 | 6.96 | 6.96
2025-04-30 04:00:00 | 6.72 | 0 | 0 | 0 | 65 | 6.72 | 6.72
2025-04-30 05:00:00 | 7.32 | 4.1629 | 0 | 0 | 65 | 3.1571 | 3.1571
2025-04-30 06:00:00 | 8.28 | 13.1605 | 0 | 0 | 65 | -4.8805 | -4.8805
2025-04-30 07:00:00 | 6.96 | 21.8514 | 0 | 0 | 65 | -14.8914 | -14.8914
2025-04-30 08:00:00 | 7.8 | 29.6435 | 0 | 0 | 65 | -21.8435 | -21.8435
2025-04-30 09:00:00 | 7.2 | 36.0057 | 0 | 0 | 65 | -28.8057 | -28.8057
2025-04-30 10:00:00 | 6.84 | 40.5045 | 0 | 0 | 65 | -33.6645 | -33.6645
2025-04-30 11:00:00 | 6.96 | 42.8332 | 0 | 0 | 65 | -35.8732 | -35.8732
2025-04-30 12:00:00 | 6.96 | 42.8332 | 0 | 0 | 65 | -35.8732 | -35.8732
2025-04-30 13:00:00 | 6.12 | 40.5045 | 0 | 0 | 65 | -34.3845 | -34.3845
2025-04-30 14:00:00 | 8.04 | 36.0057 | 0 | 0 | 65 | -27.9657 | -27.9657
2025-04-30 15:00:00 | 6.24 | 29.6435 | 0 | 0 | 65 | -23.4035 | -23.4035
2025-04-30 16:00:00 | 6.12 | 21.8514 | 0 | 0 | 65 | -15.7314 | -15.7314
2025-04-30 17:00:00 | 6.6 | 13.1605 | 2.633 | 0 | 67.3171 | -3.9275 | -6.5605
2025-04-30 18:00:00 | 6.48 | 4.1629 | 0 | 2.3171 | 65 | -3.9968e-15 | 2.3171
2025-04-30 19:00:00 | 6.48 | 0 | 0 | 0 | 65 | 6.48 | 6.48
2025-04-30 20:00:00 | 7.2 | 0 | 70.4545 | 0 | 127 | 77.6545 | 7.2
2025-04-30 21:00:00 | 6.96 | 0 | 75 | 0 | 193 | 81.96 | 6.96
2025-04-30 22:00:00 | 6.36 | 0 | 75 | 0 | 259 | 81.36 | 6.36
2025-04-30 23:00:00 | 7.68 | 0 | 75 | 0 | 325 | 82.68 | 7.68
2025-05-01 00:00:00 | 7.44 | 0 | 0 | 0 | 325 | 7.44 | 7.44
2025-05-01 01:00:00 | 7.56 | 0 | 0 | 0 | 325 | 7.56 | 7.56
2025-05-01 02:00:00 | 7.92 | 0 | 0 | 0 | 325 | 7.92 | 7.92
2025-05-01 03:00:00 | 7.32 | 0 | 0 | 0 | 325 | 7.32 | 7.32
2025-05-01 04:00:00 | 8.28 | 0 | 0 | 0 | 325 | 8.28 | 8.28
2025-05-01 05:00:00 | 7.68 | 5.0562 | 0 | 0 | 325 | 2.6238 | 2.6238
2025-05-01 06:00:00 | 8.52 | 15.4954 | 0 | 0 | 325 | -6.9754 | -6.9754
2025-05-01 07:00:00 | 7.44 | 25.5789 | 0 | 0 | 325 | -18.1389 | -18.1389
2025-05-01 08:00:00 | 8.52 | 34.6195 | 0 | 0 | 325 | -26.0995 | -26.0995
2025-05-01 09:00:00 | 6.36 | 42.0012 | 0 | 0 | 325 | -35.6412 | -35.6412
2025-05-01 10:00:00 | 6.12 | 47.2208 | 0 | 0 | 325 | -41.1008 | -41.1008
2025-05-01 11:00:00 | 17.64 | 49.9227 | 0 | 0 | 325 | -32.2827 | -32.2827
2025-05-01 12:00:00 | 21.48 | 49.9227 | 0 | 0 | 325 | -28.4427 | -28.4427
2025-05-01 13:00:00 | 20.4 | 47.2208 | 0 | 0 | 325 | -26.8208 | -26.8208
2025-05-01 14:00:00 | 8.88 | 42.0012 | 0 | 0 | 325 | -33.1212 | -33.1212
2025-05-01 15:00:00 | 6.6 | 34.6195 | 0 | 0 | 325 | -28.0195 | -28.0195
2025-05-01 16:00:00 | 5.52 | 25.5789 | 0 | 0 | 325 | -20.0589 | -20.0589
2025-05-01 17:00:00 | 6.48 | 15.4954 | 0 | 0 | 325 | -9.0154 | -9.0154
2025-05-01 18:00:00 | 6.6 | 5.0562 | 0 | 1.5438 | 323.4562 | -1.9984e-15 | 1.5438
2025-05-01 19:00:00 | 6.6 | 0 | 0 | 0 | 323.4562 | 6.6 | 6.6
2025-05-01 20:00:00 | 7.08 | 0 | 0 | 0 | 323.4562 | 7.08 | 7.08
2025-05-01 21:00:00 | 6.48 | 0 | 0 | 0 | 323.4562 | 6.48 | 6.48
2025-05-01 22:00:00 | 7.32 | 0 | 0 | 0 | 323.4562 | 7.32 | 7.32
2025-05-01 23:00:00 | 7.56 | 0 | 0 | 0 | 323.4562 | 7.56 | 7.56
2025-05-02 00:00:00 | 7.56 | 0 | 0 | 0 | 323.4562 | 7.56 | 7.56
2025-05-02 01:00:00 | 7.56 | 0 | 0 | 0 | 323.4562 | 7.56 | 7.56
2025-05-02 02:00:00 | 7.2 | 0 | 0 | 0 | 323.4562 | 7.2 | 7.2
2025-05-02 03:00:00 | 6.72 | 0 | 0 | 0 | 323.4562 | 6.72 | 6.72
2025-05-02 04:00:00 | 7.32 | 0 | 0 | 0 | 323.4562 | 7.32 | 7.32
2025-05-02 05:00:00 | 7.92 | 5.2722 | 0 | 0 | 323.4562 | 2.6478 | 2.6478
2025-05-02 06:00:00 | 7.56 | 15.6963 | 0 | 0 | 323.4562 | -8.1363 | -8.1363
2025-05-02 07:00:00 | 6.84 | 25.7651 | 0 | 0 | 323.4562 | -18.9251 | -18.9251
2025-05-02 08:00:00 | 7.08 | 34.7926 | 0 | 0 | 323.4562 | -27.7126 | -27.7126
2025-05-02 09:00:00 | 6.84 | 42.1636 | 0 | 0 | 323.4562 | -35.3236 | -35.3236
2025-05-02 10:00:00 | 6.84 | 47.3756 | 0 | 0 | 323.4562 | -40.5356 | -40.5356
2025-05-02 11:00:00 | 7.44 | 50.0735 | 0 | 0 | 323.4562 | -42.6335 | -42.6335
2025-05-02 12:00:00 | 10.92 | 50.0735 | 0 | 0 | 323.4562 | -39.1535 | -39.1535
2025-05-02 13:00:00 | 13.56 | 47.3756 | 0 | 0 | 323.4562 | -33.8156 | -33.8156
2025-05-02 14:00:00 | 12.72 | 42.1636 | 0 | 0 | 323.4562 | -29.4436 | -29.4436
2025-05-02 15:00:00 | 13.08 | 34.7926 | 0 | 0 | 323.4562 | -21.7126 | -21.7126
2025-05-02 16:00:00 | 12.96 | 25.7651 | 0 | 0 | 323.4562 | -12.8051 | -12.8051
2025-05-02 17:00:00 | 13.2 | 15.6963 | 0 | 0 | 323.4562 | -2.4963 | -2.4963
2025-05-02 18:00:00 | 13.8 | 5.2722 | 0 | 8.5278 | 314.9284 | 8.8818e-15 | 8.5278
2025-05-02 19:00:00 | 13.8 | 0 | 0 | 0 | 314.9284 | 13.8 | 13.8
2025-05-02 20:00:00 | 15 | 0 | 0 | 0 | 314.9284 | 15 | 15
2025-05-02 21:00:00 | 26.88 | 0 | 0 | 0 | 314.9284 | 26.88 | 26.88
2025-05-02 22:00:00 | 27.72 | 0 | 0 | 0 | 314.9284 | 27.72 | 27.72
2025-05-02 23:00:00 | 28.32 | 0 | 0 | 0 | 314.9284 | 28.32 | 28.32
2025-05-03 00:00:00 | 27.72 | 0 | 0 | 0 | 314.9284 | 27.72 | 27.72
2025-05-03 01:00:00 | 24.24 | 0 | 0 | 0 | 314.9284 | 24.24 | 24.24
2025-05-03 02:00:00 | 17.28 | 0 | 0 | 0 | 314.9284 | 17.28 | 17.28
2025-05-03 03:00:00 | 15.12 | 0 | 0 | 0 | 314.9284 | 15.12 | 15.12
2025-05-03 04:00:00 | 13.68 | 0 | 0 | 0 | 314.9284 | 13.68 | 13.68
2025-05-03 05:00:00 | 7.32 | 5.4849 | 0 | 0 | 314.9284 | 1.8351 | 1.8351
2025-05-03 06:00:00 | 8.04 | 15.8937 | 0 | 0 | 314.9284 | -7.8537 | -7.8537
2025-05-03 07:00:00 | 6.84 | 25.9479 | 0 | 0 | 314.9284 | -19.1079 | -19.1079
2025-05-03 08:00:00 | 6.96 | 34.9622 | 0 | 0 | 314.9284 | -28.0022 | -28.0022
2025-05-03 09:00:00 | 7.2 | 42.3224 | 0 | 0 | 314.9284 | -35.1224 | -35.1224
2025-05-03 10:00:00 | 6.36 | 47.5268 | 0 | 0 | 314.9284 | -41.1668 | -41.1668
2025-05-03 11:00:00 | 6.36 | 50.2208 | 0 | 0 | 314.9284 | -43.8608 | -43.8608
2025-05-03 12:00:00 | 6.96 | 50.2208 | 0 | 0 | 314.9284 | -43.2608 | -43.2608
2025-05-03 13:00:00 | 5.88 | 47.5268 | 0 | 0 | 314.9284 | -41.6468 | -41.6468
2025-05-03 14:00:00 | 5.88 | 42.3224 | 0 | 0 | 314.9284 | -36.4424 | -36.4424
2025-05-03 15:00:00 | 5.52 | 34.9622 | 0 | 0 | 314.9284 | -29.4422 | -29.4422
2025-05-03 16:00:00 | 5.76 | 25.9479 | 0 | 0 | 314.9284 | -20.1879 | -20.1879
2025-05-03 17:00:00 | 5.88 | 15.8937 | 0 | 0 | 314.9284 | -10.0137 | -10.0137
2025-05-03 18:00:00 | 5.64 | 5.4849 | 0 | 0 | 314.9284 | 0.15508 | 0.15508
2025-05-03 19:00:00 | 6 | 0 | 0 | 0 | 314.9284 | 6 | 6
2025-05-03 20:00:00 | 5.88 | 0 | 0 | 0 | 314.9284 | 5.88 | 5.88
2025-05-03 21:00:00 | 6.24 | 0 | 0 | 0 | 314.9284 | 6.24 | 6.24
2025-05-03 22:00:00 | 5.88 | 0 | 0 | 0 | 314.9284 | 5.88 | 5.88
2025-05-03 23:00:00 | 6.36 | 0 | 0 | 0 | 314.9284 | 6.36 | 6.36
2025-05-04 00:00:00 | 5.4 | 0 | 0 | 0 | 314.9284 | 5.4 | 5.4
2025-05-04 01:00:00 | 5.76 | 0 | 0 | 0 | 314.9284 | 5.76 | 5.76
2025-05-04 02:00:00 | 7.08 | 0 | 0 | 0 | 314.9284 | 7.08 | 7.08
2025-05-04 03:00:00 | 5.76 | 0 | 0 | 0 | 314.9284 | 5.76 | 5.76
2025-05-04 04:00:00 | 5.64 | 0 | 0 | 0 | 314.9284 | 5.64 | 5.64
2025-05-04 05:00:00 | 6.12 | 5.6943 | 0 | 0 | 314.9284 | 0.42572 | 0.42572
2025-05-04 06:00:00 | 6.36 | 16.0878 | 0 | 0 | 314.9284 | -9.7278 | -9.7278
2025-05-04 07:00:00 | 6.96 | 26.1272 | 0 | 0 | 314.9284 | -19.1672 | -19.1672
2025-05-04 08:00:00 | 5.52 | 35.1283 | 0 | 0 | 314.9284 | -29.6083 | -29.6083
2025-05-04 09:00:00 | 5.16 | 42.4776 | 0 | 0 | 314.9284 | -37.3176 | -37.3176
2025-05-04 10:00:00 | 6 | 47.6744 | 0 | 0 | 314.9284 | -41.6744 | -41.6744
2025-05-04 11:00:00 | 5.76 | 50.3644 | 0 | 0 | 314.9284 | -44.6044 | -44.6044
2025-05-04 12:00:00 | 5.52 | 50.3644 | 0 | 0 | 314.9284 | -44.8444 | -44.8444
2025-05-04 13:00:00 | 4.92 | 47.6744 | 0 | 0 | 314.9284 | -42.7544 | -42.7544
2025-05-04 14:00:00 | 4.8 | 42.4776 | 0 | 0 | 314.9284 | -37.6776 | -37.6776
2025-05-04 15:00:00 | 4.68 | 35.1283 | 0 | 0 | 314.9284 | -30.4483 | -30.4483
2025-05-04 16:00:00 | 5.04 | 26.1272 | 0 | 0 | 314.9284 | -21.0872 | -21.0872
2025-05-04 17:00:00 | 18.84 | 16.0878 | 0 | 0 | 314.9284 | 2.7522 | 2.7522
2025-05-04 18:00:00 | 18.96 | 5.6943 | 0 | 0 | 314.9284 | 13.2657 | 13.2657
2025-05-04 19:00:00 | 19.56 | 0 | 0 | 0 | 314.9284 | 19.56 | 19.56
2025-05-04 20:00:00 | 19.08 | 0 | 0 | 0 | 314.9284 | 19.08 | 19.08
2025-05-04 21:00:00 | 19.32 | 0 | 0 | 0 | 314.9284 | 19.32 | 19.32
2025-05-04 22:00:00 | 19.56 | 0 | 0 | 0 | 314.9284 | 19.56 | 19.56
2025-05-04 23:00:00 | 20.28 | 0 | 0 | 0 | 314.9284 | 20.28 | 20.28
2025-05-05 00:00:00 | 19.44 | 0 | 0 | 0 | 314.9284 | 19.44 | 19.44
2025-05-05 01:00:00 | 12.72 | 0 | 0 | 0 | 314.9284 | 12.72 | 12.72
2025-05-05 02:00:00 | 5.04 | 0 | 0 | 0 | 314.9284 | 5.04 | 5.04
2025-05-05 03:00:00 | 4.92 | 0 | 0 | 0 | 314.9284 | 4.92 | 4.92
2025-05-05 04:00:00 | 5.64 | 0 | 0 | 0 | 314.9284 | 5.64 | 5.64
2025-05-05 05:00:00 | 5.16 | 5.9002 | 0 | 0 | 314.9284 | -0.74021 | -0.74021
2025-05-05 06:00:00 | 5.16 | 16.2784 | 0 | 0 | 314.9284 | -11.1184 | -11.1184
2025-05-05 07:00:00 | 4.92 | 26.303 | 0 | 0 | 314.9284 | -21.383 | -21.383
2025-05-05 08:00:00 | 5.04 | 35.2908 | 0 | 0 | 314.9284 | -30.2508 | -30.2508
2025-05-05 09:00:00 | 5.16 | 42.6293 | 0 | 0 | 314.9284 | -37.4693 | -37.4693
2025-05-05 10:00:00 | 5.88 | 47.8184 | 0 | 0 | 314.9284 | -41.9384 | -41.9384
2025-05-05 11:00:00 | 5.64 | 50.5044 | 0 | 0 | 314.9284 | -44.8644 | -44.8644
2025-05-05 12:00:00 | 4.68 | 50.5044 | 0 | 0 | 314.9284 | -45.8244 | -45.8244
2025-05-05 13:00:00 | 5.28 | 47.8184 | 0 | 0 | 314.9284 | -42.5384 | -42.5384
2025-05-05 14:00:00 | 5.16 | 42.6293 | 0 | 0 | 314.9284 | -37.4693 | -37.4693
2025-05-05 15:00:00 | 5.4 | 35.2908 | 0 | 0 | 314.9284 | -29.8908 | -29.8908
2025-05-05 16:00:00 | 5.4 | 26.303 | 0 | 0 | 314.9284 | -20.903 | -20.903
2025-05-05 17:00:00 | 4.56 | 16.2784 | 0 | 0 | 314.9284 | -11.7184 | -11.7184
2025-05-05 18:00:00 | 5.04 | 5.9002 | 0 | 0 | 314.9284 | -0.86021 | -0.86021
2025-05-05 19:00:00 | 5.64 | 0 | 0 | 0 | 314.9284 | 5.64 | 5.64
2025-05-05 20:00:00 | 4.92 | 0 | 0 | 0 | 314.9284 | 4.92 | 4.92
2025-05-05 21:00:00 | 5.52 | 0 | 0 | 0 | 314.9284 | 5.52 | 5.52
2025-05-05 22:00:00 | 6.24 | 0 | 0 | 0 | 314.9284 | 6.24 | 6.24
2025-05-05 23:00:00 | 5.16 | 0 | 0 | 0 | 314.9284 | 5.16 | 5.16
2025-05-06 00:00:00 | 5.52 | 0 | 0 | 0 | 314.9284 | 5.52 | 5.52
2025-05-06 01:00:00 | 5.76 | 0 | 0 | 0 | 314.9284 | 5.76 | 5.76
2025-05-06 02:00:00 | 5.4 | 0 | 0 | 0 | 314.9284 | 5.4 | 5.4
2025-05-06 03:00:00 | 6.72 | 0 | 0 | 0 | 314.9284 | 6.72 | 6.72
2025-05-06 04:00:00 | 5.28 | 0 | 0 | 0 | 314.9284 | 5.28 | 5.28
2025-05-06 05:00:00 | 5.64 | 6.1027 | 0 | 0 | 314.9284 | -0.46267 | -0.46267
2025-05-06 06:00:00 | 5.88 | 16.4655 | 0 | 0 | 314.9284 | -10.5855 | -10.5855
2025-05-06 07:00:00 | 5.64 | 26.4753 | 0 | 0 | 314.9284 | -20.8353 | -20.8353
2025-05-06 08:00:00 | 5.52 | 35.4498 | 0 | 0 | 314.9284 | -29.9298 | -29.9298
2025-05-06 09:00:00 | 5.64 | 42.7774 | 0 | 0 | 314.9284 | -37.1374 | -37.1374
2025-05-06 10:00:00 | 4.08 | 47.9588 | 0 | 0 | 314.9284 | -43.8788 | -43.8788
2025-05-06 11:00:00 | 3.6 | 50.6409 | 0 | 0 | 314.9284 | -47.0409 | -47.0409
2025-05-06 12:00:00 | 3.48 | 50.6409 | 0 | 0 | 314.9284 | -47.1609 | -47.1609
2025-05-06 13:00:00 | 3.72 | 47.9588 | 0 | 0 | 314.9284 | -44.2388 | -44.2388
2025-05-06 14:00:00 | 4.2 | 42.7774 | 0 | 0 | 314.9284 | -38.5774 | -38.5774
2025-05-06 15:00:00 | 3.48 | 35.4498 | 0 | 0 | 314.9284 | -31.9698 | -31.9698
2025-05-06 16:00:00 | 3.6 | 26.4753 | 0 | 0 | 314.9284 | -22.8753 | -22.8753
2025-05-06 17:00:00 | 3.6 | 16.4655 | 0 | 0 | 314.9284 | -12.8655 | -12.8655
2025-05-06 18:00:00 | 3.48 | 6.1027 | 0 | 0 | 314.9284 | -2.6227 | -2.6227
2025-05-06 19:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-06 20:00:00 | 4.56 | 0 | 0 | 0 | 314.9284 | 4.56 | 4.56
2025-05-06 21:00:00 | 4.44 | 0 | 0 | 0 | 314.9284 | 4.44 | 4.44
2025-05-06 22:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-06 23:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-07 00:00:00 | 3.96 | 0 | 0 | 0 | 314.9284 | 3.96 | 3.96
2025-05-07 01:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-07 02:00:00 | 4.44 | 0 | 0 | 0 | 314.9284 | 4.44 | 4.44
2025-05-07 03:00:00 | 4.56 | 0 | 0 | 0 | 314.9284 | 4.56 | 4.56
2025-05-07 04:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-07 05:00:00 | 3.72 | 6.3016 | 0 | 0 | 314.9284 | -2.5816 | -2.5816
2025-05-07 06:00:00 | 3.84 | 16.6491 | 0 | 0 | 314.9284 | -12.8091 | -12.8091
2025-05-07 07:00:00 | 3.84 | 26.644 | 0 | 0 | 314.9284 | -22.804 | -22.804
2025-05-07 08:00:00 | 4.08 | 35.6052 | 0 | 0 | 314.9284 | -31.5252 | -31.5252
2025-05-07 09:00:00 | 4.08 | 42.922 | 0 | 0 | 314.9284 | -38.842 | -38.842
2025-05-07 10:00:00 | 4.44 | 48.0957 | 0 | 0 | 314.9284 | -43.6557 | -43.6557
2025-05-07 11:00:00 | 3.48 | 50.7738 | 0 | 0 | 314.9284 | -47.2938 | -47.2938
2025-05-07 12:00:00 | 3.48 | 50.7738 | 0 | 0 | 314.9284 | -47.2938 | -47.2938
2025-05-07 13:00:00 | 3.96 | 48.0957 | 0 | 0 | 314.9284 | -44.1357 | -44.1357
2025-05-07 14:00:00 | 3.24 | 42.922 | 0 | 0 | 314.9284 | -39.682 | -39.682
2025-05-07 15:00:00 | 3.12 | 35.6052 | 0 | 0 | 314.9284 | -32.4852 | -32.4852
2025-05-07 16:00:00 | 3.36 | 26.644 | 0 | 0 | 314.9284 | -23.284 | -23.284
2025-05-07 17:00:00 | 3 | 16.6491 | 0 | 0 | 314.9284 | -13.6491 | -13.6491
2025-05-07 18:00:00 | 3.12 | 6.3016 | 0 | 0 | 314.9284 | -3.1816 | -3.1816
2025-05-07 19:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-07 20:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-07 21:00:00 | 3.48 | 0 | 0 | 0 | 314.9284 | 3.48 | 3.48
2025-05-07 22:00:00 | 4.44 | 0 | 0 | 0 | 314.9284 | 4.44 | 4.44
2025-05-07 23:00:00 | 4.08 | 0 | 0 | 0 | 314.9284 | 4.08 | 4.08
2025-05-08 00:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-08 01:00:00 | 4.68 | 0 | 0 | 0 | 314.9284 | 4.68 | 4.68
2025-05-08 02:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-08 03:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-08 04:00:00 | 4.56 | 0 | 0 | 0 | 314.9284 | 4.56 | 4.56
2025-05-08 05:00:00 | 3.96 | 6.4969 | 0 | 0 | 314.9284 | -2.5369 | -2.5369
2025-05-08 06:00:00 | 3.84 | 16.8291 | 0 | 0 | 314.9284 | -12.9891 | -12.9891
2025-05-08 07:00:00 | 4.32 | 26.8092 | 0 | 0 | 314.9284 | -22.4892 | -22.4892
2025-05-08 08:00:00 | 4.2 | 35.7571 | 0 | 0 | 314.9284 | -31.5571 | -31.5571
2025-05-08 09:00:00 | 3.6 | 43.063 | 0 | 0 | 314.9284 | -39.463 | -39.463
2025-05-08 10:00:00 | 3.72 | 48.2291 | 0 | 0 | 314.9284 | -44.5091 | -44.5091
2025-05-08 11:00:00 | 3.12 | 50.9032 | 0 | 0 | 314.9284 | -47.7832 | -47.7832
2025-05-08 12:00:00 | 3 | 50.9032 | 0 | 0 | 314.9284 | -47.9032 | -47.9032
2025-05-08 13:00:00 | 3.72 | 48.2291 | 0 | 0 | 314.9284 | -44.5091 | -44.5091
2025-05-08 14:00:00 | 3.36 | 43.063 | 0 | 0 | 314.9284 | -39.703 | -39.703
2025-05-08 15:00:00 | 3 | 35.7571 | 0 | 0 | 314.9284 | -32.7571 | -32.7571
2025-05-08 16:00:00 | 2.88 | 26.8092 | 0 | 0 | 314.9284 | -23.9292 | -23.9292
2025-05-08 17:00:00 | 3.36 | 16.8291 | 0 | 0 | 314.9284 | -13.4691 | -13.4691
2025-05-08 18:00:00 | 3 | 6.4969 | 0 | 0 | 314.9284 | -3.4969 | -3.4969
2025-05-08 19:00:00 | 3.48 | 0 | 0 | 0 | 314.9284 | 3.48 | 3.48
2025-05-08 20:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-08 21:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-08 22:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-08 23:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-09 00:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-09 01:00:00 | 4.56 | 0 | 0 | 0 | 314.9284 | 4.56 | 4.56
2025-05-09 02:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-09 03:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-09 04:00:00 | 3.96 | 0 | 0 | 0 | 314.9284 | 3.96 | 3.96
2025-05-09 05:00:00 | 4.32 | 6.6886 | 0 | 0 | 314.9284 | -2.3686 | -2.3686
2025-05-09 06:00:00 | 3.84 | 17.0054 | 0 | 0 | 314.9284 | -13.1654 | -13.1654
2025-05-09 07:00:00 | 4.2 | 26.9707 | 0 | 0 | 314.9284 | -22.7707 | -22.7707
2025-05-09 08:00:00 | 3.12 | 35.9054 | 0 | 0 | 314.9284 | -32.7854 | -32.7854
2025-05-09 09:00:00 | 2.88 | 43.2005 | 0 | 0 | 314.9284 | -40.3205 | -40.3205
2025-05-09 10:00:00 | 3 | 48.3589 | 0 | 0 | 314.9284 | -45.3589 | -45.3589
2025-05-09 11:00:00 | 3.36 | 51.0291 | 0 | 0 | 314.9284 | -47.6691 | -47.6691
2025-05-09 12:00:00 | 2.64 | 51.0291 | 0 | 0 | 314.9284 | -48.3891 | -48.3891
2025-05-09 13:00:00 | 3.6 | 48.3589 | 0 | 0 | 314.9284 | -44.7589 | -44.7589
2025-05-09 14:00:00 | 2.88 | 43.2005 | 0 | 0 | 314.9284 | -40.3205 | -40.3205
2025-05-09 15:00:00 | 2.76 | 35.9054 | 0 | 0 | 314.9284 | -33.1454 | -33.1454
2025-05-09 16:00:00 | 3.36 | 26.9707 | 0 | 0 | 314.9284 | -23.6107 | -23.6107
2025-05-09 17:00:00 | 3 | 17.0054 | 0 | 0 | 314.9284 | -14.0054 | -14.0054
2025-05-09 18:00:00 | 2.88 | 6.6886 | 0 | 0 | 314.9284 | -3.8086 | -3.8086
2025-05-09 19:00:00 | 3.48 | 0 | 0 | 0 | 314.9284 | 3.48 | 3.48
2025-05-09 20:00:00 | 3.12 | 0 | 0 | 0 | 314.9284 | 3.12 | 3.12
2025-05-09 21:00:00 | 3.6 | 0 | 0 | 0 | 314.9284 | 3.6 | 3.6
2025-05-09 22:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-09 23:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-10 00:00:00 | 3.48 | 0 | 0 | 0 | 314.9284 | 3.48 | 3.48
2025-05-10 01:00:00 | 4.32 | 0 | 0 | 0 | 314.9284 | 4.32 | 4.32
2025-05-10 02:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-10 03:00:00 | 4.2 | 0 | 0 | 0 | 314.9284 | 4.2 | 4.2
2025-05-10 04:00:00 | 4.08 | 0 | 0 | 0 | 314.9284 | 4.08 | 4.08
2025-05-10 05:00:00 | 3.84 | 6.8766 | 0 | 0 | 314.9284 | -3.0366 | -3.0366
2025-05-10 06:00:00 | 3.96 | 17.1782 | 0 | 0 | 314.9284 | -13.2182 | -13.2182
2025-05-10 07:00:00 | 3.96 | 27.1287 | 0 | 0 | 314.9284 | -23.1687 | -23.1687
2025-05-10 08:00:00 | 4.08 | 36.0501 | 0 | 0 | 314.9284 | -31.9701 | -31.9701
2025-05-10 09:00:00 | 3.48 | 43.3345 | 0 | 0 | 314.9284 | -39.8545 | -39.8545
2025-05-10 10:00:00 | 3.84 | 48.4852 | 0 | 0 | 314.9284 | -44.6452 | -44.6452
2025-05-10 11:00:00 | 3.48 | 51.1515 | 0 | 0 | 314.9284 | -47.6715 | -47.6715
2025-05-10 12:00:00 | 3.48 | 51.1515 | 0 | 0 | 314.9284 | -47.6715 | -47.6715
2025-05-10 13:00:00 | 3.36 | 48.4852 | 0 | 0 | 314.9284 | -45.1252 | -45.1252
2025-05-10 14:00:00 | 3 | 43.3345 | 0 | 0 | 314.9284 | -40.3345 | -40.3345
2025-05-10 15:00:00 | 3 | 36.0501 | 0 | 0 | 314.9284 | -33.0501 | -33.0501
2025-05-10 16:00:00 | 2.88 | 27.1287 | 0 | 0 | 314.9284 | -24.2487 | -24.2487
2025-05-10 17:00:00 | 3 | 17.1782 | 0 | 0 | 314.9284 | -14.1782 | -14.1782
2025-05-10 18:00:00 | 4.08 | 6.8766 | 0 | 0 | 314.9284 | -2.7966 | -2.7966
2025-05-10 19:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-10 20:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-10 21:00:00 | 3.12 | 0 | 0 | 0 | 314.9284 | 3.12 | 3.12
2025-05-10 22:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-10 23:00:00 | 4.56 | 0 | 0 | 0 | 314.9284 | 4.56 | 4.56
2025-05-11 00:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-11 01:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-11 02:00:00 | 3.6 | 0 | 0 | 0 | 314.9284 | 3.6 | 3.6
2025-05-11 03:00:00 | 3.96 | 0 | 0 | 0 | 314.9284 | 3.96 | 3.96
2025-05-11 04:00:00 | 4.44 | 0 | 0 | 0 | 314.9284 | 4.44 | 4.44
2025-05-11 05:00:00 | 4.32 | 7.0608 | 0 | 0 | 314.9284 | -2.7408 | -2.7408
2025-05-11 06:00:00 | 3.84 | 17.3472 | 0 | 0 | 314.9284 | -13.5072 | -13.5072
2025-05-11 07:00:00 | 3.48 | 27.2831 | 0 | 0 | 314.9284 | -23.8031 | -23.8031
2025-05-11 08:00:00 | 3.6 | 36.1914 | 0 | 0 | 314.9284 | -32.5914 | -32.5914
2025-05-11 09:00:00 | 3.84 | 43.4649 | 0 | 0 | 314.9284 | -39.6249 | -39.6249
2025-05-11 10:00:00 | 5.4 | 48.6081 | 0 | 0 | 314.9284 | -43.2081 | -43.2081
2025-05-11 11:00:00 | 3.48 | 51.2704 | 0 | 0 | 314.9284 | -47.7904 | -47.7904
2025-05-11 12:00:00 | 3.12 | 51.2704 | 0 | 0 | 314.9284 | -48.1504 | -48.1504
2025-05-11 13:00:00 | 3 | 48.6081 | 0 | 0 | 314.9284 | -45.6081 | -45.6081
2025-05-11 14:00:00 | 3 | 43.4649 | 0 | 0 | 314.9284 | -40.4649 | -40.4649
2025-05-11 15:00:00 | 3.36 | 36.1914 | 0 | 0 | 314.9284 | -32.8314 | -32.8314
2025-05-11 16:00:00 | 3.6 | 27.2831 | 0 | 0 | 314.9284 | -23.6831 | -23.6831
2025-05-11 17:00:00 | 2.76 | 17.3472 | 0 | 0 | 314.9284 | -14.5872 | -14.5872
2025-05-11 18:00:00 | 2.76 | 7.0608 | 0 | 0 | 314.9284 | -4.3008 | -4.3008
2025-05-11 19:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-11 20:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-11 21:00:00 | 4.56 | 0 | 0 | 0 | 314.9284 | 4.56 | 4.56
2025-05-11 22:00:00 | 3.96 | 0 | 0 | 0 | 314.9284 | 3.96 | 3.96
2025-05-11 23:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-12 00:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-12 01:00:00 | 4.08 | 0 | 0 | 0 | 314.9284 | 4.08 | 4.08
2025-05-12 02:00:00 | 4.92 | 0 | 0 | 0 | 314.9284 | 4.92 | 4.92
2025-05-12 03:00:00 | 4.08 | 0 | 0 | 0 | 314.9284 | 4.08 | 4.08
2025-05-12 04:00:00 | 4.2 | 0 | 0 | 0 | 314.9284 | 4.2 | 4.2
2025-05-12 05:00:00 | 3.84 | 7.2413 | 0 | 0 | 314.9284 | -3.4013 | -3.4013
2025-05-12 06:00:00 | 3.84 | 17.5125 | 0 | 0 | 314.9284 | -13.6725 | -13.6725
2025-05-12 07:00:00 | 3.84 | 27.4338 | 0 | 0 | 314.9284 | -23.5938 | -23.5938
2025-05-12 08:00:00 | 4.2 | 36.329 | 0 | 0 | 314.9284 | -32.129 | -32.129
2025-05-12 09:00:00 | 3.24 | 43.5919 | 0 | 0 | 314.9284 | -40.3519 | -40.3519
2025-05-12 10:00:00 | 3.84 | 48.7275 | 0 | 0 | 314.9284 | -44.8875 | -44.8875
2025-05-12 11:00:00 | 3.24 | 51.3859 | 0 | 0 | 314.9284 | -48.1459 | -48.1459
2025-05-12 12:00:00 | 3.24 | 51.3859 | 0 | 0 | 314.9284 | -48.1459 | -48.1459
2025-05-12 13:00:00 | 3.84 | 48.7275 | 0 | 0 | 314.9284 | -44.8875 | -44.8875
2025-05-12 14:00:00 | 3.12 | 43.5919 | 0 | 0 | 314.9284 | -40.4719 | -40.4719
2025-05-12 15:00:00 | 2.88 | 36.329 | 0 | 0 | 314.9284 | -33.449 | -33.449
2025-05-12 16:00:00 | 2.88 | 27.4338 | 0 | 0 | 314.9284 | -24.5538 | -24.5538
2025-05-12 17:00:00 | 3 | 17.5125 | 0 | 0 | 314.9284 | -14.5125 | -14.5125
2025-05-12 18:00:00 | 3.84 | 7.2413 | 0 | 0 | 314.9284 | -3.4013 | -3.4013
2025-05-12 19:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-12 20:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-12 21:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-12 22:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-12 23:00:00 | 4.92 | 0 | 0 | 0 | 314.9284 | 4.92 | 4.92
2025-05-13 00:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-13 01:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-13 02:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-13 03:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-13 04:00:00 | 4.08 | 0 | 0 | 0 | 314.9284 | 4.08 | 4.08
2025-05-13 05:00:00 | 4.2 | 7.4179 | 0 | 0 | 314.9284 | -3.2179 | -3.2179
2025-05-13 06:00:00 | 3.12 | 17.6741 | 0 | 0 | 314.9284 | -14.5541 | -14.5541
2025-05-13 07:00:00 | 2.88 | 27.5809 | 0 | 0 | 314.9284 | -24.7009 | -24.7009
2025-05-13 08:00:00 | 3.12 | 36.4631 | 0 | 0 | 314.9284 | -33.3431 | -33.3431
2025-05-13 09:00:00 | 3.36 | 43.7154 | 0 | 0 | 314.9284 | -40.3554 | -40.3554
2025-05-13 10:00:00 | 4.56 | 48.8435 | 0 | 0 | 314.9284 | -44.2835 | -44.2835
2025-05-13 11:00:00 | 3.48 | 51.498 | 0 | 0 | 314.9284 | -48.018 | -48.018
2025-05-13 12:00:00 | 3.36 | 51.498 | 0 | 0 | 314.9284 | -48.138 | -48.138
2025-05-13 13:00:00 | 3.12 | 48.8435 | 0 | 0 | 314.9284 | -45.7235 | -45.7235
2025-05-13 14:00:00 | 2.88 | 43.7154 | 0 | 0 | 314.9284 | -40.8354 | -40.8354
2025-05-13 15:00:00 | 4.2 | 36.4631 | 0 | 0 | 314.9284 | -32.2631 | -32.2631
2025-05-13 16:00:00 | 3.24 | 27.5809 | 0 | 0 | 314.9284 | -24.3409 | -24.3409
2025-05-13 17:00:00 | 3.36 | 17.6741 | 0 | 0 | 314.9284 | -14.3141 | -14.3141
2025-05-13 18:00:00 | 3.24 | 7.4179 | 0 | 0 | 314.9284 | -4.1779 | -4.1779
2025-05-13 19:00:00 | 3.6 | 0 | 0 | 0 | 314.9284 | 3.6 | 3.6
2025-05-13 20:00:00 | 5.16 | 0 | 0 | 0 | 314.9284 | 5.16 | 5.16
2025-05-13 21:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-13 22:00:00 | 3.96 | 0 | 0 | 0 | 314.9284 | 3.96 | 3.96
2025-05-13 23:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-14 00:00:00 | 3.96 | 0 | 0 | 0 | 314.9284 | 3.96 | 3.96
2025-05-14 01:00:00 | 4.2 | 0 | 0 | 0 | 314.9284 | 4.2 | 4.2
2025-05-14 02:00:00 | 4.44 | 0 | 0 | 0 | 314.9284 | 4.44 | 4.44
2025-05-14 03:00:00 | 4.08 | 0 | 0 | 0 | 314.9284 | 4.08 | 4.08
2025-05-14 04:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-14 05:00:00 | 4.08 | 7.5905 | 0 | 0 | 314.9284 | -3.5105 | -3.5105
2025-05-14 06:00:00 | 4.44 | 17.8319 | 0 | 0 | 314.9284 | -13.3919 | -13.3919
2025-05-14 07:00:00 | 4.08 | 27.7244 | 0 | 0 | 314.9284 | -23.6444 | -23.6444
2025-05-14 08:00:00 | 4.08 | 36.5937 | 0 | 0 | 314.9284 | -32.5137 | -32.5137
2025-05-14 09:00:00 | 3.6 | 43.8354 | 0 | 0 | 314.9284 | -40.2354 | -40.2354
2025-05-14 10:00:00 | 3.72 | 48.9561 | 0 | 0 | 314.9284 | -45.2361 | -45.2361
2025-05-14 11:00:00 | 4.08 | 51.6068 | 0 | 0 | 314.9284 | -47.5268 | -47.5268
2025-05-14 12:00:00 | 3.84 | 51.6068 | 0 | 0 | 314.9284 | -47.7668 | -47.7668
2025-05-14 13:00:00 | 4.2 | 48.9561 | 0 | 0 | 314.9284 | -44.7561 | -44.7561
2025-05-14 14:00:00 | 3 | 43.8354 | 0 | 0 | 314.9284 | -40.8354 | -40.8354
2025-05-14 15:00:00 | 3.24 | 36.5937 | 0 | 0 | 314.9284 | -33.3537 | -33.3537
2025-05-14 16:00:00 | 3.48 | 27.7244 | 0 | 0 | 314.9284 | -24.2444 | -24.2444
2025-05-14 17:00:00 | 3.12 | 17.8319 | 0 | 0 | 314.9284 | -14.7119 | -14.7119
2025-05-14 18:00:00 | 3.48 | 7.5905 | 0 | 0 | 314.9284 | -4.1105 | -4.1105
2025-05-14 19:00:00 | 3 | 0 | 0 | 0 | 314.9284 | 3 | 3
2025-05-14 20:00:00 | 4.08 | 0 | 0 | 0 | 314.9284 | 4.08 | 4.08
2025-05-14 21:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-14 22:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-14 23:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-15 00:00:00 | 3.96 | 0 | 0 | 0 | 314.9284 | 3.96 | 3.96
2025-05-15 01:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-15 02:00:00 | 3.48 | 0 | 0 | 0 | 314.9284 | 3.48 | 3.48
2025-05-15 03:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-15 04:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-15 05:00:00 | 3.36 | 7.7593 | 0 | 0 | 314.9284 | -4.3993 | -4.3993
2025-05-15 06:00:00 | 4.32 | 17.9859 | 0 | 0 | 314.9284 | -13.6659 | -13.6659
2025-05-15 07:00:00 | 3 | 27.8641 | 0 | 0 | 314.9284 | -24.8641 | -24.8641
2025-05-15 08:00:00 | 3.12 | 36.7207 | 0 | 0 | 314.9284 | -33.6007 | -33.6007
2025-05-15 09:00:00 | 3 | 43.952 | 0 | 0 | 314.9284 | -40.952 | -40.952
2025-05-15 10:00:00 | 3.12 | 49.0653 | 0 | 0 | 314.9284 | -45.9453 | -45.9453
2025-05-15 11:00:00 | 3.84 | 51.7122 | 0 | 0 | 314.9284 | -47.8722 | -47.8722
2025-05-15 12:00:00 | 2.88 | 51.7122 | 0 | 0 | 314.9284 | -48.8322 | -48.8322
2025-05-15 13:00:00 | 2.76 | 49.0653 | 0 | 0 | 314.9284 | -46.3053 | -46.3053
2025-05-15 14:00:00 | 3.12 | 43.952 | 0 | 0 | 314.9284 | -40.832 | -40.832
2025-05-15 15:00:00 | 2.76 | 36.7207 | 0 | 0 | 314.9284 | -33.9607 | -33.9607
2025-05-15 16:00:00 | 3.72 | 27.8641 | 0 | 0 | 314.9284 | -24.1441 | -24.1441
2025-05-15 17:00:00 | 3 | 17.9859 | 0 | 0 | 314.9284 | -14.9859 | -14.9859
2025-05-15 18:00:00 | 2.64 | 7.7593 | 0 | 0 | 314.9284 | -5.1193 | -5.1193
2025-05-15 19:00:00 | 2.76 | 0 | 0 | 0 | 314.9284 | 2.76 | 2.76
2025-05-15 20:00:00 | 3.12 | 0 | 0 | 0 | 314.9284 | 3.12 | 3.12
2025-05-15 21:00:00 | 3.48 | 0 | 0 | 0 | 314.9284 | 3.48 | 3.48
2025-05-15 22:00:00 | 3.72 | 0 | 0 | 0 | 314.9284 | 3.72 | 3.72
2025-05-15 23:00:00 | 3.12 | 0 | 0 | 0 | 314.9284 | 3.12 | 3.12
2025-05-16 00:00:00 | 3.12 | 0 | 0 | 0 | 314.9284 | 3.12 | 3.12
2025-05-16 01:00:00 | 3.12 | 0 | 0 | 0 | 314.9284 | 3.12 | 3.12
2025-05-16 02:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-16 03:00:00 | 3.84 | 0 | 0 | 0 | 314.9284 | 3.84 | 3.84
2025-05-16 04:00:00 | 4.32 | 0 | 0 | 0 | 314.9284 | 4.32 | 4.32
2025-05-16 05:00:00 | 4.32 | 7.9241 | 0 | 0 | 314.9284 | -3.6041 | -3.6041
2025-05-16 06:00:00 | 3.84 | 18.1361 | 0 | 0 | 314.9284 | -14.2961 | -14.2961
2025-05-16 07:00:00 | 4.08 | 28.0002 | 0 | 0 | 314.9284 | -23.9202 | -23.9202
2025-05-16 08:00:00 | 3.24 | 36.8441 | 0 | 0 | 314.9284 | -33.6041 | -33.6041
2025-05-16 09:00:00 | 3.24 | 44.0652 | 0 | 0 | 314.9284 | -40.8252 | -40.8252
2025-05-16 10:00:00 | 2.76 | 49.1712 | 0 | 0 | 314.9284 | -46.4112 | -46.4112
2025-05-16 11:00:00 | 2.88 | 51.8143 | 0 | 0 | 314.9284 | -48.9343 | -48.9343
2025-05-16 12:00:00 | 2.88 | 51.8143 | 0 | 0 | 314.9284 | -48.9343 | -48.9343
2025-05-16 13:00:00 | 2.88 | 49.1712 | 0 | 0 | 314.9284 | -46.2912 | -46.2912
2025-05-16 14:00:00 | 3.36 | 44.0652 | 0 | 0 | 314.9284 | -40.7052 | -40.7052
2025-05-16 15:00:00 | 2.64 | 36.8441 | 0 | 0 | 314.9284 | -34.2041 | -34.2041
2025-05-16 16:00:00 | 2.64 | 28.0002 | 0 | 0 | 314.9284 | -25.3602 | -25.3602
2025-05-16 17:00:00 | 3.36 | 18.1361 | 0 | 0 | 314.9284 | -14.7761 | -14.7761
2025-05-16 18:00:00 | 2.64 | 7.9241 | 0 | 0 | 314.9284 | -5.2841 | -5.2841
2025-05-16 19:00:00 | 2.76 | 0 | 0 | 0 | 314.9284 | 2.76 | 2.76
2025-05-16 20:00:00 | 3.48 | 0 | 0 | 0 | 314.9284 | 3.48 | 3.48
2025-05-16 21:00:00 | 2.88 | 0 | 0 | 0 | 314.9284 | 2.88 | 2.88
2025-05-16 22:00:00 | 3.48 | 0 | 0 | 0 | 314.9284 | 3.48 | 3.48
2025-05-16 23:00:00 | 3.12 | 0 | 0 | 0 | 314.9284 | 3.12 | 3.12
2025-05-17 00:00:00 | 2.76 | 0 | 0 | 0 | 314.9284 | 2.76 | 2.76
2025-05-17 01:00:00 | 3.48 | 0 | 0 | 0 | 314.9284 | 3.48 | 3.48
2025-05-17 02:00:00 | 3.12 | 0 | 0 | 0 | 314.9284 | 3.12 | 3.12
2025-05-17 03:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-17 04:00:00 | 3.36 | 0 | 0 | 0 | 314.9284 | 3.36 | 3.36
2025-05-17 05:00:00 | 2.76 | 8.0848 | 0 | 0 | 314.9284 | -5.3248 | -5.3248
2025-05-17 06:00:00 | 2.88 | 18.2825 | 0 | 0 | 314.9284 | -15.4025 | -15.4025
2025-05-17 07:00:00 | 3.36 | 28.1326 | 0 | 0 | 314.9284 | -24.7726 | -24.7726
2025-05-17 08:00:00 | 2.64 | 36.9641 | 0 | 0 | 314.9284 | -34.3241 | -34.3241
2025-05-17 09:00:00 | 3.36 | 44.1749 | 0 | 0 | 314.9284 | -40.8149 | -40.8149
2025-05-17 10:00:00 | 2.52 | 49.2737 | 0 | 0 | 314.9284 | -46.7537 | -46.7537
2025-05-17 11:00:00 | 2.76 | 51.9131 | 0 | 0 | 314.9284 | -49.1531 | -49.1531
2025-05-17 12:00:00 | 2.52 | 51.9131 | 0 | 0 | 314.9284 | -49.3931 | -49.3931
2025-05-17 13:00:00 | 3.24 | 49.2737 | 0 | 0 | 314.9284 | -46.0337 | -46.0337
2025-05-17 14:00:00 | 2.52 | 44.1749 | 0 | 0 | 314.9284 | -41.6549 | -41.6549
2025-05-17 15:00:00 | 2.76 | 36.9641 | 0 | 0 | 314.9284 | -34.2041 | -34.2041
2025-05-17 16:00:00 | 2.76 | 28.1326 | 0 | 0 | 314.9284 | -25.3726 | -25.3726
2025-05-17 17:00:00 | 2.4 | 18.2825 | 0 | 0 | 314.9284 | -15.8825 | -15.8825
2025-05-17 18:00:00 | 2.52 | 8.0848 | 0 | 0 | 314.9284 | -5.5648 | -5.5648
2025-05-17 19:00:00 | 3.24 | 0 | 0 | 0 | 314.9284 | 3.24 | 3.24
2025-05-17 20:00:00 | 2.88 | 0 | 0 | 0 | 314.9284 | 2.88 | 2.88
2025-05-17 21:00:00 | 2.76 | 0 | 0 | 0 | 314.9284 | 2.76 | 2.76
2025-05-17 22:00:00 | 2.76 | 0 | 0 | 0 | 314.9284 | 2.76 | 2.76
2025-05-17 23:00:00 | 2.76 | 0 | 0 | 0 | 314.9284 | 2.76 | 2.76
2025-05-18 00:00:00 | 5.4 | 0 | 0 | 0 | 314.9284 | 5.4 | 5.4
2025-05-18 01:00:00 | 5.58 | 0 | 0 | 0 | 314.9284 | 5.58 | 5.58
2025-05-18 02:00:00 | 5.28 | 0 | 0 | 0 | 314.9284 | 5.28 | 5.28
2025-05-18 03:00:00 | 5.58 | 0 | 0 | 0 | 314.9284 | 5.58 | 5.58
2025-05-18 04:00:00 | 5.82 | 0 | 0 | 0 | 314.9284 | 5.82 | 5.82
2025-05-18 05:00:00 | 5.4 | 8.2415 | 0 | 0 | 314.9284 | -2.8415 | -2.8415
2025-05-18 06:00:00 | 5.16 | 18.4249 | 0 | 0 | 314.9284 | -13.2649 | -13.2649
2025-05-18 07:00:00 | 5.58 | 28.2614 | 0 | 0 | 314.9284 | -22.6814 | -22.6814
2025-05-18 08:00:00 | 5.28 | 37.0805 | 0 | 0 | 314.9284 | -31.8005 | -31.8005
2025-05-18 09:00:00 | 5.34 | 44.2813 | 0 | 0 | 314.9284 | -38.9413 | -38.9413
2025-05-18 10:00:00 | 4.98 | 49.373 | 0 | 0 | 314.9284 | -44.393 | -44.393
2025-05-18 11:00:00 | 7.5 | 52.0086 | 0 | 0 | 314.9284 | -44.5086 | -44.5086
2025-05-18 12:00:00 | 10.68 | 52.0086 | 0 | 0 | 314.9284 | -41.3286 | -41.3286
2025-05-18 13:00:00 | 6.48 | 49.373 | 0 | 0 | 314.9284 | -42.893 | -42.893
2025-05-18 14:00:00 | 5.1 | 44.2813 | 0 | 0 | 314.9284 | -39.1813 | -39.1813
2025-05-18 15:00:00 | 5.22 | 37.0805 | 0 | 0 | 314.9284 | -31.8605 | -31.8605
2025-05-18 16:00:00 | 4.86 | 28.2614 | 0 | 0 | 314.9284 | -23.4014 | -23.4014
2025-05-18 17:00:00 | 5.46 | 18.4249 | 0 | 0 | 314.9284 | -12.9649 | -12.9649
2025-05-18 18:00:00 | 5.64 | 8.2415 | 0 | 0 | 314.9284 | -2.6015 | -2.6015
2025-05-18 19:00:00 | 5.94 | 0 | 0 | 0 | 314.9284 | 5.94 | 5.94
2025-05-18 20:00:00 | 6.24 | 0 | 0 | 0 | 314.9284 | 6.24 | 6.24
2025-05-18 21:00:00 | 6.24 | 0 | 0 | 0 | 314.9284 | 6.24 | 6.24
2025-05-18 22:00:00 | 6.18 | 0 | 0 | 0 | 314.9284 | 6.18 | 6.18
2025-05-18 23:00:00 | 6.6 | 0 | 0 | 0 | 314.9284 | 6.6 | 6.6
2025-05-19 00:00:00 | 6.42 | 0 | 0 | 0 | 314.9284 | 6.42 | 6.42
2025-05-19 01:00:00 | 6.66 | 0 | 0 | 0 | 314.9284 | 6.66 | 6.66
2025-05-19 02:00:00 | 6.12 | 0 | 0 | 0 | 314.9284 | 6.12 | 6.12
2025-05-19 03:00:00 | 6.78 | 0 | 0 | 0 | 314.9284 | 6.78 | 6.78
2025-05-19 04:00:00 | 6.72 | 0 | 0 | 0 | 314.9284 | 6.72 | 6.72
2025-05-19 05:00:00 | 6.84 | 8.3941 | 0 | 0 | 314.9284 | -1.5541 | -1.5541
2025-05-19 06:00:00 | 6.42 | 18.5635 | 0 | 0 | 314.9284 | -12.1435 | -12.1435
2025-05-19 07:00:00 | 6.42 | 28.3864 | 0 | 0 | 314.9284 | -21.9664 | -21.9664
2025-05-19 08:00:00 | 6.24 | 37.1934 | 0 | 0 | 314.9284 | -30.9534 | -30.9534
2025-05-19 09:00:00 | 5.7 | 44.3842 | 0 | 0 | 314.9284 | -38.6842 | -38.6842
2025-05-19 10:00:00 | 6 | 49.4689 | 0 | 0 | 314.9284 | -43.4689 | -43.4689
2025-05-19 11:00:00 | 5.7 | 52.101 | 0 | 0 | 314.9284 | -46.401 | -46.401
2025-05-19 12:00:00 | 10.62 | 52.101 | 0 | 0 | 314.9284 | -41.481 | -41.481
2025-05-19 13:00:00 | 11.64 | 49.4689 | 0 | 0 | 314.9284 | -37.8289 | -37.8289
2025-05-19 14:00:00 | 12.36 | 44.3842 | 0 | 0 | 314.9284 | -32.0242 | -32.0242
2025-05-19 15:00:00 | 11.4 | 37.1934 | 0 | 0 | 314.9284 | -25.7934 | -25.7934
2025-05-19 16:00:00 | 14.88 | 28.3864 | 0 | 0 | 314.9284 | -13.5064 | -13.5064
2025-05-19 17:00:00 | 25.44 | 18.5635 | 0 | 6.8765 | 308.0519 | 1.6875e-14 | 6.8765
2025-05-19 18:00:00 | 25.8 | 8.3941 | 0 | 17.4059 | 290.6459 | -3.908e-14 | 17.4059
2025-05-19 19:00:00 | 26.16 | 0 | 0 | 0 | 290.6459 | 26.16 | 26.16
2025-05-19 20:00:00 | 24.9 | 0 | 0 | 0 | 290.6459 | 24.9 | 24.9
2025-05-19 21:00:00 | 13.14 | 0 | 0 | 0 | 290.6459 | 13.14 | 13.14
2025-05-19 22:00:00 | 13.74 | 0 | 0 | 0 | 290.6459 | 13.74 | 13.74
2025-05-19 23:00:00 | 13.8 | 0 | 0 | 0 | 290.6459 | 13.8 | 13.8
2025-05-20 00:00:00 | 14.52 | 0 | 0 | 0 | 290.6459 | 14.52 | 14.52
2025-05-20 01:00:00 | 14.22 | 0 | 0 | 0 | 290.6459 | 14.22 | 14.22
2025-05-20 02:00:00 | 14.1 | 0 | 0 | 0 | 290.6459 | 14.1 | 14.1
2025-05-20 03:00:00 | 14.64 | 0 | 0 | 0 | 290.6459 | 14.64 | 14.64
2025-05-20 04:00:00 | 14.16 | 0 | 0 | 0 | 290.6459 | 14.16 | 14.16
2025-05-20 05:00:00 | 14.28 | 8.5425 | 0 | 0 | 290.6459 | 5.7375 | 5.7375
2025-05-20 06:00:00 | 15.12 | 18.6981 | 0 | 0 | 290.6459 | -3.5781 | -3.5781
2025-05-20 07:00:00 | 15.6 | 28.5077 | 0 | 0 | 290.6459 | -12.9077 | -12.9077
2025-05-20 08:00:00 | 16.08 | 37.3027 | 0 | 0 | 290.6459 | -21.2227 | -21.2227
2025-05-20 09:00:00 | 14.82 | 44.4839 | 0 | 0 | 290.6459 | -29.6639 | -29.6639
2025-05-20 10:00:00 | 9.78 | 49.5617 | 0 | 0 | 290.6459 | -39.7817 | -39.7817
2025-05-20 11:00:00 | 7.62 | 52.1901 | 0 | 0 | 290.6459 | -44.5701 | -44.5701
2025-05-20 12:00:00 | 7.32 | 52.1901 | 0 | 0 | 290.6459 | -44.8701 | -44.8701
2025-05-20 13:00:00 | 8.04 | 49.5617 | 0 | 0 | 290.6459 | -41.5217 | -41.5217
2025-05-20 14:00:00 | 15.48 | 44.4839 | 0 | 0 | 290.6459 | -29.0039 | -29.0039
2025-05-20 15:00:00 | 6.9 | 37.3027 | 0 | 0 | 290.6459 | -30.4027 | -30.4027
2025-05-20 16:00:00 | 4.8 | 28.5077 | 0 | 0 | 290.6459 | -23.7077 | -23.7077
2025-05-20 17:00:00 | 4.68 | 18.6981 | 0 | 0 | 290.6459 | -14.0181 | -14.0181
2025-05-20 18:00:00 | 5.22 | 8.5425 | 0 | 0 | 290.6459 | -3.3225 | -3.3225
2025-05-20 19:00:00 | 4.86 | 0 | 0 | 0 | 290.6459 | 4.86 | 4.86
2025-05-20 20:00:00 | 5.82 | 0 | 0 | 0 | 290.6459 | 5.82 | 5.82
2025-05-20 21:00:00 | 5.88 | 0 | 0 | 0 | 290.6459 | 5.88 | 5.88
2025-05-20 22:00:00 | 6.3 | 0 | 0 | 0 | 290.6459 | 6.3 | 6.3
2025-05-20 23:00:00 | 6.3 | 0 | 0 | 0 | 290.6459 | 6.3 | 6.3
2025-05-21 00:00:00 | 6.48 | 0 | 0 | 0 | 290.6459 | 6.48 | 6.48
2025-05-21 01:00:00 | 6.42 | 0 | 0 | 0 | 290.6459 | 6.42 | 6.42
2025-05-21 02:00:00 | 7.08 | 0 | 0 | 0 | 290.6459 | 7.08 | 7.08
2025-05-21 03:00:00 | 8.94 | 0 | 0 | 0 | 290.6459 | 8.94 | 8.94
2025-05-21 04:00:00 | 7.86 | 0 | 0 | 0 | 290.6459 | 7.86 | 7.86
2025-05-21 05:00:00 | 6 | 8.6867 | 0 | 0 | 290.6459 | -2.6867 | -2.6867
2025-05-21 06:00:00 | 8.28 | 18.8288 | 0 | 0 | 290.6459 | -10.5488 | -10.5488
2025-05-21 07:00:00 | 7.92 | 28.6253 | 0 | 0 | 290.6459 | -20.7053 | -20.7053
2025-05-21 08:00:00 | 8.46 | 37.4086 | 0 | 0 | 290.6459 | -28.9486 | -28.9486
2025-05-21 09:00:00 | 8.16 | 44.5801 | 0 | 0 | 290.6459 | -36.4201 | -36.4201
2025-05-21 10:00:00 | 8.58 | 49.6512 | 0 | 0 | 290.6459 | -41.0712 | -41.0712
2025-05-21 11:00:00 | 8.34 | 52.2761 | 0 | 0 | 290.6459 | -43.9361 | -43.9361
2025-05-21 12:00:00 | 8.4 | 52.2761 | 0 | 0 | 290.6459 | -43.8761 | -43.8761
2025-05-21 13:00:00 | 7.62 | 49.6512 | 0 | 0 | 290.6459 | -42.0312 | -42.0312
2025-05-21 14:00:00 | 7.56 | 44.5801 | 0 | 0 | 290.6459 | -37.0201 | -37.0201
2025-05-21 15:00:00 | 7.2 | 37.4086 | 0 | 0 | 290.6459 | -30.2086 | -30.2086
2025-05-21 16:00:00 | 6.42 | 28.6253 | 0 | 0 | 290.6459 | -22.2053 | -22.2053
2025-05-21 17:00:00 | 6.06 | 18.8288 | 0 | 0 | 290.6459 | -12.7688 | -12.7688
2025-05-21 18:00:00 | 6.18 | 8.6867 | 0 | 0 | 290.6459 | -2.5067 | -2.5067
2025-05-21 19:00:00 | 6.06 | 0 | 0 | 0 | 290.6459 | 6.06 | 6.06
2025-05-21 20:00:00 | 6.36 | 0 | 0 | 0 | 290.6459 | 6.36 | 6.36
2025-05-21 21:00:00 | 7.62 | 0 | 0 | 0 | 290.6459 | 7.62 | 7.62
2025-05-21 22:00:00 | 6.3 | 0 | 0 | 0 | 290.6459 | 6.3 | 6.3
2025-05-21 23:00:00 | 6.12 | 0 | 0 | 0 | 290.6459 | 6.12 | 6.12
2025-05-22 00:00:00 | 7.02 | 0 | 0 | 0 | 290.6459 | 7.02 | 7.02
2025-05-22 01:00:00 | 6.48 | 0 | 0 | 0 | 290.6459 | 6.48 | 6.48
2025-05-22 02:00:00 | 6.66 | 0 | 0 | 0 | 290.6459 | 6.66 | 6.66
2025-05-22 03:00:00 | 6.6 | 0 | 0 | 0 | 290.6459 | 6.6 | 6.6
2025-05-22 04:00:00 | 6.78 | 0 | 0 | 0 | 290.6459 | 6.78 | 6.78
2025-05-22 05:00:00 | 7.02 | 8.8268 | 0 | 0 | 290.6459 | -1.8068 | -1.8068
2025-05-22 06:00:00 | 8.34 | 18.9556 | 0 | 0 | 290.6459 | -10.6156 | -10.6156
2025-05-22 07:00:00 | 8.58 | 28.7392 | 0 | 0 | 290.6459 | -20.1592 | -20.1592
2025-05-22 08:00:00 | 8.22 | 37.511 | 0 | 0 | 290.6459 | -29.291 | -29.291
2025-05-22 09:00:00 | 8.64 | 44.6731 | 0 | 0 | 290.6459 | -36.0331 | -36.0331
2025-05-22 10:00:00 | 8.76 | 49.7375 | 0 | 0 | 290.6459 | -40.9775 | -40.9775
2025-05-22 11:00:00 | 7.38 | 52.359 | 0 | 0 | 290.6459 | -44.979 | -44.979
2025-05-22 12:00:00 | 6.78 | 52.359 | 0 | 0 | 290.6459 | -45.579 | -45.579
2025-05-22 13:00:00 | 6.42 | 49.7375 | 0 | 0 | 290.6459 | -43.3175 | -43.3175
2025-05-22 14:00:00 | 7.32 | 44.6731 | 0 | 0 | 290.6459 | -37.3531 | -37.3531
2025-05-22 15:00:00 | 7.02 | 37.511 | 0 | 0 | 290.6459 | -30.491 | -30.491
2025-05-22 16:00:00 | 8.46 | 28.7392 | 0 | 0 | 290.6459 | -20.2792 | -20.2792
2025-05-22 17:00:00 | 5.88 | 18.9556 | 0 | 0 | 290.6459 | -13.0756 | -13.0756
2025-05-22 18:00:00 | 5.58 | 8.8268 | 0 | 0 | 290.6459 | -3.2468 | -3.2468
2025-05-22 19:00:00 | 6.3 | 0 | 0 | 0 | 290.6459 | 6.3 | 6.3
2025-05-22 20:00:00 | 6 | 0 | 0 | 0 | 290.6459 | 6 | 6
2025-05-22 21:00:00 | 6.9 | 0 | 0 | 0 | 290.6459 | 6.9 | 6.9
2025-05-22 22:00:00 | 6.36 | 0 | 0 | 0 | 290.6459 | 6.36 | 6.36
2025-05-22 23:00:00 | 6.6 | 0 | 0 | 0 | 290.6459 | 6.6 | 6.6
2025-05-23 00:00:00 | 7.2 | 0 | 0 | 0 | 290.6459 | 7.2 | 7.2
2025-05-23 01:00:00 | 6.36 | 0 | 0 | 0 | 290.6459 | 6.36 | 6.36
2025-05-23 02:00:00 | 6.66 | 0 | 0 | 0 | 290.6459 | 6.66 | 6.66
2025-05-23 03:00:00 | 7.02 | 0 | 0 | 0 | 290.6459 | 7.02 | 7.02
2025-05-23 04:00:00 | 7.14 | 0 | 0 | 0 | 290.6459 | 7.14 | 7.14
2025-05-23 05:00:00 | 6.96 | 8.9626 | 0 | 0 | 290.6459 | -2.0026 | -2.0026
2025-05-23 06:00:00 | 9 | 19.0783 | 0 | 0 | 290.6459 | -10.0783 | -10.0783
2025-05-23 07:00:00 | 8.7 | 28.8494 | 0 | 0 | 290.6459 | -20.1494 | -20.1494
2025-05-23 08:00:00 | 8.88 | 37.6099 | 0 | 0 | 290.6459 | -28.7299 | -28.7299
2025-05-23 09:00:00 | 7.92 | 44.7628 | 0 | 0 | 290.6459 | -36.8428 | -36.8428
2025-05-23 10:00:00 | 8.16 | 49.8207 | 0 | 0 | 290.6459 | -41.6607 | -41.6607
2025-05-23 11:00:00 | 7.98 | 52.4388 | 0 | 0 | 290.6459 | -44.4588 | -44.4588
2025-05-23 12:00:00 | 10.74 | 52.4388 | 0 | 0 | 290.6459 | -41.6988 | -41.6988
2025-05-23 13:00:00 | 14.76 | 49.8207 | 0 | 0 | 290.6459 | -35.0607 | -35.0607
2025-05-23 14:00:00 | 14.88 | 44.7628 | 0 | 0 | 290.6459 | -29.8828 | -29.8828
2025-05-23 15:00:00 | 8.22 | 37.6099 | 0 | 0 | 290.6459 | -29.3899 | -29.3899
2025-05-23 16:00:00 | 6.3 | 28.8494 | 0 | 0 | 290.6459 | -22.5494 | -22.5494
2025-05-23 17:00:00 | 6.36 | 19.0783 | 0 | 0 | 290.6459 | -12.7183 | -12.7183
2025-05-23 18:00:00 | 6.42 | 8.9626 | 0 | 0 | 290.6459 | -2.5426 | -2.5426
2025-05-23 19:00:00 | 6.3 | 0 | 0 | 0 | 290.6459 | 6.3 | 6.3
2025-05-23 20:00:00 | 6.84 | 0 | 0 | 0 | 290.6459 | 6.84 | 6.84
2025-05-23 21:00:00 | 6.6 | 0 | 0 | 0 | 290.6459 | 6.6 | 6.6
2025-05-23 22:00:00 | 6.9 | 0 | 0 | 0 | 290.6459 | 6.9 | 6.9
2025-05-23 23:00:00 | 7.02 | 0 | 0 | 0 | 290.6459 | 7.02 | 7.02
2025-05-24 00:00:00 | 6.66 | 0 | 0 | 0 | 290.6459 | 6.66 | 6.66
2025-05-24 01:00:00 | 6.96 | 0 | 0 | 0 | 290.6459 | 6.96 | 6.96
2025-05-24 02:00:00 | 6.72 | 0 | 0 | 0 | 290.6459 | 6.72 | 6.72
2025-05-24 03:00:00 | 6.72 | 0 | 0 | 0 | 290.6459 | 6.72 | 6.72
2025-05-24 04:00:00 | 7.38 | 0 | 0 | 0 | 290.6459 | 7.38 | 7.38
2025-05-24 05:00:00 | 6.6 | 9.0941 | 0 | 0 | 290.6459 | -2.4941 | -2.4941
2025-05-24 06:00:00 | 6.48 | 19.1971 | 0 | 0 | 290.6459 | -12.7171 | -12.7171
2025-05-24 07:00:00 | 6.9 | 28.9559 | 0 | 0 | 290.6459 | -22.0559 | -22.0559
2025-05-24 08:00:00 | 6.24 | 37.7053 | 0 | 0 | 290.6459 | -31.4653 | -31.4653
2025-05-24 09:00:00 | 6.42 | 44.8492 | 0 | 0 | 290.6459 | -38.4292 | -38.4292
2025-05-24 10:00:00 | 6 | 49.9008 | 0 | 0 | 290.6459 | -43.9008 | -43.9008
2025-05-24 11:00:00 | 5.82 | 52.5156 | 0 | 0 | 290.6459 | -46.6956 | -46.6956
2025-05-24 12:00:00 | 6.36 | 52.5156 | 0 | 0 | 290.6459 | -46.1556 | -46.1556
2025-05-24 13:00:00 | 5.7 | 49.9008 | 0 | 0 | 290.6459 | -44.2008 | -44.2008
2025-05-24 14:00:00 | 6.12 | 44.8492 | 0 | 0 | 290.6459 | -38.7292 | -38.7292
2025-05-24 15:00:00 | 5.88 | 37.7053 | 0 | 0 | 290.6459 | -31.8253 | -31.8253
2025-05-24 16:00:00 | 6.18 | 28.9559 | 0 | 0 | 290.6459 | -22.7759 | -22.7759
2025-05-24 17:00:00 | 5.94 | 19.1971 | 0 | 0 | 290.6459 | -13.2571 | -13.2571
2025-05-24 18:00:00 | 5.58 | 9.0941 | 0 | 0 | 290.6459 | -3.5141 | -3.5141
2025-05-24 19:00:00 | 5.46 | 0 | 0 | 0 | 290.6459 | 5.46 | 5.46
2025-05-24 20:00:00 | 6.48 | 0 | 0 | 0 | 290.6459 | 6.48 | 6.48
2025-05-24 21:00:00 | 6.6 | 0 | 0 | 0 | 290.6459 | 6.6 | 6.6
2025-05-24 22:00:00 | 6.72 | 0 | 0 | 0 | 290.6459 | 6.72 | 6.72
2025-05-24 23:00:00 | 6.9 | 0 | 0 | 0 | 290.6459 | 6.9 | 6.9
2025-05-25 00:00:00 | 7.44 | 0 | 0 | 0 | 290.6459 | 7.44 | 7.44
2025-05-25 01:00:00 | 7.14 | 0 | 0 | 0 | 290.6459 | 7.14 | 7.14
2025-05-25 02:00:00 | 7.2 | 0 | 0 | 0 | 290.6459 | 7.2 | 7.2
2025-05-25 03:00:00 | 7.08 | 0 | 0 | 0 | 290.6459 | 7.08 | 7.08
2025-05-25 04:00:00 | 7.86 | 0 | 0 | 0 | 290.6459 | 7.86 | 7.86
2025-05-25 05:00:00 | 7.2 | 9.2213 | 0 | 0 | 290.6459 | -2.0213 | -2.0213
2025-05-25 06:00:00 | 7.02 | 19.3118 | 0 | 0 | 290.6459 | -12.2918 | -12.2918
2025-05-25 07:00:00 | 7.44 | 29.0586 | 0 | 0 | 290.6459 | -21.6186 | -21.6186
2025-05-25 08:00:00 | 6.24 | 37.7973 | 0 | 0 | 290.6459 | -31.5573 | -31.5573
2025-05-25 09:00:00 | 10.32 | 44.9324 | 0 | 0 | 290.6459 | -34.6124 | -34.6124
2025-05-25 10:00:00 | 11.82 | 49.9777 | 0 | 0 | 290.6459 | -38.1577 | -38.1577
2025-05-25 11:00:00 | 8.88 | 52.5893 | 0 | 0 | 290.6459 | -43.7093 | -43.7093
2025-05-25 12:00:00 | 11.64 | 52.5893 | 0 | 0 | 290.6459 | -40.9493 | -40.9493
2025-05-25 13:00:00 | 11.88 | 49.9777 | 0 | 0 | 290.6459 | -38.0977 | -38.0977
2025-05-25 14:00:00 | 11.22 | 44.9324 | 0 | 0 | 290.6459 | -33.7124 | -33.7124
2025-05-25 15:00:00 | 6.12 | 37.7973 | 0 | 0 | 290.6459 | -31.6773 | -31.6773
2025-05-25 16:00:00 | 4.86 | 29.0586 | 0 | 0 | 290.6459 | -24.1986 | -24.1986
2025-05-25 17:00:00 | 4.86 | 19.3118 | 0 | 0 | 290.6459 | -14.4518 | -14.4518
2025-05-25 18:00:00 | 4.56 | 9.2213 | 0 | 0 | 290.6459 | -4.6613 | -4.6613
2025-05-25 19:00:00 | 4.86 | 0 | 0 | 0 | 290.6459 | 4.86 | 4.86
2025-05-25 20:00:00 | 5.52 | 0 | 0 | 0 | 290.6459 | 5.52 | 5.52
2025-05-25 21:00:00 | 6.48 | 0 | 0 | 0 | 290.6459 | 6.48 | 6.48
2025-05-25 22:00:00 | 5.88 | 0 | 0 | 0 | 290.6459 | 5.88 | 5.88
2025-05-25 23:00:00 | 6.36 | 0 | 0 | 0 | 290.6459 | 6.36 | 6.36
2025-05-26 00:00:00 | 6.54 | 0 | 0 | 0 | 290.6459 | 6.54 | 6.54
2025-05-26 01:00:00 | 7.02 | 0 | 0 | 0 | 290.6459 | 7.02 | 7.02
2025-05-26 02:00:00 | 6.42 | 0 | 0 | 0 | 290.6459 | 6.42 | 6.42
2025-05-26 03:00:00 | 6.84 | 0 | 0 | 0 | 290.6459 | 6.84 | 6.84
2025-05-26 04:00:00 | 6.84 | 0 | 0 | 0 | 290.6459 | 6.84 | 6.84
2025-05-26 05:00:00 | 7.02 | 9.3441 | 0 | 0 | 290.6459 | -2.3241 | -2.3241
2025-05-26 06:00:00 | 9.06 | 19.4226 | 0 | 0 | 290.6459 | -10.3626 | -10.3626
2025-05-26 07:00:00 | 7.38 | 29.1576 | 0 | 0 | 290.6459 | -21.7776 | -21.7776
2025-05-26 08:00:00 | 6.6 | 37.8858 | 0 | 0 | 290.6459 | -31.2858 | -31.2858
2025-05-26 09:00:00 | 5.7 | 45.0124 | 0 | 0 | 290.6459 | -39.3124 | -39.3124
2025-05-26 10:00:00 | 5.58 | 50.0516 | 0 | 0 | 290.6459 | -44.4716 | -44.4716
2025-05-26 11:00:00 | 5.04 | 52.6601 | 0 | 0 | 290.6459 | -47.6201 | -47.6201
2025-05-26 12:00:00 | 4.68 | 52.6601 | 0 | 0 | 290.6459 | -47.9801 | -47.9801
2025-05-26 13:00:00 | 4.92 | 50.0516 | 0 | 0 | 290.6459 | -45.1316 | -45.1316
2025-05-26 14:00:00 | 4.98 | 45.0124 | 0 | 0 | 290.6459 | -40.0324 | -40.0324
2025-05-26 15:00:00 | 4.2 | 37.8858 | 0 | 0 | 290.6459 | -33.6858 | -33.6858
2025-05-26 16:00:00 | 4.56 | 29.1576 | 0 | 0 | 290.6459 | -24.5976 | -24.5976
2025-05-26 17:00:00 | 3.78 | 19.4226 | 0 | 0 | 290.6459 | -15.6426 | -15.6426
2025-05-26 18:00:00 | 4.08 | 9.3441 | 0 | 0 | 290.6459 | -5.2641 | -5.2641
2025-05-26 19:00:00 | 3.66 | 0 | 0 | 0 | 290.6459 | 3.66 | 3.66
2025-05-26 20:00:00 | 4.74 | 0 | 0 | 0 | 290.6459 | 4.74 | 4.74
2025-05-26 21:00:00 | 5.22 | 0 | 0 | 0 | 290.6459 | 5.22 | 5.22
2025-05-26 22:00:00 | 4.8 | 0 | 0 | 0 | 290.6459 | 4.8 | 4.8
2025-05-26 23:00:00 | 5.76 | 0 | 0 | 0 | 290.6459 | 5.76 | 5.76
2025-05-27 00:00:00 | 5.4 | 0 | 0 | 0 | 290.6459 | 5.4 | 5.4
2025-05-27 01:00:00 | 5.76 | 0 | 0 | 0 | 290.6459 | 5.76 | 5.76
2025-05-27 02:00:00 | 5.94 | 0 | 0 | 0 | 290.6459 | 5.94 | 5.94
2025-05-27 03:00:00 | 5.76 | 0 | 0 | 0 | 290.6459 | 5.76 | 5.76
2025-05-27 04:00:00 | 5.88 | 0 | 0 | 0 | 290.6459 | 5.88 | 5.88
2025-05-27 05:00:00 | 5.76 | 9.4626 | 0 | 0 | 290.6459 | -3.7026 | -3.7026
2025-05-27 06:00:00 | 6.96 | 19.5293 | 0 | 0 | 290.6459 | -12.5693 | -12.5693
2025-05-27 07:00:00 | 6 | 29.2529 | 0 | 0 | 290.6459 | -23.2529 | -23.2529
2025-05-27 08:00:00 | 6.12 | 37.9709 | 0 | 0 | 290.6459 | -31.8509 | -31.8509
2025-05-27 09:00:00 | 5.88 | 45.0891 | 0 | 0 | 290.6459 | -39.2091 | -39.2091
2025-05-27 10:00:00 | 5.34 | 50.1224 | 0 | 0 | 290.6459 | -44.7824 | -44.7824
2025-05-27 11:00:00 | 5.4 | 52.7279 | 0 | 0 | 290.6459 | -47.3279 | -47.3279
2025-05-27 12:00:00 | 5.46 | 52.7279 | 0 | 0 | 290.6459 | -47.2679 | -47.2679
2025-05-27 13:00:00 | 5.34 | 50.1224 | 0 | 0 | 290.6459 | -44.7824 | -44.7824
2025-05-27 14:00:00 | 5.16 | 45.0891 | 0 | 0 | 290.6459 | -39.9291 | -39.9291
2025-05-27 15:00:00 | 4.62 | 37.9709 | 0 | 0 | 290.6459 | -33.3509 | -33.3509
2025-05-27 16:00:00 | 4.2 | 29.2529 | 0 | 0 | 290.6459 | -25.0529 | -25.0529
2025-05-27 17:00:00 | 3.48 | 19.5293 | 0 | 0 | 290.6459 | -16.0493 | -16.0493
2025-05-27 18:00:00 | 4.02 | 9.4626 | 0 | 0 | 290.6459 | -5.4426 | -5.4426
2025-05-27 19:00:00 | 3.48 | 0 | 0 | 0 | 290.6459 | 3.48 | 3.48
2025-05-27 20:00:00 | 4.14 | 0 | 0 | 0 | 290.6459 | 4.14 | 4.14
2025-05-27 21:00:00 | 4.62 | 0 | 0 | 0 | 290.6459 | 4.62 | 4.62
2025-05-27 22:00:00 | 4.98 | 0 | 0 | 0 | 290.6459 | 4.98 | 4.98
2025-05-27 23:00:00 | 4.92 | 0 | 0 | 0 | 290.6459 | 4.92 | 4.92
2025-05-28 00:00:00 | 5.58 | 0 | 0 | 0 | 290.6459 | 5.58 | 5.58
2025-05-28 01:00:00 | 5.4 | 0 | 0 | 0 | 290.6459 | 5.4 | 5.4
2025-05-28 02:00:00 | 5.1 | 0 | 0 | 0 | 290.6459 | 5.1 | 5.1
2025-05-28 03:00:00 | 6.24 | 0 | 0 | 0 | 290.6459 | 6.24 | 6.24
2025-05-28 04:00:00 | 5.46 | 0 | 0 | 0 | 290.6459 | 5.46 | 5.46
2025-05-28 05:00:00 | 6 | 9.5767 | 0 | 0 | 290.6459 | -3.5767 | -3.5767
2025-05-28 06:00:00 | 7.5 | 19.6319 | 0 | 0 | 290.6459 | -12.1319 | -12.1319
2025-05-28 07:00:00 | 7.2 | 29.3445 | 0 | 0 | 290.6459 | -22.1445 | -22.1445
2025-05-28 08:00:00 | 6.72 | 38.0526 | 0 | 0 | 290.6459 | -31.3326 | -31.3326
2025-05-28 09:00:00 | 7.14 | 45.1627 | 0 | 0 | 290.6459 | -38.0227 | -38.0227
2025-05-28 10:00:00 | 6.6 | 50.1903 | 0 | 0 | 290.6459 | -43.5903 | -43.5903
2025-05-28 11:00:00 | 6.54 | 52.7928 | 0 | 0 | 290.6459 | -46.2528 | -46.2528
2025-05-28 12:00:00 | 6.6 | 52.7928 | 0 | 0 | 290.6459 | -46.1928 | -46.1928
2025-05-28 13:00:00 | 6.6 | 50.1903 | 0 | 0 | 290.6459 | -43.5903 | -43.5903
2025-05-28 14:00:00 | 6.12 | 45.1627 | 0 | 0 | 290.6459 | -39.0427 | -39.0427
2025-05-28 15:00:00 | 6.12 | 38.0526 | 0 | 0 | 290.6459 | -31.9326 | -31.9326
2025-05-28 16:00:00 | 4.92 | 29.3445 | 0 | 0 | 290.6459 | -24.4245 | -24.4245
2025-05-28 17:00:00 | 5.4 | 19.6319 | 0 | 0 | 290.6459 | -14.2319 | -14.2319
2025-05-28 18:00:00 | 4.98 | 9.5767 | 0 | 0 | 290.6459 | -4.5967 | -4.5967
2025-05-28 19:00:00 | 5.22 | 0 | 0 | 0 | 290.6459 | 5.22 | 5.22
2025-05-28 20:00:00 | 5.82 | 0 | 0 | 0 | 290.6459 | 5.82 | 5.82
2025-05-28 21:00:00 | 5.52 | 0 | 0 | 0 | 290.6459 | 5.52 | 5.52
2025-05-28 22:00:00 | 5.58 | 0 | 0 | 0 | 290.6459 | 5.58 | 5.58
2025-05-28 23:00:00 | 11.04 | 0 | 0 | 0 | 290.6459 | 11.04 | 11.04
2025-05-29 00:00:00 | 12.48 | 0 | 0 | 0 | 290.6459 | 12.48 | 12.48
2025-05-29 01:00:00 | 12.12 | 0 | 0 | 0 | 290.6459 | 12.12 | 12.12
2025-05-29 02:00:00 | 12.3 | 0 | 0 | 0 | 290.6459 | 12.3 | 12.3
2025-05-29 03:00:00 | 12.54 | 0 | 0 | 0 | 290.6459 | 12.54 | 12.54
2025-05-29 04:00:00 | 12 | 0 | 0 | 0 | 290.6459 | 12 | 12
2025-05-29 05:00:00 | 15.78 | 9.6864 | 0 | 0 | 290.6459 | 6.0936 | 6.0936
2025-05-29 06:00:00 | 26.7 | 19.7305 | 0 | 0 | 290.6459 | 6.9695 | 6.9695
2025-05-29 07:00:00 | 25.68 | 29.4323 | 0 | 0 | 290.6459 | -3.7523 | -3.7523
2025-05-29 08:00:00 | 29.46 | 38.1308 | 0 | 0 | 290.6459 | -8.6708 | -8.6708
2025-05-29 09:00:00 | 21.84 | 45.2331 | 0 | 0 | 290.6459 | -23.3931 | -23.3931
2025-05-29 10:00:00 | 21.78 | 50.2551 | 0 | 0 | 290.6459 | -28.4751 | -28.4751
2025-05-29 11:00:00 | 21.48 | 52.8547 | 0 | 0 | 290.6459 | -31.3747 | -31.3747
2025-05-29 12:00:00 | 9.48 | 52.8547 | 0 | 0 | 290.6459 | -43.3747 | -43.3747
2025-05-29 13:00:00 | 7.08 | 50.2551 | 0 | 0 | 290.6459 | -43.1751 | -43.1751
2025-05-29 14:00:00 | 6.3 | 45.2331 | 0 | 0 | 290.6459 | -38.9331 | -38.9331
2025-05-29 15:00:00 | 5.58 | 38.1308 | 0 | 0 | 290.6459 | -32.5508 | -32.5508
2025-05-29 16:00:00 | 5.46 | 29.4323 | 0 | 0 | 290.6459 | -23.9723 | -23.9723
2025-05-29 17:00:00 | 4.5 | 19.7305 | 0 | 0 | 290.6459 | -15.2305 | -15.2305
2025-05-29 18:00:00 | 5.4 | 9.6864 | 0 | 0 | 290.6459 | -4.2864 | -4.2864
2025-05-29 19:00:00 | 4.74 | 0 | 0 | 0 | 290.6459 | 4.74 | 4.74
2025-05-29 20:00:00 | 5.82 | 0 | 0 | 0 | 290.6459 | 5.82 | 5.82
2025-05-29 21:00:00 | 5.22 | 0 | 0 | 0 | 290.6459 | 5.22 | 5.22
2025-05-29 22:00:00 | 5.34 | 0 | 0 | 0 | 290.6459 | 5.34 | 5.34
2025-05-29 23:00:00 | 6 | 0 | 0 | 0 | 290.6459 | 6 | 6
2025-05-30 00:00:00 | 5.4 | 0 | 0 | 0 | 290.6459 | 5.4 | 5.4
2025-05-30 01:00:00 | 5.7 | 0 | 0 | 0 | 290.6459 | 5.7 | 5.7
2025-05-30 02:00:00 | 5.7 | 0 | 0 | 0 | 290.6459 | 5.7 | 5.7
2025-05-30 03:00:00 | 5.52 | 0 | 0 | 0 | 290.6459 | 5.52 | 5.52
2025-05-30 04:00:00 | 6.06 | 0.10008 | 0 | 0 | 290.6459 | 5.9599 | 5.9599
2025-05-30 05:00:00 | 5.76 | 9.7916 | 0 | 0 | 290.6459 | -4.0316 | -4.0316
2025-05-30 06:00:00 | 6.66 | 19.825 | 0 | 0 | 290.6459 | -13.165 | -13.165
2025-05-30 07:00:00 | 7.44 | 29.5165 | 0 | 0 | 290.6459 | -22.0765 | -22.0765
2025-05-30 08:00:00 | 6.84 | 38.2057 | 0 | 0 | 290.6459 | -31.3657 | -31.3657
2025-05-30 09:00:00 | 6.96 | 45.3003 | 0 | 0 | 290.6459 | -38.3403 | -38.3403
2025-05-30 10:00:00 | 6 | 50.317 | 0 | 0 | 290.6459 | -44.317 | -44.317
2025-05-30 11:00:00 | 5.94 | 52.9139 | 0 | 0 | 290.6459 | -46.9739 | -46.9739
2025-05-30 12:00:00 | 6.18 | 52.9139 | 0 | 0 | 290.6459 | -46.7339 | -46.7339
2025-05-30 13:00:00 | 5.76 | 50.317 | 0 | 0 | 290.6459 | -44.557 | -44.557
2025-05-30 14:00:00 | 5.76 | 45.3003 | 0 | 0 | 290.6459 | -39.5403 | -39.5403
2025-05-30 15:00:00 | 4.98 | 38.2057 | 0 | 0 | 290.6459 | -33.2257 | -33.2257
2025-05-30 16:00:00 | 4.26 | 29.5165 | 0 | 0 | 290.6459 | -25.2565 | -25.2565
2025-05-30 17:00:00 | 3.6 | 19.825 | 0 | 0 | 290.6459 | -16.225 | -16.225
2025-05-30 18:00:00 | 4.08 | 9.7916 | 0 | 0 | 290.6459 | -5.7116 | -5.7116
2025-05-30 19:00:00 | 4.32 | 0.10008 | 0 | 0 | 290.6459 | 4.2199 | 4.2199
2025-05-30 20:00:00 | 4.56 | 0 | 0 | 0 | 290.6459 | 4.56 | 4.56
2025-05-30 21:00:00 | 4.8 | 0 | 0 | 0 | 290.6459 | 4.8 | 4.8
2025-05-30 22:00:00 | 5.04 | 0 | 0 | 0 | 290.6459 | 5.04 | 5.04
2025-05-30 23:00:00 | 5.82 | 0 | 0 | 0 | 290.6459 | 5.82 | 5.82
2025-05-31 00:00:00 | 5.22 | 0 | 0 | 0 | 290.6459 | 5.22 | 5.22
2025-05-31 01:00:00 | 6.06 | 0 | 0 | 0 | 290.6459 | 6.06 | 6.06
2025-05-31 02:00:00 | 5.4 | 0 | 0 | 0 | 290.6459 | 5.4 | 5.4
2025-05-31 03:00:00 | 6.36 | 0 | 0 | 0 | 290.6459 | 6.36 | 6.36
2025-05-31 04:00:00 | 5.94 | 0.21084 | 0 | 0 | 290.6459 | 5.7292 | 5.7292
2025-05-31 05:00:00 | 5.88 | 9.8923 | 0 | 0 | 290.6459 | -4.0123 | -4.0123
2025-05-31 06:00:00 | 6.6 | 19.9154 | 0 | 0 | 290.6459 | -13.3154 | -13.3154
2025-05-31 07:00:00 | 6.18 | 29.5969 | 0 | 0 | 290.6459 | -23.4169 | -23.4169
2025-05-31 08:00:00 | 6.18 | 38.2771 | 0 | 0 | 290.6459 | -32.0971 | -32.0971
2025-05-31 09:00:00 | 6.3 | 45.3645 | 0 | 0 | 290.6459 | -39.0645 | -39.0645
2025-05-31 10:00:00 | 6.36 | 50.376 | 0 | 0 | 290.6459 | -44.016 | -44.016
2025-05-31 11:00:00 | 6.6 | 52.9701 | 0 | 0 | 290.6459 | -46.3701 | -46.3701
2025-05-31 12:00:00 | 5.64 | 52.9701 | 0 | 0 | 290.6459 | -47.3301 | -47.3301
2025-05-31 13:00:00 | 5.76 | 50.376 | 0 | 0 | 290.6459 | -44.616 | -44.616
2025-05-31 14:00:00 | 4.92 | 45.3645 | 0 | 0 | 290.6459 | -40.4445 | -40.4445
2025-05-31 15:00:00 | 5.76 | 38.2771 | 0 | 0 | 290.6459 | -32.5171 | -32.5171
2025-05-31 16:00:00 | 4.98 | 29.5969 | 0 | 0 | 290.6459 | -24.6169 | -24.6169
2025-05-31 17:00:00 | 5.88 | 19.9154 | 0 | 0 | 290.6459 | -14.0354 | -14.0354
2025-05-31 18:00:00 | 5.46 | 9.8923 | 0 | 0 | 290.6459 | -4.4323 | -4.4323
2025-05-31 19:00:00 | 4.98 | 0.21084 | 0 | 0 | 290.6459 | 4.7692 | 4.7692
2025-05-31 20:00:00 | 6.24 | 0 | 0 | 0 | 290.6459 | 6.24 | 6.24
2025-05-31 21:00:00 | 6.48 | 0 | 0 | 0 | 290.6459 | 6.48 | 6.48
2025-05-31 22:00:00 | 6.6 | 0 | 39.0387 | 0 | 325 | 45.6387 | 6.6
2025-05-31 23:00:00 | 6.54 | 0 | 0 | 0 | 325 | 6.54 | 6.54
2025-06-01 00:00:00 | 6.84 | 0 | 0 | 0 | 325 | 6.84 | 6.84
2025-06-01 01:00:00 | 7.2 | 0 | 0 | 0 | 325 | 7.2 | 7.2
2025-06-01 02:00:00 | 6.96 | 0 | 0 | 0 | 325 | 6.96 | 6.96
2025-06-01 03:00:00 | 6.9 | 0 | 0 | 0 | 325 | 6.9 | 6.9
2025-06-01 04:00:00 | 7.38 | 0.3323 | 0 | 0 | 325 | 7.0477 | 7.0477
2025-06-01 05:00:00 | 7.44 | 10.4799 | 0 | 0 | 325 | -3.0399 | -3.0399
2025-06-01 06:00:00 | 6.9 | 20.9854 | 0 | 0 | 325 | -14.0854 | -14.0854
2025-06-01 07:00:00 | 6.6 | 31.133 | 0 | 0 | 325 | -24.533 | -24.533
2025-06-01 08:00:00 | 6.18 | 40.231 | 0 | 0 | 325 | -34.051 | -34.051
2025-06-01 09:00:00 | 5.76 | 47.6595 | 0 | 0 | 325 | -41.8995 | -41.8995
2025-06-01 10:00:00 | 5.82 | 52.9123 | 0 | 0 | 325 | -47.0923 | -47.0923
2025-06-01 11:00:00 | 5.88 | 55.6313 | 0 | 0 | 325 | -49.7513 | -49.7513
2025-06-01 12:00:00 | 4.92 | 55.6313 | 0 | 0 | 325 | -50.7113 | -50.7113
2025-06-01 13:00:00 | 5.28 | 52.9123 | 0 | 0 | 325 | -47.6323 | -47.6323
2025-06-01 14:00:00 | 5.04 | 47.6595 | 0 | 0 | 325 | -42.6195 | -42.6195
2025-06-01 15:00:00 | 4.86 | 40.231 | 0 | 0 | 325 | -35.371 | -35.371
2025-06-01 16:00:00 | 5.22 | 31.133 | 0 | 0 | 325 | -25.913 | -25.913
2025-06-01 17:00:00 | 4.62 | 20.9854 | 0 | 0 | 325 | -16.3654 | -16.3654
2025-06-01 18:00:00 | 5.58 | 10.4799 | 0 | 0 | 325 | -4.8999 | -4.8999
2025-06-01 19:00:00 | 4.86 | 0.3323 | 0 | 0 | 325 | 4.5277 | 4.5277
2025-06-01 20:00:00 | 6.18 | 0 | 0 | 0 | 325 | 6.18 | 6.18
2025-06-01 21:00:00 | 6 | 0 | 0 | 0 | 325 | 6 | 6
2025-06-01 22:00:00 | 6.66 | 0 | 0 | 0 | 325 | 6.66 | 6.66
2025-06-01 23:00:00 | 6.84 | 0 | 0 | 0 | 325 | 6.84 | 6.84
2025-06-02 00:00:00 | 7.02 | 0 | 0 | 0 | 325 | 7.02 | 7.02
2025-06-02 01:00:00 | 6.78 | 0 | 0 | 0 | 325 | 6.78 | 6.78
2025-06-02 02:00:00 | 7.02 | 0 | 0 | 0 | 325 | 7.02 | 7.02
2025-06-02 03:00:00 | 7.38 | 0 | 0 | 0 | 325 | 7.38 | 7.38
2025-06-02 04:00:00 | 7.74 | 0.43825 | 0 | 0 | 325 | 7.3018 | 7.3018
2025-06-02 05:00:00 | 7.62 | 10.5761 | 0 | 0 | 325 | -2.9561 | -2.9561
2025-06-02 06:00:00 | 7.56 | 21.0716 | 0 | 0 | 325 | -13.5116 | -13.5116
2025-06-02 07:00:00 | 7.74 | 31.2095 | 0 | 0 | 325 | -23.4695 | -23.4695
2025-06-02 08:00:00 | 6.96 | 40.2989 | 0 | 0 | 325 | -33.3389 | -33.3389
2025-06-02 09:00:00 | 7.68 | 47.7203 | 0 | 0 | 325 | -40.0403 | -40.0403
2025-06-02 10:00:00 | 6.72 | 52.9681 | 0 | 0 | 325 | -46.2481 | -46.2481
2025-06-02 11:00:00 | 6.12 | 55.6845 | 0 | 0 | 325 | -49.5645 | -49.5645
2025-06-02 12:00:00 | 6.48 | 55.6845 | 0 | 0 | 325 | -49.2045 | -49.2045
2025-06-02 13:00:00 | 6 | 52.9681 | 0 | 0 | 325 | -46.9681 | -46.9681
2025-06-02 14:00:00 | 6.06 | 47.7203 | 0 | 0 | 325 | -41.6603 | -41.6603
2025-06-02 15:00:00 | 10.26 | 40.2989 | 0 | 0 | 325 | -30.0389 | -30.0389
2025-06-02 16:00:00 | 18.78 | 31.2095 | 0 | 0 | 325 | -12.4295 | -12.4295
2025-06-02 17:00:00 | 15.06 | 21.0716 | 0 | 0 | 325 | -6.0116 | -6.0116
2025-06-02 18:00:00 | 4.02 | 10.5761 | 0 | 0 | 325 | -6.5561 | -6.5561
2025-06-02 19:00:00 | 4.08 | 0.43825 | 0 | 0 | 325 | 3.6418 | 3.6418
2025-06-02 20:00:00 | 4.74 | 0 | 0 | 0 | 325 | 4.74 | 4.74
2025-06-02 21:00:00 | 4.86 | 0 | 0 | 0 | 325 | 4.86 | 4.86
2025-06-02 22:00:00 | 5.16 | 0 | 0 | 0 | 325 | 5.16 | 5.16
2025-06-02 23:00:00 | 5.4 | 0 | 0 | 0 | 325 | 5.4 | 5.4
2025-06-03 00:00:00 | 5.52 | 0 | 0 | 0 | 325 | 5.52 | 5.52
2025-06-03 01:00:00 | 5.28 | 0 | 0 | 0 | 325 | 5.28 | 5.28
2025-06-03 02:00:00 | 6.06 | 0 | 0 | 0 | 325 | 6.06 | 6.06
2025-06-03 03:00:00 | 5.58 | 0 | 0 | 0 | 325 | 5.58 | 5.58
2025-06-03 04:00:00 | 5.82 | 0.53902 | 0 | 0 | 325 | 5.281 | 5.281
2025-06-03 05:00:00 | 6.12 | 10.6676 | 0 | 0 | 325 | -4.5476 | -4.5476
2025-06-03 06:00:00 | 6.78 | 21.1536 | 0 | 0 | 325 | -14.3736 | -14.3736
2025-06-03 07:00:00 | 7.38 | 31.2822 | 0 | 0 | 325 | -23.9022 | -23.9022
2025-06-03 08:00:00 | 7.2 | 40.3633 | 0 | 0 | 325 | -33.1633 | -33.1633
2025-06-03 09:00:00 | 6.54 | 47.7779 | 0 | 0 | 325 | -41.2379 | -41.2379
2025-06-03 10:00:00 | 7.32 | 53.0209 | 0 | 0 | 325 | -45.7009 | -45.7009
2025-06-03 11:00:00 | 7.62 | 55.7349 | 0 | 0 | 325 | -48.1149 | -48.1149
2025-06-03 12:00:00 | 7.8 | 55.7349 | 0 | 0 | 325 | -47.9349 | -47.9349
2025-06-03 13:00:00 | 7.8 | 53.0209 | 0 | 0 | 325 | -45.2209 | -45.2209
2025-06-03 14:00:00 | 8.04 | 47.7779 | 0 | 0 | 325 | -39.7379 | -39.7379
2025-06-03 15:00:00 | 7.08 | 40.3633 | 0 | 0 | 325 | -33.2833 | -33.2833
2025-06-03 16:00:00 | 5.7 | 31.2822 | 0 | 0 | 325 | -25.5822 | -25.5822
2025-06-03 17:00:00 | 5.94 | 21.1536 | 0 | 0 | 325 | -15.2136 | -15.2136
2025-06-03 18:00:00 | 5.28 | 10.6676 | 0 | 0 | 325 | -5.3876 | -5.3876
2025-06-03 19:00:00 | 5.34 | 0.53902 | 0 | 0 | 325 | 4.801 | 4.801
2025-06-03 20:00:00 | 5.7 | 0 | 0 | 0 | 325 | 5.7 | 5.7
2025-06-03 21:00:00 | 5.46 | 0 | 0 | 0 | 325 | 5.46 | 5.46
2025-06-03 22:00:00 | 5.28 | 0 | 0 | 0 | 325 | 5.28 | 5.28
2025-06-03 23:00:00 | 5.28 | 0 | 0 | 0 | 325 | 5.28 | 5.28
2025-06-04 00:00:00 | 5.82 | 0 | 0 | 0 | 325 | 5.82 | 5.82
2025-06-04 01:00:00 | 5.58 | 0 | 0 | 0 | 325 | 5.58 | 5.58
2025-06-04 02:00:00 | 5.64 | 0 | 0 | 0 | 325 | 5.64 | 5.64
2025-06-04 03:00:00 | 5.88 | 0 | 0 | 0 | 325 | 5.88 | 5.88
2025-06-04 04:00:00 | 5.7 | 0.63459 | 0 | 0 | 325 | 5.0654 | 5.0654
2025-06-04 05:00:00 | 5.52 | 10.7544 | 0 | 0 | 325 | -5.2344 | -5.2344
2025-06-04 06:00:00 | 6.78 | 21.2312 | 0 | 0 | 325 | -14.4512 | -14.4512
2025-06-04 07:00:00 | 7.26 | 31.351 | 0 | 0 | 325 | -24.091 | -24.091
2025-06-04 08:00:00 | 7.08 | 40.4241 | 0 | 0 | 325 | -33.3441 | -33.3441
2025-06-04 09:00:00 | 7.5 | 47.8323 | 0 | 0 | 325 | -40.3323 | -40.3323
2025-06-04 10:00:00 | 7.8 | 53.0707 | 0 | 0 | 325 | -45.2707 | -45.2707
2025-06-04 11:00:00 | 7.68 | 55.7823 | 0 | 0 | 325 | -48.1023 | -48.1023
2025-06-04 12:00:00 | 7.32 | 55.7823 | 0 | 0 | 325 | -48.4623 | -48.4623
2025-06-04 13:00:00 | 7.74 | 53.0707 | 0 | 0 | 325 | -45.3307 | -45.3307
2025-06-04 14:00:00 | 7.98 | 47.8323 | 0 | 0 | 325 | -39.8523 | -39.8523
2025-06-04 15:00:00 | 5.94 | 40.4241 | 0 | 0 | 325 | -34.4841 | -34.4841
2025-06-04 16:00:00 | 5.94 | 31.351 | 0 | 0 | 325 | -25.411 | -25.411
2025-06-04 17:00:00 | 5.22 | 21.2312 | 0 | 0 | 325 | -16.0112 | -16.0112
2025-06-04 18:00:00 | 5.34 | 10.7544 | 0 | 0 | 325 | -5.4144 | -5.4144
2025-06-04 19:00:00 | 5.58 | 0.63459 | 0 | 0 | 325 | 4.9454 | 4.9454
2025-06-04 20:00:00 | 5.34 | 0 | 0 | 0 | 325 | 5.34 | 5.34
2025-06-04 21:00:00 | 5.46 | 0 | 0 | 0 | 325 | 5.46 | 5.46
2025-06-04 22:00:00 | 5.7 | 0 | 0 | 0 | 325 | 5.7 | 5.7
2025-06-04 23:00:00 | 5.4 | 0 | 0 | 0 | 325 | 5.4 | 5.4
2025-06-05 00:00:00 | 5.34 | 0 | 0 | 0 | 325 | 5.34 | 5.34
2025-06-05 01:00:00 | 5.52 | 0 | 0 | 0 | 325 | 5.52 | 5.52
2025-06-05 02:00:00 | 5.94 | 0 | 0 | 0 | 325 | 5.94 | 5.94
2025-06-05 03:00:00 | 5.64 | 0 | 0 | 0 | 325 | 5.64 | 5.64
2025-06-05 04:00:00 | 5.76 | 0.72493 | 0 | 0 | 325 | 5.0351 | 5.0351
2025-06-05 05:00:00 | 6.3 | 10.8363 | 0 | 0 | 325 | -4.5363 | -4.5363
2025-06-05 06:00:00 | 7.2 | 21.3044 | 0 | 0 | 325 | -14.1044 | -14.1044
2025-06-05 07:00:00 | 7.38 | 31.4159 | 0 | 0 | 325 | -24.0359 | -24.0359
2025-06-05 08:00:00 | 7.8 | 40.4815 | 0 | 0 | 325 | -32.6815 | -32.6815
2025-06-05 09:00:00 | 7.74 | 47.8836 | 0 | 0 | 325 | -40.1436 | -40.1436
2025-06-05 10:00:00 | 8.04 | 53.1176 | 0 | 0 | 325 | -45.0776 | -45.0776
2025-06-05 11:00:00 | 13.5 | 55.827 | 0 | 0 | 325 | -42.327 | -42.327
2025-06-05 12:00:00 | 21.18 | 55.827 | 0 | 0 | 325 | -34.647 | -34.647
2025-06-05 13:00:00 | 21.66 | 53.1176 | 0 | 0 | 325 | -31.4576 | -31.4576
2025-06-05 14:00:00 | 20.1 | 47.8836 | 0 | 0 | 325 | -27.7836 | -27.7836
2025-06-05 15:00:00 | 11.4 | 40.4815 | 0 | 0 | 325 | -29.0815 | -29.0815
2025-06-05 16:00:00 | 6.3 | 31.4159 | 0 | 0 | 325 | -25.1159 | -25.1159
2025-06-05 17:00:00 | 5.1 | 21.3044 | 0 | 0 | 325 | -16.2044 | -16.2044
2025-06-05 18:00:00 | 5.1 | 10.8363 | 0 | 0 | 325 | -5.7363 | -5.7363
2025-06-05 19:00:00 | 5.28 | 0.72493 | 0 | 0 | 325 | 4.5551 | 4.5551
2025-06-05 20:00:00 | 5.58 | 0 | 0 | 0 | 325 | 5.58 | 5.58
2025-06-05 21:00:00 | 5.58 | 0 | 0 | 0 | 325 | 5.58 | 5.58
2025-06-05 22:00:00 | 5.46 | 0 | 0 | 0 | 325 | 5.46 | 5.46
2025-06-05 23:00:00 | 5.94 | 0 | 0 | 0 | 325 | 5.94 | 5.94
2025-06-06 00:00:00 | 5.58 | 0 | 0 | 0 | 325 | 5.58 | 5.58
2025-06-06 01:00:00 | 5.46 | 0 | 0 | 0 | 325 | 5.46 | 5.46
2025-06-06 02:00:00 | 5.82 | 0 | 0 | 0 | 325 | 5.82 | 5.82
2025-06-06 03:00:00 | 5.58 | 0 | 0 | 0 | 325 | 5.58 | 5.58
2025-06-06 04:00:00 | 5.88 | 0.81001 | 0 | 0 | 325 | 5.07 | 5.07
2025-06-06 05:00:00 | 5.46 | 10.9135 | 0 | 0 | 325 | -5.4535 | -5.4535
2025-06-06 06:00:00 | 7.32 | 21.3734 | 0 | 0 | 325 | -14.0534 | -14.0534
2025-06-06 07:00:00 | 7.68 | 31.4768 | 0 | 0 | 325 | -23.7968 | -23.7968
2025-06-06 08:00:00 | 6.96 | 40.5354 | 0 | 0 | 325 | -33.5754 | -33.5754
2025-06-06 09:00:00 | 7.2 | 47.9316 | 0 | 0 | 325 | -40.7316 | -40.7316
2025-06-06 10:00:00 | 7.2 | 53.1616 | 0 | 0 | 325 | -45.9616 | -45.9616
2025-06-06 11:00:00 | 7.68 | 55.8688 | 0 | 0 | 325 | -48.1888 | -48.1888
2025-06-06 12:00:00 | 13.68 | 55.8688 | 0 | 0 | 325 | -42.1888 | -42.1888
2025-06-06 13:00:00 | 10.86 | 53.1616 | 0 | 0 | 325 | -42.3016 | -42.3016
2025-06-06 14:00:00 | 6.48 | 47.9316 | 0 | 0 | 325 | -41.4516 | -41.4516
2025-06-06 15:00:00 | 5.34 | 40.5354 | 0 | 0 | 325 | -35.1954 | -35.1954
2025-06-06 16:00:00 | 5.28 | 31.4768 | 0 | 0 | 325 | -26.1968 | -26.1968
2025-06-06 17:00:00 | 5.58 | 21.3734 | 0 | 0 | 325 | -15.7934 | -15.7934
2025-06-06 18:00:00 | 12 | 10.9135 | 0 | 1.0865 | 323.9135 | 2.2204e-16 | 1.0865
2025-06-06 19:00:00 | 11.7 | 0.81001 | 0 | 0 | 323.9135 | 10.89 | 10.89
2025-06-06 20:00:00 | 12.24 | 0 | 0 | 0 | 323.9135 | 12.24 | 12.24
2025-06-06 21:00:00 | 11.82 | 0 | 0 | 0 | 323.9135 | 11.82 | 11.82
2025-06-06 22:00:00 | 12 | 0 | 0 | 0 | 323.9135 | 12 | 12
2025-06-06 23:00:00 | 12.36 | 0 | 0 | 0 | 323.9135 | 12.36 | 12.36
2025-06-07 00:00:00 | 12.42 | 0 | 0 | 0 | 323.9135 | 12.42 | 12.42
2025-06-07 01:00:00 | 12.24 | 0 | 0 | 0 | 323.9135 | 12.24 | 12.24
2025-06-07 02:00:00 | 11.94 | 0 | 0 | 0 | 323.9135 | 11.94 | 11.94
2025-06-07 03:00:00 | 12.06 | 0 | 0 | 0 | 323.9135 | 12.06 | 12.06
2025-06-07 04:00:00 | 12.18 | 0.88981 | 0 | 0 | 323.9135 | 11.2902 | 11.2902
2025-06-07 05:00:00 | 12.18 | 10.9858 | 0 | 0 | 323.9135 | 1.1942 | 1.1942
2025-06-07 06:00:00 | 11.94 | 21.438 | 0 | 0 | 323.9135 | -9.498 | -9.498
2025-06-07 07:00:00 | 11.88 | 31.534 | 0 | 0 | 323.9135 | -19.654 | -19.654
2025-06-07 08:00:00 | 11.94 | 40.5858 | 0 | 0 | 323.9135 | -28.6458 | -28.6458
2025-06-07 09:00:00 | 11.64 | 47.9766 | 0 | 0 | 323.9135 | -36.3366 | -36.3366
2025-06-07 10:00:00 | 11.22 | 53.2026 | 0 | 0 | 323.9135 | -41.9826 | -41.9826
2025-06-07 11:00:00 | 5.04 | 55.9079 | 0 | 0 | 323.9135 | -50.8679 | -50.8679
2025-06-07 12:00:00 | 17.46 | 55.9079 | 0 | 0 | 323.9135 | -38.4479 | -38.4479
2025-06-07 13:00:00 | 7.8 | 53.2026 | 0 | 0 | 323.9135 | -45.4026 | -45.4026
2025-06-07 14:00:00 | 5.16 | 47.9766 | 0 | 0 | 323.9135 | -42.8166 | -42.8166
2025-06-07 15:00:00 | 5.16 | 40.5858 | 0 | 0 | 323.9135 | -35.4258 | -35.4258
2025-06-07 16:00:00 | 5.22 | 31.534 | 0 | 0 | 323.9135 | -26.314 | -26.314
2025-06-07 17:00:00 | 5.34 | 21.438 | 0 | 0 | 323.9135 | -16.098 | -16.098
2025-06-07 18:00:00 | 5.34 | 10.9858 | 0 | 0 | 323.9135 | -5.6458 | -5.6458
2025-06-07 19:00:00 | 5.04 | 0.88981 | 0 | 0 | 323.9135 | 4.1502 | 4.1502
2025-06-07 20:00:00 | 5.28 | 0 | 0 | 0 | 323.9135 | 5.28 | 5.28
2025-06-07 21:00:00 | 5.22 | 0 | 0 | 0 | 323.9135 | 5.22 | 5.22
2025-06-07 22:00:00 | 5.52 | 0 | 0 | 0 | 323.9135 | 5.52 | 5.52
2025-06-07 23:00:00 | 5.46 | 0 | 0 | 0 | 323.9135 | 5.46 | 5.46
2025-06-08 00:00:00 | 5.64 | 0 | 0 | 0 | 323.9135 | 5.64 | 5.64
2025-06-08 01:00:00 | 5.52 | 0 | 0 | 0 | 323.9135 | 5.52 | 5.52
2025-06-08 02:00:00 | 5.94 | 0 | 0 | 0 | 323.9135 | 5.94 | 5.94
2025-06-08 03:00:00 | 5.82 | 0 | 0 | 0 | 323.9135 | 5.82 | 5.82
2025-06-08 04:00:00 | 5.4 | 0.9643 | 0 | 0 | 323.9135 | 4.4357 | 4.4357
2025-06-08 05:00:00 | 5.76 | 11.0533 | 0 | 0 | 323.9135 | -5.2933 | -5.2933
2025-06-08 06:00:00 | 5.46 | 21.4982 | 0 | 0 | 323.9135 | -16.0382 | -16.0382
2025-06-08 07:00:00 | 5.4 | 31.5872 | 0 | 0 | 323.9135 | -26.1872 | -26.1872
2025-06-08 08:00:00 | 5.7 | 40.6327 | 0 | 0 | 323.9135 | -34.9327 | -34.9327
2025-06-08 09:00:00 | 5.04 | 48.0184 | 0 | 0 | 323.9135 | -42.9784 | -42.9784
2025-06-08 10:00:00 | 5.1 | 53.2408 | 0 | 0 | 323.9135 | -48.1408 | -48.1408
2025-06-08 11:00:00 | 5.22 | 55.9442 | 0 | 0 | 323.9135 | -50.7242 | -50.7242
2025-06-08 12:00:00 | 5.46 | 55.9442 | 0 | 0 | 323.9135 | -50.4842 | -50.4842
2025-06-08 13:00:00 | 5.34 | 53.2408 | 0 | 0 | 323.9135 | -47.9008 | -47.9008
2025-06-08 14:00:00 | 4.98 | 48.0184 | 0 | 0 | 323.9135 | -43.0384 | -43.0384
2025-06-08 15:00:00 | 5.28 | 40.6327 | 0 | 0 | 323.9135 | -35.3527 | -35.3527
2025-06-08 16:00:00 | 5.16 | 31.5872 | 0 | 0 | 323.9135 | -26.4272 | -26.4272
2025-06-08 17:00:00 | 5.22 | 21.4982 | 0 | 0 | 323.9135 | -16.2782 | -16.2782
2025-06-08 18:00:00 | 9.18 | 11.0533 | 0 | 0 | 323.9135 | -1.8733 | -1.8733
2025-06-08 19:00:00 | 11.76 | 0.9643 | 0 | 0 | 323.9135 | 10.7957 | 10.7957
2025-06-08 20:00:00 | 11.82 | 0 | 0 | 0 | 323.9135 | 11.82 | 11.82
2025-06-08 21:00:00 | 11.82 | 0 | 0 | 0 | 323.9135 | 11.82 | 11.82
2025-06-08 22:00:00 | 12.12 | 0 | 0 | 0 | 323.9135 | 12.12 | 12.12
2025-06-08 23:00:00 | 12.18 | 0 | 0 | 0 | 323.9135 | 12.18 | 12.18
2025-06-09 00:00:00 | 12.18 | 0 | 0 | 0 | 323.9135 | 12.18 | 12.18
2025-06-09 01:00:00 | 12 | 0 | 0 | 0 | 323.9135 | 12 | 12
2025-06-09 02:00:00 | 12.54 | 0 | 0 | 0 | 323.9135 | 12.54 | 12.54
2025-06-09 03:00:00 | 12.48 | 0 | 0 | 0 | 323.9135 | 12.48 | 12.48
2025-06-09 04:00:00 | 12.18 | 1.0335 | 0 | 0 | 323.9135 | 11.1465 | 11.1465
2025-06-09 05:00:00 | 11.82 | 11.1159 | 0 | 0 | 323.9135 | 0.70408 | 0.70408
2025-06-09 06:00:00 | 12.12 | 21.5541 | 0 | 0 | 323.9135 | -9.4341 | -9.4341
2025-06-09 07:00:00 | 7.56 | 31.6365 | 0 | 0 | 323.9135 | -24.0765 | -24.0765
2025-06-09 08:00:00 | 7.44 | 40.6762 | 0 | 0 | 323.9135 | -33.2362 | -33.2362
2025-06-09 09:00:00 | 7.32 | 48.0571 | 0 | 0 | 323.9135 | -40.7371 | -40.7371
2025-06-09 10:00:00 | 7.14 | 53.2761 | 0 | 0 | 323.9135 | -46.1361 | -46.1361
2025-06-09 11:00:00 | 7.26 | 55.9777 | 0 | 0 | 323.9135 | -48.7177 | -48.7177
2025-06-09 12:00:00 | 7.08 | 55.9777 | 0 | 0 | 323.9135 | -48.8977 | -48.8977
2025-06-09 13:00:00 | 7.08 | 53.2761 | 0 | 0 | 323.9135 | -46.1961 | -46.1961
2025-06-09 14:00:00 | 7.08 | 48.0571 | 0 | 0 | 323.9135 | -40.9771 | -40.9771
2025-06-09 15:00:00 | 6.48 | 40.6762 | 0 | 0 | 323.9135 | -34.1962 | -34.1962
2025-06-09 16:00:00 | 5.1 | 31.6365 | 0 | 0 | 323.9135 | -26.5365 | -26.5365
2025-06-09 17:00:00 | 5.34 | 21.5541 | 0 | 0 | 323.9135 | -16.2141 | -16.2141
2025-06-09 18:00:00 | 5.22 | 11.1159 | 0 | 0 | 323.9135 | -5.8959 | -5.8959
2025-06-09 19:00:00 | 5.1 | 1.0335 | 0 | 0 | 323.9135 | 4.0665 | 4.0665
2025-06-09 20:00:00 | 5.34 | 0 | 0 | 0 | 323.9135 | 5.34 | 5.34
2025-06-09 21:00:00 | 5.28 | 0 | 0 | 0 | 323.9135 | 5.28 | 5.28
2025-06-09 22:00:00 | 5.64 | 0 | 0 | 0 | 323.9135 | 5.64 | 5.64
2025-06-09 23:00:00 | 5.46 | 0 | 0 | 0 | 323.9135 | 5.46 | 5.46
2025-06-10 00:00:00 | 5.58 | 0 | 0 | 0 | 323.9135 | 5.58 | 5.58
2025-06-10 01:00:00 | 5.88 | 0 | 0 | 0 | 323.9135 | 5.88 | 5.88
2025-06-10 02:00:00 | 5.58 | 0 | 0 | 0 | 323.9135 | 5.58 | 5.58
2025-06-10 03:00:00 | 5.88 | 0 | 0 | 0 | 323.9135 | 5.88 | 5.88
2025-06-10 04:00:00 | 5.34 | 1.0973 | 0 | 0 | 323.9135 | 4.2427 | 4.2427
2025-06-10 05:00:00 | 6.12 | 11.1737 | 0 | 0 | 323.9135 | -5.0537 | -5.0537
2025-06-10 06:00:00 | 6.3 | 21.6056 | 0 | 0 | 323.9135 | -15.3056 | -15.3056
2025-06-10 07:00:00 | 6.48 | 31.682 | 0 | 0 | 323.9135 | -25.202 | -25.202
2025-06-10 08:00:00 | 6.66 | 40.7162 | 0 | 0 | 323.9135 | -34.0562 | -34.0562
2025-06-10 09:00:00 | 6.78 | 48.0927 | 0 | 0 | 323.9135 | -41.3127 | -41.3127
2025-06-10 10:00:00 | 6.9 | 53.3086 | 0 | 0 | 323.9135 | -46.4086 | -46.4086
2025-06-10 11:00:00 | 6.48 | 56.0086 | 0 | 0 | 323.9135 | -49.5286 | -49.5286
2025-06-10 12:00:00 | 6.54 | 56.0086 | 0 | 0 | 323.9135 | -49.4686 | -49.4686
2025-06-10 13:00:00 | 6.12 | 53.3086 | 0 | 0 | 323.9135 | -47.1886 | -47.1886
2025-06-10 14:00:00 | 6.42 | 48.0927 | 0 | 0 | 323.9135 | -41.6727 | -41.6727
2025-06-10 15:00:00 | 6 | 40.7162 | 0 | 0 | 323.9135 | -34.7162 | -34.7162
2025-06-10 16:00:00 | 5.16 | 31.682 | 0 | 0 | 323.9135 | -26.522 | -26.522
2025-06-10 17:00:00 | 5.46 | 21.6056 | 0 | 0 | 323.9135 | -16.1456 | -16.1456
2025-06-10 18:00:00 | 5.46 | 11.1737 | 0 | 0 | 323.9135 | -5.7137 | -5.7137
2025-06-10 19:00:00 | 5.4 | 1.0973 | 0 | 0 | 323.9135 | 4.3027 | 4.3027
2025-06-10 20:00:00 | 5.82 | 0 | 0 | 0 | 323.9135 | 5.82 | 5.82
2025-06-10 21:00:00 | 5.22 | 0 | 0 | 0 | 323.9135 | 5.22 | 5.22
2025-06-10 22:00:00 | 5.52 | 0 | 0 | 0 | 323.9135 | 5.52 | 5.52
2025-06-10 23:00:00 | 6.78 | 0 | 0 | 0 | 323.9135 | 6.78 | 6.78
2025-06-11 00:00:00 | 6 | 0 | 0 | 0 | 323.9135 | 6 | 6
2025-06-11 01:00:00 | 5.58 | 0 | 0 | 0 | 323.9135 | 5.58 | 5.58
2025-06-11 02:00:00 | 5.64 | 0 | 0 | 0 | 323.9135 | 5.64 | 5.64
2025-06-11 03:00:00 | 5.82 | 0 | 0 | 0 | 323.9135 | 5.82 | 5.82
2025-06-11 04:00:00 | 5.88 | 1.1557 | 0 | 0 | 323.9135 | 4.7243 | 4.7243
2025-06-11 05:00:00 | 5.34 | 11.2266 | 0 | 0 | 323.9135 | -5.8866 | -5.8866
2025-06-11 06:00:00 | 7.44 | 21.6527 | 0 | 0 | 323.9135 | -14.2127 | -14.2127
2025-06-11 07:00:00 | 7.32 | 31.7235 | 0 | 0 | 323.9135 | -24.4035 | -24.4035
2025-06-11 08:00:00 | 7.38 | 40.7528 | 0 | 0 | 323.9135 | -33.3728 | -33.3728
2025-06-11 09:00:00 | 7.68 | 48.1252 | 0 | 0 | 323.9135 | -40.4452 | -40.4452
2025-06-11 10:00:00 | 7.5 | 53.3383 | 0 | 0 | 323.9135 | -45.8383 | -45.8383
2025-06-11 11:00:00 | 7.44 | 56.0367 | 0 | 0 | 323.9135 | -48.5967 | -48.5967
2025-06-11 12:00:00 | 7.86 | 56.0367 | 0 | 0 | 323.9135 | -48.1767 | -48.1767
2025-06-11 13:00:00 | 8.04 | 53.3383 | 0 | 0 | 323.9135 | -45.2983 | -45.2983
2025-06-11 14:00:00 | 7.08 | 48.1252 | 0 | 0 | 323.9135 | -41.0452 | -41.0452
2025-06-11 15:00:00 | 6.66 | 40.7528 | 0 | 0 | 323.9135 | -34.0928 | -34.0928
2025-06-11 16:00:00 | 5.46 | 31.7235 | 0 | 0 | 323.9135 | -26.2635 | -26.2635
2025-06-11 17:00:00 | 5.16 | 21.6527 | 0 | 0 | 323.9135 | -16.4927 | -16.4927
2025-06-11 18:00:00 | 5.1 | 11.2266 | 0 | 0 | 323.9135 | -6.1266 | -6.1266
2025-06-11 19:00:00 | 5.52 | 1.1557 | 0 | 0 | 323.9135 | 4.3643 | 4.3643
2025-06-11 20:00:00 | 5.16 | 0 | 0 | 0 | 323.9135 | 5.16 | 5.16
2025-06-11 21:00:00 | 14.28 | 0 | 0 | 0 | 323.9135 | 14.28 | 14.28
2025-06-11 22:00:00 | 19.98 | 0 | 0 | 0 | 323.9135 | 19.98 | 19.98
2025-06-11 23:00:00 | 19.8 | 0 | 0 | 0 | 323.9135 | 19.8 | 19.8
2025-06-12 00:00:00 | 19.92 | 0 | 0 | 0 | 323.9135 | 19.92 | 19.92
2025-06-12 01:00:00 | 19.86 | 0 | 0 | 0 | 323.9135 | 19.86 | 19.86
2025-06-12 02:00:00 | 20.4 | 0 | 0 | 0 | 323.9135 | 20.4 | 20.4
2025-06-12 03:00:00 | 20.1 | 0 | 0 | 0 | 323.9135 | 20.1 | 20.1
2025-06-12 04:00:00 | 17.04 | 1.2088 | 0 | 0 | 323.9135 | 15.8312 | 15.8312
2025-06-12 05:00:00 | 5.4 | 11.2746 | 0 | 0 | 323.9135 | -5.8746 | -5.8746
2025-06-12 06:00:00 | 6.42 | 21.6955 | 0 | 0 | 323.9135 | -15.2755 | -15.2755
2025-06-12 07:00:00 | 7.26 | 31.7613 | 0 | 0 | 323.9135 | -24.5013 | -24.5013
2025-06-12 08:00:00 | 7.32 | 40.786 | 0 | 0 | 323.9135 | -33.466 | -33.466
2025-06-12 09:00:00 | 7.32 | 48.1547 | 0 | 0 | 323.9135 | -40.8347 | -40.8347
2025-06-12 10:00:00 | 7.02 | 53.3651 | 0 | 0 | 323.9135 | -46.3451 | -46.3451
2025-06-12 11:00:00 | 6.6 | 56.0622 | 0 | 0 | 323.9135 | -49.4622 | -49.4622
2025-06-12 12:00:00 | 6.84 | 56.0622 | 0 | 0 | 323.9135 | -49.2222 | -49.2222
2025-06-12 13:00:00 | 7.08 | 53.3651 | 0 | 0 | 323.9135 | -46.2851 | -46.2851
2025-06-12 14:00:00 | 6.48 | 48.1547 | 0 | 0 | 323.9135 | -41.6747 | -41.6747
2025-06-12 15:00:00 | 5.28 | 40.786 | 0 | 0 | 323.9135 | -35.506 | -35.506
2025-06-12 16:00:00 | 4.56 | 31.7613 | 0 | 0 | 323.9135 | -27.2013 | -27.2013
2025-06-12 17:00:00 | 4.98 | 21.6955 | 0 | 0 | 323.9135 | -16.7155 | -16.7155
2025-06-12 18:00:00 | 4.5 | 11.2746 | 0 | 0 | 323.9135 | -6.7746 | -6.7746
2025-06-12 19:00:00 | 4.74 | 1.2088 | 0 | 0 | 323.9135 | 3.5312 | 3.5312
2025-06-12 20:00:00 | 4.8 | 0 | 0 | 0 | 323.9135 | 4.8 | 4.8
2025-06-12 21:00:00 | 4.92 | 0 | 0 | 0 | 323.9135 | 4.92 | 4.92
2025-06-12 22:00:00 | 5.04 | 0 | 0 | 0 | 323.9135 | 5.04 | 5.04
2025-06-12 23:00:00 | 5.28 | 0 | 0 | 0 | 323.9135 | 5.28 | 5.28
2025-06-13 00:00:00 | 4.98 | 0 | 0 | 0 | 323.9135 | 4.98 | 4.98
2025-06-13 01:00:00 | 5.22 | 0 | 0 | 0 | 323.9135 | 5.22 | 5.22
2025-06-13 02:00:00 | 5.52 | 0 | 0 | 0 | 323.9135 | 5.52 | 5.52
2025-06-13 03:00:00 | 5.28 | 0 | 0 | 0 | 323.9135 | 5.28 | 5.28
2025-06-13 04:00:00 | 5.58 | 1.2564 | 0 | 0 | 323.9135 | 4.3236 | 4.3236
2025-06-13 05:00:00 | 5.1 | 11.3177 | 0 | 0 | 323.9135 | -6.2177 | -6.2177
2025-06-13 06:00:00 | 6.84 | 21.7338 | 0 | 0 | 323.9135 | -14.8938 | -14.8938
2025-06-13 07:00:00 | 6.9 | 31.7951 | 0 | 0 | 323.9135 | -24.8951 | -24.8951
2025-06-13 08:00:00 | 6.54 | 40.8157 | 0 | 0 | 323.9135 | -34.2757 | -34.2757
2025-06-13 09:00:00 | 6.9 | 48.1811 | 0 | 0 | 323.9135 | -41.2811 | -41.2811
2025-06-13 10:00:00 | 6.36 | 53.3892 | 0 | 0 | 323.9135 | -47.0292 | -47.0292
2025-06-13 11:00:00 | 6.48 | 56.0851 | 0 | 0 | 323.9135 | -49.6051 | -49.6051
2025-06-13 12:00:00 | 6.78 | 56.0851 | 0 | 0 | 323.9135 | -49.3051 | -49.3051
2025-06-13 13:00:00 | 6.72 | 53.3892 | 0 | 0 | 323.9135 | -46.6692 | -46.6692
2025-06-13 14:00:00 | 5.88 | 48.1811 | 0 | 0 | 323.9135 | -42.3011 | -42.3011
2025-06-13 15:00:00 | 5.28 | 40.8157 | 0 | 0 | 323.9135 | -35.5357 | -35.5357
2025-06-13 16:00:00 | 9.3 | 31.7951 | 0 | 0 | 323.9135 | -22.4951 | -22.4951
2025-06-13 17:00:00 | 11.52 | 21.7338 | 0 | 0 | 323.9135 | -10.2138 | -10.2138
2025-06-13 18:00:00 | 11.28 | 11.3177 | 0 | 0 | 323.9135 | -0.037674 | -0.037674
2025-06-13 19:00:00 | 11.7 | 1.2564 | 0 | 0 | 323.9135 | 10.4436 | 10.4436
2025-06-13 20:00:00 | 11.4 | 0 | 0 | 0 | 323.9135 | 11.4 | 11.4
2025-06-13 21:00:00 | 11.82 | 0 | 0 | 0 | 323.9135 | 11.82 | 11.82
2025-06-13 22:00:00 | 11.76 | 0 | 0 | 0 | 323.9135 | 11.76 | 11.76
2025-06-13 23:00:00 | 12.06 | 0 | 0 | 0 | 323.9135 | 12.06 | 12.06
2025-06-14 00:00:00 | 11.88 | 0 | 0 | 0 | 323.9135 | 11.88 | 11.88
2025-06-14 01:00:00 | 11.88 | 0 | 0 | 0 | 323.9135 | 11.88 | 11.88
2025-06-14 02:00:00 | 11.7 | 0 | 0 | 0 | 323.9135 | 11.7 | 11.7
2025-06-14 03:00:00 | 12.12 | 0 | 0 | 0 | 323.9135 | 12.12 | 12.12
2025-06-14 04:00:00 | 12.3 | 1.2987 | 0 | 0 | 323.9135 | 11.0013 | 11.0013
2025-06-14 05:00:00 | 11.64 | 11.3559 | 0 | 0 | 323.9135 | 0.28413 | 0.28413
2025-06-14 06:00:00 | 11.76 | 21.7678 | 0 | 0 | 323.9135 | -10.0078 | -10.0078
2025-06-14 07:00:00 | 12.06 | 31.825 | 0 | 0 | 323.9135 | -19.765 | -19.765
2025-06-14 08:00:00 | 11.52 | 40.8421 | 0 | 0 | 323.9135 | -29.3221 | -29.3221
2025-06-14 09:00:00 | 11.82 | 48.2044 | 0 | 0 | 323.9135 | -36.3844 | -36.3844
2025-06-14 10:00:00 | 11.28 | 53.4104 | 0 | 0 | 323.9135 | -42.1304 | -42.1304
2025-06-14 11:00:00 | 6.18 | 56.1053 | 0 | 0 | 323.9135 | -49.9253 | -49.9253
2025-06-14 12:00:00 | 4.68 | 56.1053 | 0 | 0 | 323.9135 | -51.4253 | -51.4253
2025-06-14 13:00:00 | 4.68 | 53.4104 | 0 | 0 | 323.9135 | -48.7304 | -48.7304
2025-06-14 14:00:00 | 4.98 | 48.2044 | 0 | 0 | 323.9135 | -43.2244 | -43.2244
2025-06-14 15:00:00 | 4.56 | 40.8421 | 0 | 0 | 323.9135 | -36.2821 | -36.2821
2025-06-14 16:00:00 | 4.92 | 31.825 | 0 | 0 | 323.9135 | -26.905 | -26.905
2025-06-14 17:00:00 | 4.68 | 21.7678 | 0 | 0 | 323.9135 | -17.0878 | -17.0878
2025-06-14 18:00:00 | 4.74 | 11.3559 | 0 | 0 | 323.9135 | -6.6159 | -6.6159
2025-06-14 19:00:00 | 4.74 | 1.2987 | 0 | 0 | 323.9135 | 3.4413 | 3.4413
2025-06-14 20:00:00 | 4.8 | 0 | 0 | 0 | 323.9135 | 4.8 | 4.8
2025-06-14 21:00:00 | 5.04 | 0 | 0 | 0 | 323.9135 | 5.04 | 5.04
2025-06-14 22:00:00 | 5.1 | 0 | 0 | 0 | 323.9135 | 5.1 | 5.1
2025-06-14 23:00:00 | 5.34 | 0 | 0 | 0 | 323.9135 | 5.34 | 5.34
2025-06-15 00:00:00 | 5.04 | 0 | 0 | 0 | 323.9135 | 5.04 | 5.04
2025-06-15 01:00:00 | 5.52 | 0 | 0 | 0 | 323.9135 | 5.52 | 5.52
2025-06-15 02:00:00 | 5.16 | 0 | 0 | 0 | 323.9135 | 5.16 | 5.16
2025-06-15 03:00:00 | 5.58 | 0 | 0 | 0 | 323.9135 | 5.58 | 5.58
2025-06-15 04:00:00 | 5.22 | 1.3355 | 0 | 0 | 323.9135 | 3.8845 | 3.8845
2025-06-15 05:00:00 | 5.4 | 11.3892 | 0 | 0 | 323.9135 | -5.9892 | -5.9892
2025-06-15 06:00:00 | 5.28 | 21.7975 | 0 | 0 | 323.9135 | -16.5175 | -16.5175
2025-06-15 07:00:00 | 5.04 | 31.8511 | 0 | 0 | 323.9135 | -26.8111 | -26.8111
2025-06-15 08:00:00 | 4.8 | 40.865 | 0 | 0 | 323.9135 | -36.065 | -36.065
2025-06-15 09:00:00 | 4.86 | 48.2248 | 0 | 0 | 323.9135 | -43.3648 | -43.3648
2025-06-15 10:00:00 | 4.86 | 53.4289 | 0 | 0 | 323.9135 | -48.5689 | -48.5689
2025-06-15 11:00:00 | 18 | 56.1228 | 0 | 0 | 323.9135 | -38.1228 | -38.1228
2025-06-15 12:00:00 | 18.72 | 56.1228 | 0 | 0 | 323.9135 | -37.4028 | -37.4028
2025-06-15 13:00:00 | 19.02 | 53.4289 | 0 | 0 | 323.9135 | -34.4089 | -34.4089
2025-06-15 14:00:00 | 19.62 | 48.2248 | 0 | 0 | 323.9135 | -28.6048 | -28.6048
2025-06-15 15:00:00 | 19.44 | 40.865 | 0 | 0 | 323.9135 | -21.425 | -21.425
2025-06-15 16:00:00 | 18.9 | 31.8511 | 0 | 0 | 323.9135 | -12.9511 | -12.9511
2025-06-15 17:00:00 | 18.9 | 21.7975 | 0 | 0 | 323.9135 | -2.8975 | -2.8975
2025-06-15 18:00:00 | 5.46 | 11.3892 | 0 | 0 | 323.9135 | -5.9292 | -5.9292
2025-06-15 19:00:00 | 5.22 | 1.3355 | 0 | 0 | 323.9135 | 3.8845 | 3.8845
2025-06-15 20:00:00 | 5.1 | 0 | 0 | 0 | 323.9135 | 5.1 | 5.1
2025-06-15 21:00:00 | 5.16 | 0 | 0 | 0 | 323.9135 | 5.16 | 5.16
2025-06-15 22:00:00 | 5.16 | 0 | 0 | 0 | 323.9135 | 5.16 | 5.16
2025-06-15 23:00:00 | 5.22 | 0 | 0 | 0 | 323.9135 | 5.22 | 5.22
2025-06-16 00:00:00 | 5.58 | 0 | 0 | 0 | 323.9135 | 5.58 | 5.58
2025-06-16 01:00:00 | 5.4 | 0 | 0 | 0 | 323.9135 | 5.4 | 5.4
2025-06-16 02:00:00 | 5.46 | 0 | 0 | 0 | 323.9135 | 5.46 | 5.46
2025-06-16 03:00:00 | 5.34 | 0 | 0 | 0 | 323.9135 | 5.34 | 5.34
2025-06-16 04:00:00 | 5.7 | 1.3669 | 0 | 0 | 323.9135 | 4.3331 | 4.3331
2025-06-16 05:00:00 | 5.7 | 11.4175 | 0 | 0 | 323.9135 | -5.7175 | -5.7175
2025-06-16 06:00:00 | 5.34 | 21.8227 | 0 | 0 | 323.9135 | -16.4827 | -16.4827
2025-06-16 07:00:00 | 6.48 | 31.8733 | 0 | 0 | 323.9135 | -25.3933 | -25.3933
2025-06-16 08:00:00 | 6.66 | 40.8845 | 0 | 0 | 323.9135 | -34.2245 | -34.2245
2025-06-16 09:00:00 | 6.84 | 48.2421 | 0 | 0 | 323.9135 | -41.4021 | -41.4021
2025-06-16 10:00:00 | 6.78 | 53.4447 | 0 | 0 | 323.9135 | -46.6647 | -46.6647
2025-06-16 11:00:00 | 7.26 | 56.1377 | 0 | 0 | 323.9135 | -48.8777 | -48.8777
2025-06-16 12:00:00 | 7.2 | 56.1377 | 0 | 0 | 323.9135 | -48.9377 | -48.9377
2025-06-16 13:00:00 | 7.08 | 53.4447 | 0 | 0 | 323.9135 | -46.3647 | -46.3647
2025-06-16 14:00:00 | 6.48 | 48.2421 | 0 | 0 | 323.9135 | -41.7621 | -41.7621
2025-06-16 15:00:00 | 7.08 | 40.8845 | 0 | 0 | 323.9135 | -33.8045 | -33.8045
2025-06-16 16:00:00 | 5.94 | 31.8733 | 0 | 0 | 323.9135 | -25.9333 | -25.9333
2025-06-16 17:00:00 | 5.52 | 21.8227 | 0 | 0 | 323.9135 | -16.3027 | -16.3027
2025-06-16 18:00:00 | 5.22 | 11.4175 | 0 | 0 | 323.9135 | -6.1975 | -6.1975
2025-06-16 19:00:00 | 5.16 | 1.3669 | 0 | 0 | 323.9135 | 3.7931 | 3.7931
2025-06-16 20:00:00 | 5.58 | 0 | 0 | 0 | 323.9135 | 5.58 | 5.58
2025-06-16 21:00:00 | 5.16 | 0 | 0 | 0 | 323.9135 | 5.16 | 5.16
2025-06-16 22:00:00 | 5.34 | 0 | 0 | 0 | 323.9135 | 5.34 | 5.34
2025-06-16 23:00:00 | 5.28 | 0 | 0 | 0 | 323.9135 | 5.28 | 5.28
2025-06-17 00:00:00 | 5.34 | 0 | 0 | 0 | 323.9135 | 5.34 | 5.34
2025-06-17 01:00:00 | 5.1 | 0 | 0 | 0 | 323.9135 | 5.1 | 5.1
2025-06-17 02:00:00 | 5.04 | 0 | 0 | 0 | 323.9135 | 5.04 | 5.04
2025-06-17 03:00:00 | 5.58 | 0 | 0 | 0 | 323.9135 | 5.58 | 5.58
2025-06-17 04:00:00 | 5.7 | 1.3928 | 0 | 0 | 323.9135 | 4.3072 | 4.3072
2025-06-17 05:00:00 | 5.28 | 11.441 | 0 | 0 | 323.9135 | -6.161 | -6.161
2025-06-17 06:00:00 | 6 | 21.8436 | 0 | 0 | 323.9135 | -15.8436 | -15.8436
2025-06-17 07:00:00 | 5.94 | 31.8917 | 0 | 0 | 323.9135 | -25.9517 | -25.9517
2025-06-17 08:00:00 | 6.36 | 40.9006 | 0 | 0 | 323.9135 | -34.5406 | -34.5406
2025-06-17 09:00:00 | 6.96 | 48.2564 | 0 | 0 | 323.9135 | -41.2964 | -41.2964
2025-06-17 10:00:00 | 6.66 | 53.4577 | 0 | 0 | 323.9135 | -46.7977 | -46.7977
2025-06-17 11:00:00 | 6.6 | 56.1501 | 0 | 0 | 323.9135 | -49.5501 | -49.5501
2025-06-17 12:00:00 | 6.48 | 56.1501 | 0 | 0 | 323.9135 | -49.6701 | -49.6701
2025-06-17 13:00:00 | 6.48 | 53.4577 | 0 | 0 | 323.9135 | -46.9777 | -46.9777
2025-06-17 14:00:00 | 6.42 | 48.2564 | 0 | 0 | 323.9135 | -41.8364 | -41.8364
2025-06-17 15:00:00 | 5.94 | 40.9006 | 0 | 0 | 323.9135 | -34.9606 | -34.9606
2025-06-17 16:00:00 | 4.5 | 31.8917 | 0 | 0 | 323.9135 | -27.3917 | -27.3917
2025-06-17 17:00:00 | 3.6 | 21.8436 | 0 | 0 | 323.9135 | -18.2436 | -18.2436
2025-06-17 18:00:00 | 4.26 | 11.441 | 0 | 0 | 323.9135 | -7.181 | -7.181
2025-06-17 19:00:00 | 3.54 | 1.3928 | 0 | 0 | 323.9135 | 2.1472 | 2.1472
2025-06-17 20:00:00 | 4.14 | 0 | 0 | 0 | 323.9135 | 4.14 | 4.14
2025-06-17 21:00:00 | 3.72 | 0 | 0 | 0 | 323.9135 | 3.72 | 3.72
2025-06-17 22:00:00 | 3.48 | 0 | 0 | 0 | 323.9135 | 3.48 | 3.48
2025-06-17 23:00:00 | 3.84 | 0 | 0 | 0 | 323.9135 | 3.84 | 3.84
2025-06-18 00:00:00 | 3.9 | 0 | 0 | 0 | 323.9135 | 3.9 | 3.9
2025-06-18 01:00:00 | 3.36 | 0 | 0 | 0 | 323.9135 | 3.36 | 3.36
2025-06-18 02:00:00 | 3.72 | 0 | 0 | 0 | 323.9135 | 3.72 | 3.72
2025-06-18 03:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-18 04:00:00 | 3.78 | 1.4133 | 0 | 0 | 323.9135 | 2.3667 | 2.3667
2025-06-18 05:00:00 | 3.3 | 11.4595 | 0 | 0 | 323.9135 | -8.1595 | -8.1595
2025-06-18 06:00:00 | 5.04 | 21.86 | 0 | 0 | 323.9135 | -16.82 | -16.82
2025-06-18 07:00:00 | 5.94 | 31.9062 | 0 | 0 | 323.9135 | -25.9662 | -25.9662
2025-06-18 08:00:00 | 6.12 | 40.9133 | 0 | 0 | 323.9135 | -34.7933 | -34.7933
2025-06-18 09:00:00 | 6.24 | 48.2676 | 0 | 0 | 323.9135 | -42.0276 | -42.0276
2025-06-18 10:00:00 | 6.6 | 53.4679 | 0 | 0 | 323.9135 | -46.8679 | -46.8679
2025-06-18 11:00:00 | 6.48 | 56.1598 | 0 | 0 | 323.9135 | -49.6798 | -49.6798
2025-06-18 12:00:00 | 6.78 | 56.1598 | 0 | 0 | 323.9135 | -49.3798 | -49.3798
2025-06-18 13:00:00 | 6.6 | 53.4679 | 0 | 0 | 323.9135 | -46.8679 | -46.8679
2025-06-18 14:00:00 | 5.76 | 48.2676 | 0 | 0 | 323.9135 | -42.5076 | -42.5076
2025-06-18 15:00:00 | 5.58 | 40.9133 | 0 | 0 | 323.9135 | -35.3333 | -35.3333
2025-06-18 16:00:00 | 3.84 | 31.9062 | 0 | 0 | 323.9135 | -28.0662 | -28.0662
2025-06-18 17:00:00 | 3.24 | 21.86 | 0 | 0 | 323.9135 | -18.62 | -18.62
2025-06-18 18:00:00 | 3.54 | 11.4595 | 0 | 0 | 323.9135 | -7.9195 | -7.9195
2025-06-18 19:00:00 | 3.18 | 1.4133 | 0 | 0 | 323.9135 | 1.7667 | 1.7667
2025-06-18 20:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-18 21:00:00 | 3.48 | 0 | 0 | 0 | 323.9135 | 3.48 | 3.48
2025-06-18 22:00:00 | 3.18 | 0 | 0 | 0 | 323.9135 | 3.18 | 3.18
2025-06-18 23:00:00 | 3.24 | 0 | 0 | 0 | 323.9135 | 3.24 | 3.24
2025-06-19 00:00:00 | 3.48 | 0 | 0 | 0 | 323.9135 | 3.48 | 3.48
2025-06-19 01:00:00 | 3.36 | 0 | 0 | 0 | 323.9135 | 3.36 | 3.36
2025-06-19 02:00:00 | 3.3 | 0 | 0 | 0 | 323.9135 | 3.3 | 3.3
2025-06-19 03:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-19 04:00:00 | 3.42 | 1.4283 | 0 | 0 | 323.9135 | 1.9917 | 1.9917
2025-06-19 05:00:00 | 3.66 | 11.473 | 0 | 0 | 323.9135 | -7.813 | -7.813
2025-06-19 06:00:00 | 4.92 | 21.8721 | 0 | 0 | 323.9135 | -16.9521 | -16.9521
2025-06-19 07:00:00 | 5.46 | 31.9168 | 0 | 0 | 323.9135 | -26.4568 | -26.4568
2025-06-19 08:00:00 | 5.22 | 40.9227 | 0 | 0 | 323.9135 | -35.7027 | -35.7027
2025-06-19 09:00:00 | 6.18 | 48.2759 | 0 | 0 | 323.9135 | -42.0959 | -42.0959
2025-06-19 10:00:00 | 5.88 | 53.4754 | 0 | 0 | 323.9135 | -47.5954 | -47.5954
2025-06-19 11:00:00 | 5.64 | 56.1669 | 0 | 0 | 323.9135 | -50.5269 | -50.5269
2025-06-19 12:00:00 | 6.12 | 56.1669 | 0 | 0 | 323.9135 | -50.0469 | -50.0469
2025-06-19 13:00:00 | 5.76 | 53.4754 | 0 | 0 | 323.9135 | -47.7154 | -47.7154
2025-06-19 14:00:00 | 5.76 | 48.2759 | 0 | 0 | 323.9135 | -42.5159 | -42.5159
2025-06-19 15:00:00 | 5.58 | 40.9227 | 0 | 0 | 323.9135 | -35.3427 | -35.3427
2025-06-19 16:00:00 | 4.32 | 31.9168 | 0 | 0 | 323.9135 | -27.5968 | -27.5968
2025-06-19 17:00:00 | 3.72 | 21.8721 | 0 | 0 | 323.9135 | -18.1521 | -18.1521
2025-06-19 18:00:00 | 3.42 | 11.473 | 0 | 0 | 323.9135 | -8.053 | -8.053
2025-06-19 19:00:00 | 4.02 | 1.4283 | 0 | 0 | 323.9135 | 2.5917 | 2.5917
2025-06-19 20:00:00 | 4.02 | 0 | 0 | 0 | 323.9135 | 4.02 | 4.02
2025-06-19 21:00:00 | 4.38 | 0 | 0 | 0 | 323.9135 | 4.38 | 4.38
2025-06-19 22:00:00 | 4.08 | 0 | 0 | 0 | 323.9135 | 4.08 | 4.08
2025-06-19 23:00:00 | 4.5 | 0 | 0 | 0 | 323.9135 | 4.5 | 4.5
2025-06-20 00:00:00 | 4.2 | 0 | 0 | 0 | 323.9135 | 4.2 | 4.2
2025-06-20 01:00:00 | 4.56 | 0 | 0 | 0 | 323.9135 | 4.56 | 4.56
2025-06-20 02:00:00 | 4.74 | 0 | 0 | 0 | 323.9135 | 4.74 | 4.74
2025-06-20 03:00:00 | 4.2 | 0 | 0 | 0 | 323.9135 | 4.2 | 4.2
2025-06-20 04:00:00 | 4.2 | 1.4379 | 0 | 0 | 323.9135 | 2.7621 | 2.7621
2025-06-20 05:00:00 | 5.94 | 11.4817 | 0 | 0 | 323.9135 | -5.5417 | -5.5417
2025-06-20 06:00:00 | 6.12 | 21.8798 | 0 | 0 | 323.9135 | -15.7598 | -15.7598
2025-06-20 07:00:00 | 5.88 | 31.9236 | 0 | 0 | 323.9135 | -26.0436 | -26.0436
2025-06-20 08:00:00 | 5.7 | 40.9286 | 0 | 0 | 323.9135 | -35.2286 | -35.2286
2025-06-20 09:00:00 | 5.7 | 48.2812 | 0 | 0 | 323.9135 | -42.5812 | -42.5812
2025-06-20 10:00:00 | 5.46 | 53.4802 | 0 | 0 | 323.9135 | -48.0202 | -48.0202
2025-06-20 11:00:00 | 5.22 | 56.1714 | 0 | 0 | 323.9135 | -50.9514 | -50.9514
2025-06-20 12:00:00 | 6.18 | 56.1714 | 0 | 0 | 323.9135 | -49.9914 | -49.9914
2025-06-20 13:00:00 | 6.06 | 53.4802 | 0 | 0 | 323.9135 | -47.4202 | -47.4202
2025-06-20 14:00:00 | 5.76 | 48.2812 | 0 | 0 | 323.9135 | -42.5212 | -42.5212
2025-06-20 15:00:00 | 4.74 | 40.9286 | 0 | 0 | 323.9135 | -36.1886 | -36.1886
2025-06-20 16:00:00 | 3.6 | 31.9236 | 0 | 0 | 323.9135 | -28.3236 | -28.3236
2025-06-20 17:00:00 | 3.24 | 21.8798 | 0 | 0 | 323.9135 | -18.6398 | -18.6398
2025-06-20 18:00:00 | 3.3 | 11.4817 | 0 | 0 | 323.9135 | -8.1817 | -8.1817
2025-06-20 19:00:00 | 3.36 | 1.4379 | 0 | 0 | 323.9135 | 1.9221 | 1.9221
2025-06-20 20:00:00 | 3.42 | 0 | 0 | 0 | 323.9135 | 3.42 | 3.42
2025-06-20 21:00:00 | 3.36 | 0 | 0 | 0 | 323.9135 | 3.36 | 3.36
2025-06-20 22:00:00 | 3.48 | 0 | 0 | 0 | 323.9135 | 3.48 | 3.48
2025-06-20 23:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-21 00:00:00 | 3.96 | 0 | 0 | 0 | 323.9135 | 3.96 | 3.96
2025-06-21 01:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-21 02:00:00 | 4.38 | 0 | 0 | 0 | 323.9135 | 4.38 | 4.38
2025-06-21 03:00:00 | 4.08 | 0 | 0 | 0 | 323.9135 | 4.08 | 4.08
2025-06-21 04:00:00 | 4.14 | 1.442 | 0 | 0 | 323.9135 | 2.698 | 2.698
2025-06-21 05:00:00 | 3.78 | 11.4854 | 0 | 0 | 323.9135 | -7.7054 | -7.7054
2025-06-21 06:00:00 | 4.08 | 21.8831 | 0 | 0 | 323.9135 | -17.8031 | -17.8031
2025-06-21 07:00:00 | 3.18 | 31.9265 | 0 | 0 | 323.9135 | -28.7465 | -28.7465
2025-06-21 08:00:00 | 3.18 | 40.9311 | 0 | 0 | 323.9135 | -37.7511 | -37.7511
2025-06-21 09:00:00 | 3.36 | 48.2834 | 0 | 0 | 323.9135 | -44.9234 | -44.9234
2025-06-21 10:00:00 | 3.42 | 53.4822 | 0 | 0 | 323.9135 | -50.0622 | -50.0622
2025-06-21 11:00:00 | 3.18 | 56.1734 | 0 | 0 | 323.9135 | -52.9934 | -52.9934
2025-06-21 12:00:00 | 3.24 | 56.1734 | 0 | 0 | 323.9135 | -52.9334 | -52.9334
2025-06-21 13:00:00 | 3.42 | 53.4822 | 0 | 0 | 323.9135 | -50.0622 | -50.0622
2025-06-21 14:00:00 | 3.18 | 48.2834 | 0 | 0 | 323.9135 | -45.1034 | -45.1034
2025-06-21 15:00:00 | 3.42 | 40.9311 | 0 | 0 | 323.9135 | -37.5111 | -37.5111
2025-06-21 16:00:00 | 3.18 | 31.9265 | 0 | 0 | 323.9135 | -28.7465 | -28.7465
2025-06-21 17:00:00 | 3.48 | 21.8831 | 0 | 0 | 323.9135 | -18.4031 | -18.4031
2025-06-21 18:00:00 | 3.36 | 11.4854 | 0 | 0 | 323.9135 | -8.1254 | -8.1254
2025-06-21 19:00:00 | 3.24 | 1.442 | 0 | 0 | 323.9135 | 1.798 | 1.798
2025-06-21 20:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-21 21:00:00 | 3.6 | 0 | 0 | 0 | 323.9135 | 3.6 | 3.6
2025-06-21 22:00:00 | 3.66 | 0 | 0 | 0 | 323.9135 | 3.66 | 3.66
2025-06-21 23:00:00 | 3.18 | 0 | 0 | 0 | 323.9135 | 3.18 | 3.18
2025-06-22 00:00:00 | 3.6 | 0 | 0 | 0 | 323.9135 | 3.6 | 3.6
2025-06-22 01:00:00 | 3.24 | 0 | 0 | 0 | 323.9135 | 3.24 | 3.24
2025-06-22 02:00:00 | 3.78 | 0 | 0 | 0 | 323.9135 | 3.78 | 3.78
2025-06-22 03:00:00 | 3.48 | 0 | 0 | 0 | 323.9135 | 3.48 | 3.48
2025-06-22 04:00:00 | 3.3 | 1.4406 | 0 | 0 | 323.9135 | 1.8594 | 1.8594
2025-06-22 05:00:00 | 3.3 | 11.4842 | 0 | 0 | 323.9135 | -8.1842 | -8.1842
2025-06-22 06:00:00 | 9.36 | 21.882 | 0 | 0 | 323.9135 | -12.522 | -12.522
2025-06-22 07:00:00 | 18 | 31.9255 | 0 | 0 | 323.9135 | -13.9255 | -13.9255
2025-06-22 08:00:00 | 17.88 | 40.9303 | 0 | 0 | 323.9135 | -23.0503 | -23.0503
2025-06-22 09:00:00 | 14.4 | 48.2827 | 0 | 0 | 323.9135 | -33.8827 | -33.8827
2025-06-22 10:00:00 | 18.18 | 53.4816 | 0 | 0 | 323.9135 | -35.3016 | -35.3016
2025-06-22 11:00:00 | 18.12 | 56.1727 | 0 | 0 | 323.9135 | -38.0527 | -38.0527
2025-06-22 12:00:00 | 12.24 | 56.1727 | 0 | 0 | 323.9135 | -43.9327 | -43.9327
2025-06-22 13:00:00 | 13.38 | 53.4816 | 0 | 0 | 323.9135 | -40.1016 | -40.1016
2025-06-22 14:00:00 | 18.48 | 48.2827 | 0 | 0 | 323.9135 | -29.8027 | -29.8027
2025-06-22 15:00:00 | 18.24 | 40.9303 | 0 | 0 | 323.9135 | -22.6903 | -22.6903
2025-06-22 16:00:00 | 5.34 | 31.9255 | 0 | 0 | 323.9135 | -26.5855 | -26.5855
2025-06-22 17:00:00 | 4.2 | 21.882 | 0 | 0 | 323.9135 | -17.682 | -17.682
2025-06-22 18:00:00 | 3.84 | 11.4842 | 0 | 0 | 323.9135 | -7.6442 | -7.6442
2025-06-22 19:00:00 | 3.36 | 1.4406 | 0 | 0 | 323.9135 | 1.9194 | 1.9194
2025-06-22 20:00:00 | 3.9 | 0 | 0 | 0 | 323.9135 | 3.9 | 3.9
2025-06-22 21:00:00 | 3.66 | 0 | 0 | 0 | 323.9135 | 3.66 | 3.66
2025-06-22 22:00:00 | 3.72 | 0 | 0 | 0 | 323.9135 | 3.72 | 3.72
2025-06-22 23:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-23 00:00:00 | 3.42 | 0 | 0 | 0 | 323.9135 | 3.42 | 3.42
2025-06-23 01:00:00 | 3.24 | 0 | 0 | 0 | 323.9135 | 3.24 | 3.24
2025-06-23 02:00:00 | 3.66 | 0 | 0 | 0 | 323.9135 | 3.66 | 3.66
2025-06-23 03:00:00 | 3.42 | 0 | 0 | 0 | 323.9135 | 3.42 | 3.42
2025-06-23 04:00:00 | 3.36 | 1.4338 | 0 | 0 | 323.9135 | 1.9262 | 1.9262
2025-06-23 05:00:00 | 5.1 | 11.478 | 0 | 0 | 323.9135 | -6.378 | -6.378
2025-06-23 06:00:00 | 4.5 | 21.8765 | 0 | 0 | 323.9135 | -17.3765 | -17.3765
2025-06-23 07:00:00 | 5.76 | 31.9207 | 0 | 0 | 323.9135 | -26.1607 | -26.1607
2025-06-23 08:00:00 | 5.22 | 40.926 | 0 | 0 | 323.9135 | -35.706 | -35.706
2025-06-23 09:00:00 | 5.76 | 48.2789 | 0 | 0 | 323.9135 | -42.5189 | -42.5189
2025-06-23 10:00:00 | 6.06 | 53.4782 | 0 | 0 | 323.9135 | -47.4182 | -47.4182
2025-06-23 11:00:00 | 6 | 56.1695 | 0 | 0 | 323.9135 | -50.1695 | -50.1695
2025-06-23 12:00:00 | 5.64 | 56.1695 | 0 | 0 | 323.9135 | -50.5295 | -50.5295
2025-06-23 13:00:00 | 6.18 | 53.4782 | 0 | 0 | 323.9135 | -47.2982 | -47.2982
2025-06-23 14:00:00 | 6.06 | 48.2789 | 0 | 0 | 323.9135 | -42.2189 | -42.2189
2025-06-23 15:00:00 | 5.28 | 40.926 | 0 | 0 | 323.9135 | -35.646 | -35.646
2025-06-23 16:00:00 | 3.84 | 31.9207 | 0 | 0 | 323.9135 | -28.0807 | -28.0807
2025-06-23 17:00:00 | 3.72 | 21.8765 | 0 | 0 | 323.9135 | -18.1565 | -18.1565
2025-06-23 18:00:00 | 3.72 | 11.478 | 0 | 0 | 323.9135 | -7.758 | -7.758
2025-06-23 19:00:00 | 3.72 | 1.4338 | 0 | 0 | 323.9135 | 2.2862 | 2.2862
2025-06-23 20:00:00 | 3.6 | 0 | 0 | 0 | 323.9135 | 3.6 | 3.6
2025-06-23 21:00:00 | 3.42 | 0 | 0 | 0 | 323.9135 | 3.42 | 3.42
2025-06-23 22:00:00 | 3.48 | 0 | 0 | 0 | 323.9135 | 3.48 | 3.48
2025-06-23 23:00:00 | 3.36 | 0 | 0 | 0 | 323.9135 | 3.36 | 3.36
2025-06-24 00:00:00 | 3.36 | 0 | 0 | 0 | 323.9135 | 3.36 | 3.36
2025-06-24 01:00:00 | 3.36 | 0 | 0 | 0 | 323.9135 | 3.36 | 3.36
2025-06-24 02:00:00 | 3.12 | 0 | 0 | 0 | 323.9135 | 3.12 | 3.12
2025-06-24 03:00:00 | 3.3 | 0 | 0 | 0 | 323.9135 | 3.3 | 3.3
2025-06-24 04:00:00 | 3.48 | 1.4215 | 0 | 0 | 323.9135 | 2.0585 | 2.0585
2025-06-24 05:00:00 | 4.68 | 11.4669 | 0 | 0 | 323.9135 | -6.7869 | -6.7869
2025-06-24 06:00:00 | 5.16 | 21.8666 | 0 | 0 | 323.9135 | -16.7066 | -16.7066
2025-06-24 07:00:00 | 5.76 | 31.912 | 0 | 0 | 323.9135 | -26.152 | -26.152
2025-06-24 08:00:00 | 5.88 | 40.9184 | 0 | 0 | 323.9135 | -35.0384 | -35.0384
2025-06-24 09:00:00 | 6.72 | 48.2721 | 0 | 0 | 323.9135 | -41.5521 | -41.5521
2025-06-24 10:00:00 | 6.84 | 53.472 | 0 | 0 | 323.9135 | -46.632 | -46.632
2025-06-24 11:00:00 | 7.5 | 56.1637 | 0 | 0 | 323.9135 | -48.6637 | -48.6637
2025-06-24 12:00:00 | 7.56 | 56.1637 | 0 | 0 | 323.9135 | -48.6037 | -48.6037
2025-06-24 13:00:00 | 7.86 | 53.472 | 0 | 0 | 323.9135 | -45.612 | -45.612
2025-06-24 14:00:00 | 8.34 | 48.2721 | 0 | 0 | 323.9135 | -39.9321 | -39.9321
2025-06-24 15:00:00 | 7.38 | 40.9184 | 0 | 0 | 323.9135 | -33.5384 | -33.5384
2025-06-24 16:00:00 | 6.18 | 31.912 | 0 | 0 | 323.9135 | -25.732 | -25.732
2025-06-24 17:00:00 | 4.8 | 21.8666 | 0 | 0 | 323.9135 | -17.0666 | -17.0666
2025-06-24 18:00:00 | 4.86 | 11.4669 | 0 | 0 | 323.9135 | -6.6069 | -6.6069
2025-06-24 19:00:00 | 4.68 | 1.4215 | 0 | 0 | 323.9135 | 3.2585 | 3.2585
2025-06-24 20:00:00 | 4.38 | 0 | 0 | 0 | 323.9135 | 4.38 | 4.38
2025-06-24 21:00:00 | 4.38 | 0 | 0 | 0 | 323.9135 | 4.38 | 4.38
2025-06-24 22:00:00 | 4.14 | 0 | 0 | 0 | 323.9135 | 4.14 | 4.14
2025-06-24 23:00:00 | 4.44 | 0 | 0 | 0 | 323.9135 | 4.44 | 4.44
2025-06-25 00:00:00 | 3.96 | 0 | 0 | 0 | 323.9135 | 3.96 | 3.96
2025-06-25 01:00:00 | 4.38 | 0 | 0 | 0 | 323.9135 | 4.38 | 4.38
2025-06-25 02:00:00 | 4.02 | 0 | 0 | 0 | 323.9135 | 4.02 | 4.02
2025-06-25 03:00:00 | 4.2 | 0 | 0 | 0 | 323.9135 | 4.2 | 4.2
2025-06-25 04:00:00 | 3.78 | 1.4037 | 0 | 0 | 323.9135 | 2.3763 | 2.3763
2025-06-25 05:00:00 | 3.96 | 11.4508 | 0 | 0 | 323.9135 | -7.4908 | -7.4908
2025-06-25 06:00:00 | 5.52 | 21.8523 | 0 | 0 | 323.9135 | -16.3323 | -16.3323
2025-06-25 07:00:00 | 6.06 | 31.8994 | 0 | 0 | 323.9135 | -25.8394 | -25.8394
2025-06-25 08:00:00 | 6.18 | 40.9074 | 0 | 0 | 323.9135 | -34.7274 | -34.7274
2025-06-25 09:00:00 | 6.06 | 48.2624 | 0 | 0 | 323.9135 | -42.2024 | -42.2024
2025-06-25 10:00:00 | 6.66 | 53.4631 | 0 | 0 | 323.9135 | -46.8031 | -46.8031
2025-06-25 11:00:00 | 6.78 | 56.1552 | 0 | 0 | 323.9135 | -49.3752 | -49.3752
2025-06-25 12:00:00 | 7.26 | 56.1552 | 0 | 0 | 323.9135 | -48.8952 | -48.8952
2025-06-25 13:00:00 | 7.2 | 53.4631 | 0 | 0 | 323.9135 | -46.2631 | -46.2631
2025-06-25 14:00:00 | 6.72 | 48.2624 | 0 | 0 | 323.9135 | -41.5424 | -41.5424
2025-06-25 15:00:00 | 10.2 | 40.9074 | 0 | 0 | 323.9135 | -30.7074 | -30.7074
2025-06-25 16:00:00 | 8.82 | 31.8994 | 0 | 0 | 323.9135 | -23.0794 | -23.0794
2025-06-25 17:00:00 | 4.08 | 21.8523 | 0 | 0 | 323.9135 | -17.7723 | -17.7723
2025-06-25 18:00:00 | 3.96 | 11.4508 | 0 | 0 | 323.9135 | -7.4908 | -7.4908
2025-06-25 19:00:00 | 3.66 | 1.4037 | 0 | 0 | 323.9135 | 2.2563 | 2.2563
2025-06-25 20:00:00 | 3.42 | 0 | 0 | 0 | 323.9135 | 3.42 | 3.42
2025-06-25 21:00:00 | 3.42 | 0 | 0 | 0 | 323.9135 | 3.42 | 3.42
2025-06-25 22:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-25 23:00:00 | 3.24 | 0 | 0 | 0 | 323.9135 | 3.24 | 3.24
2025-06-26 00:00:00 | 3.36 | 0 | 0 | 0 | 323.9135 | 3.36 | 3.36
2025-06-26 01:00:00 | 3.24 | 0 | 0 | 0 | 323.9135 | 3.24 | 3.24
2025-06-26 02:00:00 | 3.48 | 0 | 0 | 0 | 323.9135 | 3.48 | 3.48
2025-06-26 03:00:00 | 3.06 | 0 | 0 | 0 | 323.9135 | 3.06 | 3.06
2025-06-26 04:00:00 | 3 | 1.3805 | 0 | 0 | 323.9135 | 1.6195 | 1.6195
2025-06-26 05:00:00 | 2.88 | 11.4299 | 0 | 0 | 323.9135 | -8.5499 | -8.5499
2025-06-26 06:00:00 | 3.06 | 21.8337 | 0 | 0 | 323.9135 | -18.7737 | -18.7737
2025-06-26 07:00:00 | 3.18 | 31.883 | 0 | 0 | 323.9135 | -28.703 | -28.703
2025-06-26 08:00:00 | 3.78 | 40.893 | 0 | 0 | 323.9135 | -37.113 | -37.113
2025-06-26 09:00:00 | 4.5 | 48.2496 | 0 | 0 | 323.9135 | -43.7496 | -43.7496
2025-06-26 10:00:00 | 4.5 | 53.4515 | 0 | 0 | 323.9135 | -48.9515 | -48.9515
2025-06-26 11:00:00 | 5.88 | 56.1442 | 0 | 0 | 323.9135 | -50.2642 | -50.2642
2025-06-26 12:00:00 | 18.18 | 56.1442 | 0 | 0 | 323.9135 | -37.9642 | -37.9642
2025-06-26 13:00:00 | 18.12 | 53.4515 | 0 | 0 | 323.9135 | -35.3315 | -35.3315
2025-06-26 14:00:00 | 18.36 | 48.2496 | 0 | 0 | 323.9135 | -29.8896 | -29.8896
2025-06-26 15:00:00 | 13.26 | 40.893 | 0 | 0 | 323.9135 | -27.633 | -27.633
2025-06-26 16:00:00 | 3 | 31.883 | 0 | 0 | 323.9135 | -28.883 | -28.883
2025-06-26 17:00:00 | 3.3 | 21.8337 | 0 | 0 | 323.9135 | -18.5337 | -18.5337
2025-06-26 18:00:00 | 3.36 | 11.4299 | 0 | 0 | 323.9135 | -8.0699 | -8.0699
2025-06-26 19:00:00 | 3 | 1.3805 | 0 | 0 | 323.9135 | 1.6195 | 1.6195
2025-06-26 20:00:00 | 3.3 | 0 | 0 | 0 | 323.9135 | 3.3 | 3.3
2025-06-26 21:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-26 22:00:00 | 3.84 | 0 | 0 | 0 | 323.9135 | 3.84 | 3.84
2025-06-26 23:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-27 00:00:00 | 3.54 | 0 | 0 | 0 | 323.9135 | 3.54 | 3.54
2025-06-27 01:00:00 | 3.66 | 0 | 0 | 0 | 323.9135 | 3.66 | 3.66
2025-06-27 02:00:00 | 3.6 | 0 | 0 | 0 | 323.9135 | 3.6 | 3.6
2025-06-27 03:00:00 | 3.9 | 0 | 0 | 0 | 323.9135 | 3.9 | 3.9
2025-06-27 04:00:00 | 3.66 | 1.3519 | 0 | 0 | 323.9135 | 2.3081 | 2.3081
2025-06-27 05:00:00 | 5.28 | 11.404 | 0 | 0 | 323.9135 | -6.124 | -6.124
2025-06-27 06:00:00 | 5.4 | 21.8106 | 0 | 0 | 323.9135 | -16.4106 | -16.4106
2025-06-27 07:00:00 | 5.16 | 31.8627 | 0 | 0 | 323.9135 | -26.7027 | -26.7027
2025-06-27 08:00:00 | 5.16 | 40.8752 | 0 | 0 | 323.9135 | -35.7152 | -35.7152
2025-06-27 09:00:00 | 5.28 | 48.2338 | 0 | 0 | 323.9135 | -42.9538 | -42.9538
2025-06-27 10:00:00 | 5.1 | 53.4371 | 0 | 0 | 323.9135 | -48.3371 | -48.3371
2025-06-27 11:00:00 | 5.34 | 56.1306 | 0 | 0 | 323.9135 | -50.7906 | -50.7906
2025-06-27 12:00:00 | 8.46 | 56.1306 | 0 | 0 | 323.9135 | -47.6706 | -47.6706
2025-06-27 13:00:00 | 26.52 | 53.4371 | 0 | 0 | 323.9135 | -26.9171 | -26.9171
2025-06-27 14:00:00 | 25.32 | 48.2338 | 0 | 0 | 323.9135 | -22.9138 | -22.9138
2025-06-27 15:00:00 | 20.64 | 40.8752 | 0 | 0 | 323.9135 | -20.2352 | -20.2352
2025-06-27 16:00:00 | 18.3 | 31.8627 | 0 | 0 | 323.9135 | -13.5627 | -13.5627
2025-06-27 17:00:00 | 18 | 21.8106 | 0 | 0 | 323.9135 | -3.8106 | -3.8106
2025-06-27 18:00:00 | 17.52 | 11.404 | 0 | 6.116 | 317.7974 | -5.3291e-15 | 6.116
2025-06-27 19:00:00 | 16.08 | 1.3519 | 0 | 0 | 317.7974 | 14.7281 | 14.7281
2025-06-27 20:00:00 | 24.12 | 0 | 0 | 0 | 317.7974 | 24.12 | 24.12
2025-06-27 21:00:00 | 23.82 | 0 | 0 | 0 | 317.7974 | 23.82 | 23.82
2025-06-27 22:00:00 | 23.82 | 0 | 0 | 0 | 317.7974 | 23.82 | 23.82
2025-06-27 23:00:00 | 23.76 | 0 | 0 | 0 | 317.7974 | 23.76 | 23.76
2025-06-28 00:00:00 | 23.76 | 0 | 0 | 0 | 317.7974 | 23.76 | 23.76
2025-06-28 01:00:00 | 24 | 0 | 0 | 0 | 317.7974 | 24 | 24
2025-06-28 02:00:00 | 15.84 | 0 | 0 | 0 | 317.7974 | 15.84 | 15.84
2025-06-28 03:00:00 | 10.8 | 0 | 0 | 0 | 317.7974 | 10.8 | 10.8
2025-06-28 04:00:00 | 9.78 | 1.3178 | 0 | 0 | 317.7974 | 8.4622 | 8.4622
2025-06-28 05:00:00 | 7.14 | 11.3731 | 0 | 0 | 317.7974 | -4.2331 | -4.2331
2025-06-28 06:00:00 | 3 | 21.7832 | 0 | 0 | 317.7974 | -18.7832 | -18.7832
2025-06-28 07:00:00 | 3.12 | 31.8386 | 0 | 0 | 317.7974 | -28.7186 | -28.7186
2025-06-28 08:00:00 | 3.12 | 40.854 | 0 | 0 | 317.7974 | -37.734 | -37.734
2025-06-28 09:00:00 | 3.06 | 48.215 | 0 | 0 | 317.7974 | -45.155 | -45.155
2025-06-28 10:00:00 | 3.24 | 53.42 | 0 | 0 | 317.7974 | -50.18 | -50.18
2025-06-28 11:00:00 | 3.48 | 56.1144 | 0 | 0 | 317.7974 | -52.6344 | -52.6344
2025-06-28 12:00:00 | 3.06 | 56.1144 | 0 | 0 | 317.7974 | -53.0544 | -53.0544
2025-06-28 13:00:00 | 3.12 | 53.42 | 0 | 0 | 317.7974 | -50.3 | -50.3
2025-06-28 14:00:00 | 3 | 48.215 | 0 | 0 | 317.7974 | -45.215 | -45.215
2025-06-28 15:00:00 | 3.18 | 40.854 | 0 | 0 | 317.7974 | -37.674 | -37.674
2025-06-28 16:00:00 | 3.24 | 31.8386 | 0 | 0 | 317.7974 | -28.5986 | -28.5986
2025-06-28 17:00:00 | 3.06 | 21.7832 | 0 | 0 | 317.7974 | -18.7232 | -18.7232
2025-06-28 18:00:00 | 3.12 | 11.3731 | 0 | 0 | 317.7974 | -8.2531 | -8.2531
2025-06-28 19:00:00 | 3.12 | 1.3178 | 0 | 0 | 317.7974 | 1.8022 | 1.8022
2025-06-28 20:00:00 | 3.36 | 0 | 0 | 0 | 317.7974 | 3.36 | 3.36
2025-06-28 21:00:00 | 2.88 | 0 | 0 | 0 | 317.7974 | 2.88 | 2.88
2025-06-28 22:00:00 | 3.3 | 0 | 0 | 0 | 317.7974 | 3.3 | 3.3
2025-06-28 23:00:00 | 3.06 | 0 | 0 | 0 | 317.7974 | 3.06 | 3.06
2025-06-29 00:00:00 | 3.42 | 0 | 0 | 0 | 317.7974 | 3.42 | 3.42
2025-06-29 01:00:00 | 3.78 | 0 | 0 | 0 | 317.7974 | 3.78 | 3.78
2025-06-29 02:00:00 | 3.78 | 0 | 0 | 0 | 317.7974 | 3.78 | 3.78
2025-06-29 03:00:00 | 3.66 | 0 | 0 | 0 | 317.7974 | 3.66 | 3.66
2025-06-29 04:00:00 | 3.66 | 1.2782 | 0 | 0 | 317.7974 | 2.3818 | 2.3818
2025-06-29 05:00:00 | 3.78 | 11.3374 | 0 | 0 | 317.7974 | -7.5574 | -7.5574
2025-06-29 06:00:00 | 3.3 | 21.7514 | 0 | 0 | 317.7974 | -18.4514 | -18.4514
2025-06-29 07:00:00 | 3.12 | 31.8105 | 0 | 0 | 317.7974 | -28.6905 | -28.6905
2025-06-29 08:00:00 | 3.12 | 40.8293 | 0 | 0 | 317.7974 | -37.7093 | -37.7093
2025-06-29 09:00:00 | 3 | 48.1931 | 0 | 0 | 317.7974 | -45.1931 | -45.1931
2025-06-29 10:00:00 | 3.06 | 53.4001 | 0 | 0 | 317.7974 | -50.3401 | -50.3401
2025-06-29 11:00:00 | 10.38 | 56.0955 | 0 | 0 | 317.7974 | -45.7155 | -45.7155
2025-06-29 12:00:00 | 9.84 | 56.0955 | 0 | 0 | 317.7974 | -46.2555 | -46.2555
2025-06-29 13:00:00 | 3.12 | 53.4001 | 0 | 0 | 317.7974 | -50.2801 | -50.2801
2025-06-29 14:00:00 | 3.24 | 48.1931 | 0 | 0 | 317.7974 | -44.9531 | -44.9531
2025-06-29 15:00:00 | 3.42 | 40.8293 | 0 | 0 | 317.7974 | -37.4093 | -37.4093
2025-06-29 16:00:00 | 3.72 | 31.8105 | 0 | 0 | 317.7974 | -28.0905 | -28.0905
2025-06-29 17:00:00 | 3.6 | 21.7514 | 0 | 0 | 317.7974 | -18.1514 | -18.1514
2025-06-29 18:00:00 | 3.36 | 11.3374 | 0 | 0 | 317.7974 | -7.9774 | -7.9774
2025-06-29 19:00:00 | 3.24 | 1.2782 | 0 | 0 | 317.7974 | 1.9618 | 1.9618
2025-06-29 20:00:00 | 3.3 | 0 | 0 | 0 | 317.7974 | 3.3 | 3.3
2025-06-29 21:00:00 | 3.54 | 0 | 0 | 0 | 317.7974 | 3.54 | 3.54
2025-06-29 22:00:00 | 3.12 | 0 | 0 | 0 | 317.7974 | 3.12 | 3.12
2025-06-29 23:00:00 | 3.12 | 0 | 0 | 0 | 317.7974 | 3.12 | 3.12
2025-06-30 00:00:00 | 3.06 | 0 | 0 | 0 | 317.7974 | 3.06 | 3.06
2025-06-30 01:00:00 | 3.12 | 0 | 0 | 0 | 317.7974 | 3.12 | 3.12
2025-06-30 02:00:00 | 3.3 | 0 | 0 | 0 | 317.7974 | 3.3 | 3.3
2025-06-30 03:00:00 | 3 | 0 | 0 | 0 | 317.7974 | 3 | 3
2025-06-30 04:00:00 | 2.94 | 1.2333 | 0 | 0 | 317.7974 | 1.7067 | 1.7067
2025-06-30 05:00:00 | 3.12 | 11.2967 | 0 | 0 | 317.7974 | -8.1767 | -8.1767
2025-06-30 06:00:00 | 3.06 | 21.7152 | 0 | 0 | 317.7974 | -18.6552 | -18.6552
2025-06-30 07:00:00 | 3.06 | 31.7786 | 0 | 0 | 317.7974 | -28.7186 | -28.7186
2025-06-30 08:00:00 | 3.06 | 40.8013 | 0 | 0 | 317.7974 | -37.7413 | -37.7413
2025-06-30 09:00:00 | 3.12 | 48.1683 | 0 | 0 | 317.7974 | -45.0483 | -45.0483
2025-06-30 10:00:00 | 3.06 | 53.3775 | 0 | 0 | 317.7974 | -50.3175 | -50.3175
2025-06-30 11:00:00 | 3.6 | 56.074 | 0 | 0 | 317.7974 | -52.474 | -52.474
2025-06-30 12:00:00 | 3.24 | 56.074 | 0 | 0 | 317.7974 | -52.834 | -52.834
2025-06-30 13:00:00 | 3.54 | 53.3775 | 0 | 0 | 317.7974 | -49.8375 | -49.8375
2025-06-30 14:00:00 | 3.36 | 48.1683 | 0 | 0 | 317.7974 | -44.8083 | -44.8083
2025-06-30 15:00:00 | 3.42 | 40.8013 | 0 | 0 | 317.7974 | -37.3813 | -37.3813
2025-06-30 16:00:00 | 3.18 | 31.7786 | 0 | 0 | 317.7974 | -28.5986 | -28.5986
2025-06-30 17:00:00 | 3.12 | 21.7152 | 0 | 0 | 317.7974 | -18.5952 | -18.5952
2025-06-30 18:00:00 | 3.18 | 11.2967 | 0 | 0 | 317.7974 | -8.1167 | -8.1167
2025-06-30 19:00:00 | 3.18 | 1.2333 | 0 | 0 | 317.7974 | 1.9467 | 1.9467
2025-06-30 20:00:00 | 3.12 | 0 | 0 | 0 | 317.7974 | 3.12 | 3.12
2025-06-30 21:00:00 | 3.3 | 0 | 8.1847 | 0 | 325 | 11.4847 | 3.3
2025-06-30 22:00:00 | 3.24 | 0 | 0 | 0 | 325 | 3.24 | 3.24
2025-06-30 23:00:00 | 3.06 | 0 | 0 | 0 | 325 | 3.06 | 3.06
2025-07-01 00:00:00 | 3.18 | 0 | 0 | 0 | 325 | 3.18 | 3.18
2025-07-01 01:00:00 | 3.48 | 0 | 0 | 0 | 325 | 3.48 | 3.48
2025-07-01 02:00:00 | 3.12 | 0 | 0 | 0 | 325 | 3.12 | 3.12
2025-07-01 03:00:00 | 3.06 | 0 | 0 | 0 | 325 | 3.06 | 3.06
2025-07-01 04:00:00 | 3 | 1.2014 | 0 | 0 | 325 | 1.7986 | 1.7986
2025-07-01 05:00:00 | 3.18 | 11.427 | 0 | 0 | 325 | -8.247 | -8.247
2025-07-01 06:00:00 | 3.48 | 22.0133 | 0 | 0 | 325 | -18.5333 | -18.5333
2025-07-01 07:00:00 | 4.98 | 32.2389 | 0 | 0 | 325 | -27.2589 | -27.2589
2025-07-01 08:00:00 | 5.1 | 41.4069 | 0 | 0 | 325 | -36.3069 | -36.3069
2025-07-01 09:00:00 | 5.34 | 48.8925 | 0 | 0 | 325 | -43.5525 | -43.5525
2025-07-01 10:00:00 | 4.86 | 54.1857 | 0 | 0 | 325 | -49.3257 | -49.3257
2025-07-01 11:00:00 | 5.52 | 56.9256 | 0 | 0 | 325 | -51.4056 | -51.4056
2025-07-01 12:00:00 | 5.64 | 56.9256 | 0 | 0 | 325 | -51.2856 | -51.2856
2025-07-01 13:00:00 | 6.18 | 54.1857 | 0 | 0 | 325 | -48.0057 | -48.0057
2025-07-01 14:00:00 | 5.64 | 48.8925 | 0 | 0 | 325 | -43.2525 | -43.2525
2025-07-01 15:00:00 | 18.18 | 41.4069 | 0 | 0 | 325 | -23.2269 | -23.2269
2025-07-01 16:00:00 | 18.42 | 32.2389 | 0 | 0 | 325 | -13.8189 | -13.8189
2025-07-01 17:00:00 | 18.66 | 22.0133 | 0 | 0 | 325 | -3.3533 | -3.3533
2025-07-01 18:00:00 | 18.42 | 11.427 | 0 | 6.993 | 318.007 | -2.4869e-14 | 6.993
2025-07-01 19:00:00 | 18.24 | 1.2014 | 0 | 0 | 318.007 | 17.0386 | 17.0386
2025-07-01 20:00:00 | 17.1 | 0 | 0 | 0 | 318.007 | 17.1 | 17.1
2025-07-01 21:00:00 | 4.32 | 0 | 0 | 0 | 318.007 | 4.32 | 4.32
2025-07-01 22:00:00 | 4.2 | 0 | 0 | 0 | 318.007 | 4.2 | 4.2
2025-07-01 23:00:00 | 3.84 | 0 | 0 | 0 | 318.007 | 3.84 | 3.84
2025-07-02 00:00:00 | 3.9 | 0 | 0 | 0 | 318.007 | 3.9 | 3.9
2025-07-02 01:00:00 | 4.02 | 0 | 0 | 0 | 318.007 | 4.02 | 4.02
2025-07-02 02:00:00 | 3.84 | 0 | 0 | 0 | 318.007 | 3.84 | 3.84
2025-07-02 03:00:00 | 4.2 | 0 | 0 | 0 | 318.007 | 4.2 | 4.2
2025-07-02 04:00:00 | 4.08 | 1.1448 | 0 | 0 | 318.007 | 2.9352 | 2.9352
2025-07-02 05:00:00 | 3.78 | 11.3757 | 0 | 0 | 318.007 | -7.5957 | -7.5957
2025-07-02 06:00:00 | 4.92 | 21.9676 | 0 | 0 | 318.007 | -17.0476 | -17.0476
2025-07-02 07:00:00 | 5.16 | 32.1986 | 0 | 0 | 318.007 | -27.0386 | -27.0386
2025-07-02 08:00:00 | 5.64 | 41.3714 | 0 | 0 | 318.007 | -35.7314 | -35.7314
2025-07-02 09:00:00 | 5.88 | 48.861 | 0 | 0 | 318.007 | -42.981 | -42.981
2025-07-02 10:00:00 | 6.18 | 54.157 | 0 | 0 | 318.007 | -47.977 | -47.977
2025-07-02 11:00:00 | 6.36 | 56.8984 | 0 | 0 | 318.007 | -50.5384 | -50.5384
2025-07-02 12:00:00 | 6.36 | 56.8984 | 0 | 0 | 318.007 | -50.5384 | -50.5384
2025-07-02 13:00:00 | 6.42 | 54.157 | 0 | 0 | 318.007 | -47.737 | -47.737
2025-07-02 14:00:00 | 6.96 | 48.861 | 0 | 0 | 318.007 | -41.901 | -41.901
2025-07-02 15:00:00 | 5.04 | 41.3714 | 0 | 0 | 318.007 | -36.3314 | -36.3314
2025-07-02 16:00:00 | 3.9 | 32.1986 | 0 | 0 | 318.007 | -28.2986 | -28.2986
2025-07-02 17:00:00 | 3.42 | 21.9676 | 0 | 0 | 318.007 | -18.5476 | -18.5476
2025-07-02 18:00:00 | 3.42 | 11.3757 | 0 | 0 | 318.007 | -7.9557 | -7.9557
2025-07-02 19:00:00 | 3.36 | 1.1448 | 0 | 0 | 318.007 | 2.2152 | 2.2152
2025-07-02 20:00:00 | 3.42 | 0 | 0 | 0 | 318.007 | 3.42 | 3.42
2025-07-02 21:00:00 | 3.36 | 0 | 0 | 0 | 318.007 | 3.36 | 3.36
2025-07-02 22:00:00 | 3.36 | 0 | 0 | 0 | 318.007 | 3.36 | 3.36
2025-07-02 23:00:00 | 3 | 0 | 0 | 0 | 318.007 | 3 | 3
2025-07-03 00:00:00 | 3.48 | 0 | 0 | 0 | 318.007 | 3.48 | 3.48
2025-07-03 01:00:00 | 3.12 | 0 | 0 | 0 | 318.007 | 3.12 | 3.12
2025-07-03 02:00:00 | 2.88 | 0 | 0 | 0 | 318.007 | 2.88 | 2.88
2025-07-03 03:00:00 | 2.88 | 0 | 0 | 0 | 318.007 | 2.88 | 2.88
2025-07-03 04:00:00 | 3.3 | 1.0827 | 0 | 0 | 318.007 | 2.2173 | 2.2173
2025-07-03 05:00:00 | 2.76 | 11.3196 | 0 | 0 | 318.007 | -8.5596 | -8.5596
2025-07-03 06:00:00 | 3.18 | 21.9175 | 0 | 0 | 318.007 | -18.7375 | -18.7375
2025-07-03 07:00:00 | 3.6 | 32.1544 | 0 | 0 | 318.007 | -28.5544 | -28.5544
2025-07-03 08:00:00 | 4.26 | 41.3325 | 0 | 0 | 318.007 | -37.0725 | -37.0725
2025-07-03 09:00:00 | 4.5 | 48.8264 | 0 | 0 | 318.007 | -44.3264 | -44.3264
2025-07-03 10:00:00 | 4.44 | 54.1254 | 0 | 0 | 318.007 | -49.6854 | -49.6854
2025-07-03 11:00:00 | 4.68 | 56.8684 | 0 | 0 | 318.007 | -52.1884 | -52.1884
2025-07-03 12:00:00 | 4.8 | 56.8684 | 0 | 0 | 318.007 | -52.0684 | -52.0684
2025-07-03 13:00:00 | 4.8 | 54.1254 | 0 | 0 | 318.007 | -49.3254 | -49.3254
2025-07-03 14:00:00 | 4.44 | 48.8264 | 0 | 0 | 318.007 | -44.3864 | -44.3864
2025-07-03 15:00:00 | 4.2 | 41.3325 | 0 | 0 | 318.007 | -37.1325 | -37.1325
2025-07-03 16:00:00 | 3.24 | 32.1544 | 0 | 0 | 318.007 | -28.9144 | -28.9144
2025-07-03 17:00:00 | 3.18 | 21.9175 | 0 | 0 | 318.007 | -18.7375 | -18.7375
2025-07-03 18:00:00 | 3.54 | 11.3196 | 0 | 0 | 318.007 | -7.7796 | -7.7796
2025-07-03 19:00:00 | 3.06 | 1.0827 | 0 | 0 | 318.007 | 1.9773 | 1.9773
2025-07-03 20:00:00 | 3 | 0 | 0 | 0 | 318.007 | 3 | 3
2025-07-03 21:00:00 | 2.88 | 0 | 0 | 0 | 318.007 | 2.88 | 2.88
2025-07-03 22:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-03 23:00:00 | 3.06 | 0 | 0 | 0 | 318.007 | 3.06 | 3.06
2025-07-04 00:00:00 | 3.42 | 0 | 0 | 0 | 318.007 | 3.42 | 3.42
2025-07-04 01:00:00 | 3.54 | 0 | 0 | 0 | 318.007 | 3.54 | 3.54
2025-07-04 02:00:00 | 3.6 | 0 | 0 | 0 | 318.007 | 3.6 | 3.6
2025-07-04 03:00:00 | 4.2 | 0 | 0 | 0 | 318.007 | 4.2 | 4.2
2025-07-04 04:00:00 | 3.84 | 1.0152 | 0 | 0 | 318.007 | 2.8248 | 2.8248
2025-07-04 05:00:00 | 5.1 | 11.2584 | 0 | 0 | 318.007 | -6.1584 | -6.1584
2025-07-04 06:00:00 | 5.1 | 21.863 | 0 | 0 | 318.007 | -16.763 | -16.763
2025-07-04 07:00:00 | 5.64 | 32.1063 | 0 | 0 | 318.007 | -26.4663 | -26.4663
2025-07-04 08:00:00 | 5.1 | 41.2901 | 0 | 0 | 318.007 | -36.1901 | -36.1901
2025-07-04 09:00:00 | 5.4 | 48.7887 | 0 | 0 | 318.007 | -43.3887 | -43.3887
2025-07-04 10:00:00 | 5.28 | 54.091 | 0 | 0 | 318.007 | -48.811 | -48.811
2025-07-04 11:00:00 | 5.4 | 56.8357 | 0 | 0 | 318.007 | -51.4357 | -51.4357
2025-07-04 12:00:00 | 5.64 | 56.8357 | 0 | 0 | 318.007 | -51.1957 | -51.1957
2025-07-04 13:00:00 | 6 | 54.091 | 0 | 0 | 318.007 | -48.091 | -48.091
2025-07-04 14:00:00 | 5.76 | 48.7887 | 0 | 0 | 318.007 | -43.0287 | -43.0287
2025-07-04 15:00:00 | 4.44 | 41.2901 | 0 | 0 | 318.007 | -36.8501 | -36.8501
2025-07-04 16:00:00 | 3.84 | 32.1063 | 0 | 0 | 318.007 | -28.2663 | -28.2663
2025-07-04 17:00:00 | 3.36 | 21.863 | 0 | 0 | 318.007 | -18.503 | -18.503
2025-07-04 18:00:00 | 3.3 | 11.2584 | 0 | 0 | 318.007 | -7.9584 | -7.9584
2025-07-04 19:00:00 | 3.24 | 1.0152 | 0 | 0 | 318.007 | 2.2248 | 2.2248
2025-07-04 20:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-04 21:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-04 22:00:00 | 3.18 | 0 | 0 | 0 | 318.007 | 3.18 | 3.18
2025-07-04 23:00:00 | 2.94 | 0 | 0 | 0 | 318.007 | 2.94 | 2.94
2025-07-05 00:00:00 | 3.12 | 0 | 0 | 0 | 318.007 | 3.12 | 3.12
2025-07-05 01:00:00 | 3.24 | 0 | 0 | 0 | 318.007 | 3.24 | 3.24
2025-07-05 02:00:00 | 3 | 0 | 0 | 0 | 318.007 | 3 | 3
2025-07-05 03:00:00 | 3 | 0 | 0 | 0 | 318.007 | 3 | 3
2025-07-05 04:00:00 | 3.06 | 0.94221 | 0 | 0 | 318.007 | 2.1178 | 2.1178
2025-07-05 05:00:00 | 2.82 | 11.1923 | 0 | 0 | 318.007 | -8.3723 | -8.3723
2025-07-05 06:00:00 | 3.12 | 21.8041 | 0 | 0 | 318.007 | -18.6841 | -18.6841
2025-07-05 07:00:00 | 3 | 32.0542 | 0 | 0 | 318.007 | -29.0542 | -29.0542
2025-07-05 08:00:00 | 3.06 | 41.2442 | 0 | 0 | 318.007 | -38.1842 | -38.1842
2025-07-05 09:00:00 | 3.06 | 48.7478 | 0 | 0 | 318.007 | -45.6878 | -45.6878
2025-07-05 10:00:00 | 3.6 | 54.0537 | 0 | 0 | 318.007 | -50.4537 | -50.4537
2025-07-05 11:00:00 | 3.66 | 56.8002 | 0 | 0 | 318.007 | -53.1402 | -53.1402
2025-07-05 12:00:00 | 3.6 | 56.8002 | 0 | 0 | 318.007 | -53.2002 | -53.2002
2025-07-05 13:00:00 | 3.9 | 54.0537 | 0 | 0 | 318.007 | -50.1537 | -50.1537
2025-07-05 14:00:00 | 3.96 | 48.7478 | 0 | 0 | 318.007 | -44.7878 | -44.7878
2025-07-05 15:00:00 | 4.08 | 41.2442 | 0 | 0 | 318.007 | -37.1642 | -37.1642
2025-07-05 16:00:00 | 17.82 | 32.0542 | 0 | 0 | 318.007 | -14.2342 | -14.2342
2025-07-05 17:00:00 | 17.7 | 21.8041 | 0 | 0 | 318.007 | -4.1041 | -4.1041
2025-07-05 18:00:00 | 17.52 | 11.1923 | 0 | 0 | 318.007 | 6.3277 | 6.3277
2025-07-05 19:00:00 | 17.58 | 0.94221 | 0 | 0 | 318.007 | 16.6378 | 16.6378
2025-07-05 20:00:00 | 17.7 | 0 | 0 | 0 | 318.007 | 17.7 | 17.7
2025-07-05 21:00:00 | 17.34 | 0 | 0 | 0 | 318.007 | 17.34 | 17.34
2025-07-05 22:00:00 | 17.46 | 0 | 0 | 0 | 318.007 | 17.46 | 17.46
2025-07-05 23:00:00 | 15.54 | 0 | 0 | 0 | 318.007 | 15.54 | 15.54
2025-07-06 00:00:00 | 6.66 | 0 | 0 | 0 | 318.007 | 6.66 | 6.66
2025-07-06 01:00:00 | 4.26 | 0 | 0 | 0 | 318.007 | 4.26 | 4.26
2025-07-06 02:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-06 03:00:00 | 3.18 | 0 | 0 | 0 | 318.007 | 3.18 | 3.18
2025-07-06 04:00:00 | 3.12 | 0.86386 | 0 | 0 | 318.007 | 2.2561 | 2.2561
2025-07-06 05:00:00 | 2.88 | 11.1213 | 0 | 0 | 318.007 | -8.2413 | -8.2413
2025-07-06 06:00:00 | 3 | 21.7407 | 0 | 0 | 318.007 | -18.7407 | -18.7407
2025-07-06 07:00:00 | 3.36 | 31.9982 | 0 | 0 | 318.007 | -28.6382 | -28.6382
2025-07-06 08:00:00 | 3.3 | 41.1948 | 0 | 0 | 318.007 | -37.8948 | -37.8948
2025-07-06 09:00:00 | 3.54 | 48.7038 | 0 | 0 | 318.007 | -45.1638 | -45.1638
2025-07-06 10:00:00 | 3.66 | 54.0134 | 0 | 0 | 318.007 | -50.3534 | -50.3534
2025-07-06 11:00:00 | 4.08 | 56.7619 | 0 | 0 | 318.007 | -52.6819 | -52.6819
2025-07-06 12:00:00 | 4.26 | 56.7619 | 0 | 0 | 318.007 | -52.5019 | -52.5019
2025-07-06 13:00:00 | 4.08 | 54.0134 | 0 | 0 | 318.007 | -49.9334 | -49.9334
2025-07-06 14:00:00 | 3.9 | 48.7038 | 0 | 0 | 318.007 | -44.8038 | -44.8038
2025-07-06 15:00:00 | 4.26 | 41.1948 | 0 | 0 | 318.007 | -36.9348 | -36.9348
2025-07-06 16:00:00 | 3.72 | 31.9982 | 0 | 0 | 318.007 | -28.2782 | -28.2782
2025-07-06 17:00:00 | 4.32 | 21.7407 | 0 | 0 | 318.007 | -17.4207 | -17.4207
2025-07-06 18:00:00 | 3.96 | 11.1213 | 0 | 0 | 318.007 | -7.1613 | -7.1613
2025-07-06 19:00:00 | 6.78 | 0.86386 | 0 | 0 | 318.007 | 5.9161 | 5.9161
2025-07-06 20:00:00 | 10.26 | 0 | 0 | 0 | 318.007 | 10.26 | 10.26
2025-07-06 21:00:00 | 10.08 | 0 | 0 | 0 | 318.007 | 10.08 | 10.08
2025-07-06 22:00:00 | 10.02 | 0 | 0 | 0 | 318.007 | 10.02 | 10.02
2025-07-06 23:00:00 | 10.2 | 0 | 0 | 0 | 318.007 | 10.2 | 10.2
2025-07-07 00:00:00 | 9.96 | 0 | 0 | 0 | 318.007 | 9.96 | 9.96
2025-07-07 01:00:00 | 9.84 | 0 | 0 | 0 | 318.007 | 9.84 | 9.84
2025-07-07 02:00:00 | 9.9 | 0 | 0 | 0 | 318.007 | 9.9 | 9.9
2025-07-07 03:00:00 | 9.96 | 0 | 0 | 0 | 318.007 | 9.96 | 9.96
2025-07-07 04:00:00 | 10.08 | 0.78013 | 0 | 0 | 318.007 | 9.2999 | 9.2999
2025-07-07 05:00:00 | 9.78 | 11.0454 | 0 | 0 | 318.007 | -1.2654 | -1.2654
2025-07-07 06:00:00 | 10.38 | 21.6729 | 0 | 0 | 318.007 | -11.2929 | -11.2929
2025-07-07 07:00:00 | 9.36 | 31.9382 | 0 | 0 | 318.007 | -22.5782 | -22.5782
2025-07-07 08:00:00 | 4.74 | 41.1418 | 0 | 0 | 318.007 | -36.4018 | -36.4018
2025-07-07 09:00:00 | 4.74 | 48.6566 | 0 | 0 | 318.007 | -43.9166 | -43.9166
2025-07-07 10:00:00 | 4.68 | 53.9703 | 0 | 0 | 318.007 | -49.2903 | -49.2903
2025-07-07 11:00:00 | 5.04 | 56.7209 | 0 | 0 | 318.007 | -51.6809 | -51.6809
2025-07-07 12:00:00 | 4.68 | 56.7209 | 0 | 0 | 318.007 | -52.0409 | -52.0409
2025-07-07 13:00:00 | 4.86 | 53.9703 | 0 | 0 | 318.007 | -49.1103 | -49.1103
2025-07-07 14:00:00 | 6.12 | 48.6566 | 0 | 0 | 318.007 | -42.5366 | -42.5366
2025-07-07 15:00:00 | 4.92 | 41.1418 | 0 | 0 | 318.007 | -36.2218 | -36.2218
2025-07-07 16:00:00 | 3.42 | 31.9382 | 0 | 0 | 318.007 | -28.5182 | -28.5182
2025-07-07 17:00:00 | 3.36 | 21.6729 | 0 | 0 | 318.007 | -18.3129 | -18.3129
2025-07-07 18:00:00 | 3.18 | 11.0454 | 0 | 0 | 318.007 | -7.8654 | -7.8654
2025-07-07 19:00:00 | 3.72 | 0.78013 | 0 | 0 | 318.007 | 2.9399 | 2.9399
2025-07-07 20:00:00 | 3.24 | 0 | 0 | 0 | 318.007 | 3.24 | 3.24
2025-07-07 21:00:00 | 3.18 | 0 | 0 | 0 | 318.007 | 3.18 | 3.18
2025-07-07 22:00:00 | 3.12 | 0 | 0 | 0 | 318.007 | 3.12 | 3.12
2025-07-07 23:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-08 00:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-08 01:00:00 | 3.18 | 0 | 0 | 0 | 318.007 | 3.18 | 3.18
2025-07-08 02:00:00 | 3.06 | 0 | 0 | 0 | 318.007 | 3.06 | 3.06
2025-07-08 03:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-08 04:00:00 | 3.3 | 0.69105 | 0 | 0 | 318.007 | 2.609 | 2.609
2025-07-08 05:00:00 | 2.88 | 10.9647 | 0 | 0 | 318.007 | -8.0847 | -8.0847
2025-07-08 06:00:00 | 2.94 | 21.6007 | 0 | 0 | 318.007 | -18.6607 | -18.6607
2025-07-08 07:00:00 | 3.84 | 31.8743 | 0 | 0 | 318.007 | -28.0343 | -28.0343
2025-07-08 08:00:00 | 5.64 | 41.0853 | 0 | 0 | 318.007 | -35.4453 | -35.4453
2025-07-08 09:00:00 | 5.22 | 48.6061 | 0 | 0 | 318.007 | -43.3861 | -43.3861
2025-07-08 10:00:00 | 5.52 | 53.9241 | 0 | 0 | 318.007 | -48.4041 | -48.4041
2025-07-08 11:00:00 | 5.28 | 56.6769 | 0 | 0 | 318.007 | -51.3969 | -51.3969
2025-07-08 12:00:00 | 5.88 | 56.6769 | 0 | 0 | 318.007 | -50.7969 | -50.7969
2025-07-08 13:00:00 | 5.64 | 53.9241 | 0 | 0 | 318.007 | -48.2841 | -48.2841
2025-07-08 14:00:00 | 5.76 | 48.6061 | 0 | 0 | 318.007 | -42.8461 | -42.8461
2025-07-08 15:00:00 | 4.98 | 41.0853 | 0 | 0 | 318.007 | -36.1053 | -36.1053
2025-07-08 16:00:00 | 3.48 | 31.8743 | 0 | 0 | 318.007 | -28.3943 | -28.3943
2025-07-08 17:00:00 | 3.78 | 21.6007 | 0 | 0 | 318.007 | -17.8207 | -17.8207
2025-07-08 18:00:00 | 3.54 | 10.9647 | 0 | 0 | 318.007 | -7.4247 | -7.4247
2025-07-08 19:00:00 | 3.42 | 0.69105 | 0 | 0 | 318.007 | 2.729 | 2.729
2025-07-08 20:00:00 | 3.6 | 0 | 0 | 0 | 318.007 | 3.6 | 3.6
2025-07-08 21:00:00 | 3.42 | 0 | 0 | 0 | 318.007 | 3.42 | 3.42
2025-07-08 22:00:00 | 3.06 | 0 | 0 | 0 | 318.007 | 3.06 | 3.06
2025-07-08 23:00:00 | 3.36 | 0 | 0 | 0 | 318.007 | 3.36 | 3.36
2025-07-09 00:00:00 | 3.18 | 0 | 0 | 0 | 318.007 | 3.18 | 3.18
2025-07-09 01:00:00 | 2.94 | 0 | 0 | 0 | 318.007 | 2.94 | 2.94
2025-07-09 02:00:00 | 3.18 | 0 | 0 | 0 | 318.007 | 3.18 | 3.18
2025-07-09 03:00:00 | 3.42 | 0 | 0 | 0 | 318.007 | 3.42 | 3.42
2025-07-09 04:00:00 | 3.12 | 0.59664 | 0 | 0 | 318.007 | 2.5234 | 2.5234
2025-07-09 05:00:00 | 4.26 | 10.879 | 0 | 0 | 318.007 | -6.619 | -6.619
2025-07-09 06:00:00 | 4.8 | 21.5241 | 0 | 0 | 318.007 | -16.7241 | -16.7241
2025-07-09 07:00:00 | 5.28 | 31.8064 | 0 | 0 | 318.007 | -26.5264 | -26.5264
2025-07-09 08:00:00 | 5.28 | 41.0253 | 0 | 0 | 318.007 | -35.7453 | -35.7453
2025-07-09 09:00:00 | 5.64 | 48.5525 | 0 | 0 | 318.007 | -42.9125 | -42.9125
2025-07-09 10:00:00 | 6 | 53.875 | 0 | 0 | 318.007 | -47.875 | -47.875
2025-07-09 11:00:00 | 6.06 | 56.6302 | 0 | 0 | 318.007 | -50.5702 | -50.5702
2025-07-09 12:00:00 | 5.82 | 56.6302 | 0 | 0 | 318.007 | -50.8102 | -50.8102
2025-07-09 13:00:00 | 6.12 | 53.875 | 0 | 0 | 318.007 | -47.755 | -47.755
2025-07-09 14:00:00 | 6.12 | 48.5525 | 0 | 0 | 318.007 | -42.4325 | -42.4325
2025-07-09 15:00:00 | 5.76 | 41.0253 | 0 | 0 | 318.007 | -35.2653 | -35.2653
2025-07-09 16:00:00 | 3.96 | 31.8064 | 0 | 0 | 318.007 | -27.8464 | -27.8464
2025-07-09 17:00:00 | 3.54 | 21.5241 | 0 | 0 | 318.007 | -17.9841 | -17.9841
2025-07-09 18:00:00 | 3.66 | 10.879 | 0 | 0 | 318.007 | -7.219 | -7.219
2025-07-09 19:00:00 | 3.18 | 0.59664 | 0 | 0 | 318.007 | 2.5834 | 2.5834
2025-07-09 20:00:00 | 3.24 | 0 | 0 | 0 | 318.007 | 3.24 | 3.24
2025-07-09 21:00:00 | 3.24 | 0 | 0 | 0 | 318.007 | 3.24 | 3.24
2025-07-09 22:00:00 | 3.06 | 0 | 0 | 0 | 318.007 | 3.06 | 3.06
2025-07-09 23:00:00 | 3.12 | 0 | 0 | 0 | 318.007 | 3.12 | 3.12
2025-07-10 00:00:00 | 3.24 | 0 | 0 | 0 | 318.007 | 3.24 | 3.24
2025-07-10 01:00:00 | 3.12 | 0 | 0 | 0 | 318.007 | 3.12 | 3.12
2025-07-10 02:00:00 | 3.24 | 0 | 0 | 0 | 318.007 | 3.24 | 3.24
2025-07-10 03:00:00 | 3.18 | 0 | 0 | 0 | 318.007 | 3.18 | 3.18
2025-07-10 04:00:00 | 3 | 0.49693 | 0 | 0 | 318.007 | 2.5031 | 2.5031
2025-07-10 05:00:00 | 4.44 | 10.7885 | 0 | 0 | 318.007 | -6.3485 | -6.3485
2025-07-10 06:00:00 | 4.92 | 21.443 | 0 | 0 | 318.007 | -16.523 | -16.523
2025-07-10 07:00:00 | 5.04 | 31.7346 | 0 | 0 | 318.007 | -26.6946 | -26.6946
2025-07-10 08:00:00 | 4.32 | 40.9617 | 0 | 0 | 318.007 | -36.6417 | -36.6417
2025-07-10 09:00:00 | 5.22 | 48.4956 | 0 | 0 | 318.007 | -43.2756 | -43.2756
2025-07-10 10:00:00 | 5.28 | 53.8229 | 0 | 0 | 318.007 | -48.5429 | -48.5429
2025-07-10 11:00:00 | 5.7 | 56.5805 | 0 | 0 | 318.007 | -50.8805 | -50.8805
2025-07-10 12:00:00 | 6.12 | 56.5805 | 0 | 0 | 318.007 | -50.4605 | -50.4605
2025-07-10 13:00:00 | 6.72 | 53.8229 | 0 | 0 | 318.007 | -47.1029 | -47.1029
2025-07-10 14:00:00 | 5.82 | 48.4956 | 0 | 0 | 318.007 | -42.6756 | -42.6756
2025-07-10 15:00:00 | 5.52 | 40.9617 | 0 | 0 | 318.007 | -35.4417 | -35.4417
2025-07-10 16:00:00 | 4.02 | 31.7346 | 0 | 0 | 318.007 | -27.7146 | -27.7146
2025-07-10 17:00:00 | 3.84 | 21.443 | 0 | 0 | 318.007 | -17.603 | -17.603
2025-07-10 18:00:00 | 3.96 | 10.7885 | 0 | 0 | 318.007 | -6.8285 | -6.8285
2025-07-10 19:00:00 | 3.24 | 0.49693 | 0 | 0 | 318.007 | 2.7431 | 2.7431
2025-07-10 20:00:00 | 3.66 | 0 | 0 | 0 | 318.007 | 3.66 | 3.66
2025-07-10 21:00:00 | 3.36 | 0 | 0 | 0 | 318.007 | 3.36 | 3.36
2025-07-10 22:00:00 | 3.42 | 0 | 0 | 0 | 318.007 | 3.42 | 3.42
2025-07-10 23:00:00 | 3.42 | 0 | 0 | 0 | 318.007 | 3.42 | 3.42
2025-07-11 00:00:00 | 3.06 | 0 | 0 | 0 | 318.007 | 3.06 | 3.06
2025-07-11 01:00:00 | 3 | 0 | 0 | 0 | 318.007 | 3 | 3
2025-07-11 02:00:00 | 3.36 | 0 | 0 | 0 | 318.007 | 3.36 | 3.36
2025-07-11 03:00:00 | 2.82 | 0 | 0 | 0 | 318.007 | 2.82 | 2.82
2025-07-11 04:00:00 | 3.06 | 0.39195 | 0 | 0 | 318.007 | 2.6681 | 2.6681
2025-07-11 05:00:00 | 3.06 | 10.6931 | 0 | 0 | 318.007 | -7.6331 | -7.6331
2025-07-11 06:00:00 | 4.56 | 21.3576 | 0 | 0 | 318.007 | -16.7976 | -16.7976
2025-07-11 07:00:00 | 5.22 | 31.6588 | 0 | 0 | 318.007 | -26.4388 | -26.4388
2025-07-11 08:00:00 | 5.58 | 40.8945 | 0 | 0 | 318.007 | -35.3145 | -35.3145
2025-07-11 09:00:00 | 5.82 | 48.4355 | 0 | 0 | 318.007 | -42.6155 | -42.6155
2025-07-11 10:00:00 | 5.94 | 53.7678 | 0 | 0 | 318.007 | -47.8278 | -47.8278
2025-07-11 11:00:00 | 6.24 | 56.528 | 0 | 0 | 318.007 | -50.288 | -50.288
2025-07-11 12:00:00 | 5.94 | 56.528 | 0 | 0 | 318.007 | -50.588 | -50.588
2025-07-11 13:00:00 | 15.42 | 53.7678 | 0 | 0 | 318.007 | -38.3478 | -38.3478
2025-07-11 14:00:00 | 19.5 | 48.4355 | 0 | 0 | 318.007 | -28.9355 | -28.9355
2025-07-11 15:00:00 | 18.84 | 40.8945 | 0 | 0 | 318.007 | -22.0545 | -22.0545
2025-07-11 16:00:00 | 15.66 | 31.6588 | 0 | 0 | 318.007 | -15.9988 | -15.9988
2025-07-11 17:00:00 | 3.84 | 21.3576 | 0 | 0 | 318.007 | -17.5176 | -17.5176
2025-07-11 18:00:00 | 3.84 | 10.6931 | 0 | 0 | 318.007 | -6.8531 | -6.8531
2025-07-11 19:00:00 | 3.6 | 0.39195 | 0 | 0 | 318.007 | 3.2081 | 3.2081
2025-07-11 20:00:00 | 3.78 | 0 | 0 | 0 | 318.007 | 3.78 | 3.78
2025-07-11 21:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-11 22:00:00 | 3.84 | 0 | 0 | 0 | 318.007 | 3.84 | 3.84
2025-07-11 23:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-12 00:00:00 | 3.36 | 0 | 0 | 0 | 318.007 | 3.36 | 3.36
2025-07-12 01:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-12 02:00:00 | 3.54 | 0 | 0 | 0 | 318.007 | 3.54 | 3.54
2025-07-12 03:00:00 | 3.36 | 0 | 0 | 0 | 318.007 | 3.36 | 3.36
2025-07-12 04:00:00 | 3.06 | 0.28173 | 0 | 0 | 318.007 | 2.7783 | 2.7783
2025-07-12 05:00:00 | 3.18 | 10.5929 | 0 | 0 | 318.007 | -7.4129 | -7.4129
2025-07-12 06:00:00 | 3.42 | 21.2678 | 0 | 0 | 318.007 | -17.8478 | -17.8478
2025-07-12 07:00:00 | 3.18 | 31.579 | 0 | 0 | 318.007 | -28.399 | -28.399
2025-07-12 08:00:00 | 3.42 | 40.8238 | 0 | 0 | 318.007 | -37.4038 | -37.4038
2025-07-12 09:00:00 | 3.36 | 48.3721 | 0 | 0 | 318.007 | -45.0121 | -45.0121
2025-07-12 10:00:00 | 3.84 | 53.7096 | 0 | 0 | 318.007 | -49.8696 | -49.8696
2025-07-12 11:00:00 | 3.9 | 56.4725 | 0 | 0 | 318.007 | -52.5725 | -52.5725
2025-07-12 12:00:00 | 3.84 | 56.4725 | 0 | 0 | 318.007 | -52.6325 | -52.6325
2025-07-12 13:00:00 | 4.08 | 53.7096 | 0 | 0 | 318.007 | -49.6296 | -49.6296
2025-07-12 14:00:00 | 7.2 | 48.3721 | 0 | 0 | 318.007 | -41.1721 | -41.1721
2025-07-12 15:00:00 | 4.32 | 40.8238 | 0 | 0 | 318.007 | -36.5038 | -36.5038
2025-07-12 16:00:00 | 7.44 | 31.579 | 0 | 0 | 318.007 | -24.139 | -24.139
2025-07-12 17:00:00 | 17.76 | 21.2678 | 0 | 0 | 318.007 | -3.5078 | -3.5078
2025-07-12 18:00:00 | 18.06 | 10.5929 | 0 | 0 | 318.007 | 7.4671 | 7.4671
2025-07-12 19:00:00 | 17.7 | 0.28173 | 0 | 0 | 318.007 | 17.4183 | 17.4183
2025-07-12 20:00:00 | 6.66 | 0 | 0 | 0 | 318.007 | 6.66 | 6.66
2025-07-12 21:00:00 | 4.02 | 0 | 0 | 0 | 318.007 | 4.02 | 4.02
2025-07-12 22:00:00 | 3.54 | 0 | 0 | 0 | 318.007 | 3.54 | 3.54
2025-07-12 23:00:00 | 3.48 | 0 | 0 | 0 | 318.007 | 3.48 | 3.48
2025-07-13 00:00:00 | 3.66 | 0 | 0 | 0 | 318.007 | 3.66 | 3.66
2025-07-13 01:00:00 | 3.3 | 0 | 0 | 0 | 318.007 | 3.3 | 3.3
2025-07-13 02:00:00 | 3.66 | 0 | 0 | 0 | 318.007 | 3.66 | 3.66
2025-07-13 03:00:00 | 3.48 | 0 | 0 | 0 | 318.007 | 3.48 | 3.48
2025-07-13 04:00:00 | 3.18 | 0.1663 | 0 | 0 | 318.007 | 3.0137 | 3.0137
2025-07-13 05:00:00 | 3.3 | 10.4879 | 0 | 0 | 318.007 | -7.1879 | -7.1879
2025-07-13 06:00:00 | 2.94 | 21.1737 | 0 | 0 | 318.007 | -18.2337 | -18.2337
2025-07-13 07:00:00 | 3.48 | 31.4953 | 0 | 0 | 318.007 | -28.0153 | -28.0153
2025-07-13 08:00:00 | 3.12 | 40.7495 | 0 | 0 | 318.007 | -37.6295 | -37.6295
2025-07-13 09:00:00 | 3.36 | 48.3054 | 0 | 0 | 318.007 | -44.9454 | -44.9454
2025-07-13 10:00:00 | 3.72 | 53.6483 | 0 | 0 | 318.007 | -49.9283 | -49.9283
2025-07-13 11:00:00 | 3.78 | 56.414 | 0 | 0 | 318.007 | -52.634 | -52.634
2025-07-13 12:00:00 | 4.02 | 56.414 | 0 | 0 | 318.007 | -52.394 | -52.394
2025-07-13 13:00:00 | 3.96 | 53.6483 | 0 | 0 | 318.007 | -49.6883 | -49.6883
2025-07-13 14:00:00 | 4.44 | 48.3054 | 0 | 0 | 318.007 | -43.8654 | -43.8654
2025-07-13 15:00:00 | 4.02 | 40.7495 | 0 | 0 | 318.007 | -36.7295 | -36.7295
2025-07-13 16:00:00 | 3.9 | 31.4953 | 0 | 0 | 318.007 | -27.5953 | -27.5953
2025-07-13 17:00:00 | 4.08 | 21.1737 | 0 | 0 | 318.007 | -17.0937 | -17.0937
2025-07-13 18:00:00 | 3.66 | 10.4879 | 0 | 0 | 318.007 | -6.8279 | -6.8279
2025-07-13 19:00:00 | 3.48 | 0.1663 | 0 | 0 | 318.007 | 3.3137 | 3.3137
2025-07-13 20:00:00 | 5.1 | 0 | 0 | 0 | 318.007 | 5.1 | 5.1
2025-07-13 21:00:00 | 10.02 | 0 | 0 | 0 | 318.007 | 10.02 | 10.02
2025-07-13 22:00:00 | 9.96 | 0 | 0 | 0 | 318.007 | 9.96 | 9.96
2025-07-13 23:00:00 | 10.02 | 0 | 0 | 0 | 318.007 | 10.02 | 10.02
2025-07-14 00:00:00 | 9.96 | 0 | 0 | 0 | 318.007 | 9.96 | 9.96
2025-07-14 01:00:00 | 9.72 | 0 | 0 | 0 | 318.007 | 9.72 | 9.72
2025-07-14 02:00:00 | 9.9 | 0 | 0 | 0 | 318.007 | 9.9 | 9.9
2025-07-14 03:00:00 | 9.66 | 0 | 0 | 0 | 318.007 | 9.66 | 9.66
2025-07-14 04:00:00 | 10.02 | 0.045702 | 0 | 0 | 318.007 | 9.9743 | 9.9743
2025-07-14 05:00:00 | 8.88 | 10.3782 | 0 | 0 | 318.007 | -1.4982 | -1.4982
2025-07-14 06:00:00 | 4.74 | 21.0752 | 0 | 0 | 318.007 | -16.3352 | -16.3352
2025-07-14 07:00:00 | 4.92 | 31.4077 | 0 | 0 | 318.007 | -26.4877 | -26.4877
2025-07-14 08:00:00 | 5.1 | 40.6715 | 0 | 0 | 318.007 | -35.5715 | -35.5715
2025-07-14 09:00:00 | 5.16 | 48.2354 | 0 | 0 | 318.007 | -43.0754 | -43.0754
2025-07-14 10:00:00 | 5.46 | 53.5839 | 0 | 0 | 318.007 | -48.1239 | -48.1239
2025-07-14 11:00:00 | 6 | 56.3525 | 0 | 0 | 318.007 | -50.3525 | -50.3525
2025-07-14 12:00:00 | 6.36 | 56.3525 | 0 | 0 | 318.007 | -49.9925 | -49.9925
2025-07-14 13:00:00 | 9.3 | 53.5839 | 0 | 0 | 318.007 | -44.2839 | -44.2839
2025-07-14 14:00:00 | 20.76 | 48.2354 | 0 | 0 | 318.007 | -27.4754 | -27.4754
2025-07-14 15:00:00 | 19.44 | 40.6715 | 0 | 0 | 318.007 | -21.2315 | -21.2315
2025-07-14 16:00:00 | 18.48 | 31.4077 | 0 | 0 | 318.007 | -12.9277 | -12.9277
2025-07-14 17:00:00 | 17.88 | 21.0752 | 0 | 0 | 318.007 | -3.1952 | -3.1952
2025-07-14 18:00:00 | 17.82 | 10.3782 | 0 | 7.4418 | 310.5652 | -7.1054e-15 | 7.4418
2025-07-14 19:00:00 | 6.72 | 0.045702 | 0 | 0 | 310.5652 | 6.6743 | 6.6743
2025-07-14 20:00:00 | 4.02 | 0 | 0 | 0 | 310.5652 | 4.02 | 4.02
2025-07-14 21:00:00 | 3.3 | 0 | 0 | 0 | 310.5652 | 3.3 | 3.3
2025-07-14 22:00:00 | 3.36 | 0 | 0 | 0 | 310.5652 | 3.36 | 3.36
2025-07-14 23:00:00 | 3.36 | 0 | 0 | 0 | 310.5652 | 3.36 | 3.36
2025-07-15 00:00:00 | 3.3 | 0 | 0 | 0 | 310.5652 | 3.3 | 3.3
2025-07-15 01:00:00 | 3.3 | 0 | 0 | 0 | 310.5652 | 3.3 | 3.3
2025-07-15 02:00:00 | 2.94 | 0 | 0 | 0 | 310.5652 | 2.94 | 2.94
2025-07-15 03:00:00 | 3.24 | 0 | 0 | 0 | 310.5652 | 3.24 | 3.24
2025-07-15 04:00:00 | 2.94 | 0 | 0 | 0 | 310.5652 | 2.94 | 2.94
2025-07-15 05:00:00 | 4.68 | 10.2637 | 0 | 0 | 310.5652 | -5.5837 | -5.5837
2025-07-15 06:00:00 | 4.68 | 20.9723 | 0 | 0 | 310.5652 | -16.2923 | -16.2923
2025-07-15 07:00:00 | 5.1 | 31.316 | 0 | 0 | 310.5652 | -26.216 | -26.216
2025-07-15 08:00:00 | 5.58 | 40.59 | 0 | 0 | 310.5652 | -35.01 | -35.01
2025-07-15 09:00:00 | 6.18 | 48.1621 | 0 | 0 | 310.5652 | -41.9821 | -41.9821
2025-07-15 10:00:00 | 6.48 | 53.5164 | 0 | 0 | 310.5652 | -47.0364 | -47.0364
2025-07-15 11:00:00 | 6.3 | 56.288 | 0 | 0 | 310.5652 | -49.988 | -49.988
2025-07-15 12:00:00 | 6.42 | 56.288 | 0 | 0 | 310.5652 | -49.868 | -49.868
2025-07-15 13:00:00 | 6.6 | 53.5164 | 0 | 0 | 310.5652 | -46.9164 | -46.9164
2025-07-15 14:00:00 | 6.6 | 48.1621 | 0 | 0 | 310.5652 | -41.5621 | -41.5621
2025-07-15 15:00:00 | 5.82 | 40.59 | 0 | 0 | 310.5652 | -34.77 | -34.77
2025-07-15 16:00:00 | 4.68 | 31.316 | 0 | 0 | 310.5652 | -26.636 | -26.636
2025-07-15 17:00:00 | 4.26 | 20.9723 | 0 | 0 | 310.5652 | -16.7123 | -16.7123
2025-07-15 18:00:00 | 4.08 | 10.2637 | 0 | 0 | 310.5652 | -6.1837 | -6.1837
2025-07-15 19:00:00 | 3.9 | 0 | 0 | 0 | 310.5652 | 3.9 | 3.9
2025-07-15 20:00:00 | 3.78 | 0 | 0 | 0 | 310.5652 | 3.78 | 3.78
2025-07-15 21:00:00 | 3.66 | 0 | 0 | 0 | 310.5652 | 3.66 | 3.66
2025-07-15 22:00:00 | 3.6 | 0 | 0 | 0 | 310.5652 | 3.6 | 3.6
2025-07-15 23:00:00 | 6.66 | 0 | 0 | 0 | 310.5652 | 6.66 | 6.66
2025-07-16 00:00:00 | 9.84 | 0 | 0 | 0 | 310.5652 | 9.84 | 9.84
2025-07-16 01:00:00 | 10.08 | 0 | 0 | 0 | 310.5652 | 10.08 | 10.08
2025-07-16 02:00:00 | 9.66 | 0 | 0 | 0 | 310.5652 | 9.66 | 9.66
2025-07-16 03:00:00 | 10.08 | 0 | 0 | 0 | 310.5652 | 10.08 | 10.08
2025-07-16 04:00:00 | 9.72 | 0 | 0 | 0 | 310.5652 | 9.72 | 9.72
2025-07-16 05:00:00 | 9.54 | 10.1445 | 0 | 0 | 310.5652 | -0.60447 | -0.60447
2025-07-16 06:00:00 | 10.32 | 20.8651 | 0 | 0 | 310.5652 | -10.5451 | -10.5451
2025-07-16 07:00:00 | 6 | 31.2204 | 0 | 0 | 310.5652 | -25.2204 | -25.2204
2025-07-16 08:00:00 | 5.64 | 40.5048 | 0 | 0 | 310.5652 | -34.8648 | -34.8648
2025-07-16 09:00:00 | 6.66 | 48.0854 | 0 | 0 | 310.5652 | -41.4254 | -41.4254
2025-07-16 10:00:00 | 6.96 | 53.4457 | 0 | 0 | 310.5652 | -46.4857 | -46.4857
2025-07-16 11:00:00 | 7.14 | 56.2204 | 0 | 0 | 310.5652 | -49.0804 | -49.0804
2025-07-16 12:00:00 | 7.38 | 56.2204 | 0 | 0 | 310.5652 | -48.8404 | -48.8404
2025-07-16 13:00:00 | 7.2 | 53.4457 | 0 | 0 | 310.5652 | -46.2457 | -46.2457
2025-07-16 14:00:00 | 7.2 | 48.0854 | 0 | 0 | 310.5652 | -40.8854 | -40.8854
2025-07-16 15:00:00 | 6.24 | 40.5048 | 0 | 0 | 310.5652 | -34.2648 | -34.2648
2025-07-16 16:00:00 | 4.62 | 31.2204 | 0 | 0 | 310.5652 | -26.6004 | -26.6004
2025-07-16 17:00:00 | 3.84 | 20.8651 | 0 | 0 | 310.5652 | -17.0251 | -17.0251
2025-07-16 18:00:00 | 3.48 | 10.1445 | 0 | 0 | 310.5652 | -6.6645 | -6.6645
2025-07-16 19:00:00 | 3.66 | 0 | 0 | 0 | 310.5652 | 3.66 | 3.66
2025-07-16 20:00:00 | 3.42 | 0 | 0 | 0 | 310.5652 | 3.42 | 3.42
2025-07-16 21:00:00 | 7.74 | 0 | 0 | 0 | 310.5652 | 7.74 | 7.74
2025-07-16 22:00:00 | 10.14 | 0 | 0 | 0 | 310.5652 | 10.14 | 10.14
2025-07-16 23:00:00 | 10.08 | 0 | 0 | 0 | 310.5652 | 10.08 | 10.08
2025-07-17 00:00:00 | 9.78 | 0 | 0 | 0 | 310.5652 | 9.78 | 9.78
2025-07-17 01:00:00 | 10.02 | 0 | 0 | 0 | 310.5652 | 10.02 | 10.02
2025-07-17 02:00:00 | 10.02 | 0 | 0 | 0 | 310.5652 | 10.02 | 10.02
2025-07-17 03:00:00 | 10.2 | 0 | 0 | 0 | 310.5652 | 10.2 | 10.2
2025-07-17 04:00:00 | 10.08 | 0 | 0 | 0 | 310.5652 | 10.08 | 10.08
2025-07-17 05:00:00 | 9.54 | 10.0206 | 0 | 0 | 310.5652 | -0.48055 | -0.48055
2025-07-17 06:00:00 | 10.08 | 20.7536 | 0 | 0 | 310.5652 | -10.6736 | -10.6736
2025-07-17 07:00:00 | 7.56 | 31.1209 | 0 | 0 | 310.5652 | -23.5609 | -23.5609
2025-07-17 08:00:00 | 5.52 | 40.4159 | 0 | 0 | 310.5652 | -34.8959 | -34.8959
2025-07-17 09:00:00 | 4.98 | 48.0053 | 0 | 0 | 310.5652 | -43.0253 | -43.0253
2025-07-17 10:00:00 | 5.22 | 53.3718 | 0 | 0 | 310.5652 | -48.1518 | -48.1518
2025-07-17 11:00:00 | 4.74 | 56.1497 | 0 | 0 | 310.5652 | -51.4097 | -51.4097
2025-07-17 12:00:00 | 4.56 | 56.1497 | 0 | 0 | 310.5652 | -51.5897 | -51.5897
2025-07-17 13:00:00 | 5.34 | 53.3718 | 0 | 0 | 310.5652 | -48.0318 | -48.0318
2025-07-17 14:00:00 | 4.74 | 48.0053 | 0 | 0 | 310.5652 | -43.2653 | -43.2653
2025-07-17 15:00:00 | 3.72 | 40.4159 | 0 | 0 | 310.5652 | -36.6959 | -36.6959
2025-07-17 16:00:00 | 3.24 | 31.1209 | 0 | 0 | 310.5652 | -27.8809 | -27.8809
2025-07-17 17:00:00 | 2.88 | 20.7536 | 0 | 0 | 310.5652 | -17.8736 | -17.8736
2025-07-17 18:00:00 | 3.18 | 10.0206 | 0 | 0 | 310.5652 | -6.8406 | -6.8406
2025-07-17 19:00:00 | 3.06 | 0 | 0 | 0 | 310.5652 | 3.06 | 3.06
2025-07-17 20:00:00 | 3 | 0 | 0 | 0 | 310.5652 | 3 | 3
2025-07-17 21:00:00 | 2.88 | 0 | 0 | 0 | 310.5652 | 2.88 | 2.88
2025-07-17 22:00:00 | 3.24 | 0 | 0 | 0 | 310.5652 | 3.24 | 3.24
2025-07-17 23:00:00 | 3 | 0 | 0 | 0 | 310.5652 | 3 | 3
2025-07-18 00:00:00 | 3.18 | 0 | 0 | 0 | 310.5652 | 3.18 | 3.18
2025-07-18 01:00:00 | 3.24 | 0 | 0 | 0 | 310.5652 | 3.24 | 3.24
2025-07-18 02:00:00 | 3.3 | 0 | 0 | 0 | 310.5652 | 3.3 | 3.3
2025-07-18 03:00:00 | 4.02 | 0 | 0 | 0 | 310.5652 | 4.02 | 4.02
2025-07-18 04:00:00 | 3.78 | 0 | 0 | 0 | 310.5652 | 3.78 | 3.78
2025-07-18 05:00:00 | 3.72 | 9.892 | 0 | 0 | 310.5652 | -6.172 | -6.172
2025-07-18 06:00:00 | 8.04 | 20.6377 | 0 | 0 | 310.5652 | -12.5977 | -12.5977
2025-07-18 07:00:00 | 11.46 | 31.0173 | 0 | 0 | 310.5652 | -19.5573 | -19.5573
2025-07-18 08:00:00 | 11.4 | 40.3234 | 0 | 0 | 310.5652 | -28.9234 | -28.9234
2025-07-18 09:00:00 | 5.7 | 47.9218 | 0 | 0 | 310.5652 | -42.2218 | -42.2218
2025-07-18 10:00:00 | 4.14 | 53.2947 | 0 | 0 | 310.5652 | -49.1547 | -49.1547
2025-07-18 11:00:00 | 4.02 | 56.0759 | 0 | 0 | 310.5652 | -52.0559 | -52.0559
2025-07-18 12:00:00 | 4.32 | 56.0759 | 0 | 0 | 310.5652 | -51.7559 | -51.7559
2025-07-18 13:00:00 | 4.44 | 53.2947 | 0 | 0 | 310.5652 | -48.8547 | -48.8547
2025-07-18 14:00:00 | 4.68 | 47.9218 | 0 | 0 | 310.5652 | -43.2418 | -43.2418
2025-07-18 15:00:00 | 4.32 | 40.3234 | 0 | 0 | 310.5652 | -36.0034 | -36.0034
2025-07-18 16:00:00 | 3.36 | 31.0173 | 0 | 0 | 310.5652 | -27.6573 | -27.6573
2025-07-18 17:00:00 | 3 | 20.6377 | 0 | 0 | 310.5652 | -17.6377 | -17.6377
2025-07-18 18:00:00 | 3.24 | 9.892 | 0 | 0 | 310.5652 | -6.652 | -6.652
2025-07-18 19:00:00 | 2.76 | 0 | 0 | 0 | 310.5652 | 2.76 | 2.76
2025-07-18 20:00:00 | 3 | 0 | 0 | 0 | 310.5652 | 3 | 3
2025-07-18 21:00:00 | 3 | 0 | 0 | 0 | 310.5652 | 3 | 3
2025-07-18 22:00:00 | 3.24 | 0 | 0 | 0 | 310.5652 | 3.24 | 3.24
2025-07-18 23:00:00 | 3.12 | 0 | 0 | 0 | 310.5652 | 3.12 | 3.12
2025-07-19 00:00:00 | 6.06 | 0 | 0 | 0 | 310.5652 | 6.06 | 6.06
2025-07-19 01:00:00 | 11.94 | 0 | 0 | 0 | 310.5652 | 11.94 | 11.94
2025-07-19 02:00:00 | 11.7 | 0 | 0 | 0 | 310.5652 | 11.7 | 11.7
2025-07-19 03:00:00 | 11.82 | 0 | 0 | 0 | 310.5652 | 11.82 | 11.82
2025-07-19 04:00:00 | 12.06 | 0 | 0 | 0 | 310.5652 | 12.06 | 12.06
2025-07-19 05:00:00 | 12.3 | 9.7587 | 0 | 0 | 310.5652 | 2.5413 | 2.5413
2025-07-19 06:00:00 | 11.34 | 20.5176 | 0 | 0 | 310.5652 | -9.1776 | -9.1776
2025-07-19 07:00:00 | 11.28 | 30.9098 | 0 | 0 | 310.5652 | -19.6298 | -19.6298
2025-07-19 08:00:00 | 11.1 | 40.2273 | 0 | 0 | 310.5652 | -29.1273 | -29.1273
2025-07-19 09:00:00 | 11.22 | 47.8349 | 0 | 0 | 310.5652 | -36.6149 | -36.6149
2025-07-19 10:00:00 | 11.28 | 53.2143 | 0 | 0 | 310.5652 | -41.9343 | -41.9343
2025-07-19 11:00:00 | 11.1 | 55.9989 | 0 | 0 | 310.5652 | -44.8989 | -44.8989
2025-07-19 12:00:00 | 11.94 | 55.9989 | 0 | 0 | 310.5652 | -44.0589 | -44.0589
2025-07-19 13:00:00 | 15.42 | 53.2143 | 0 | 0 | 310.5652 | -37.7943 | -37.7943
2025-07-19 14:00:00 | 17.34 | 47.8349 | 0 | 0 | 310.5652 | -30.4949 | -30.4949
2025-07-19 15:00:00 | 17.46 | 40.2273 | 0 | 0 | 310.5652 | -22.7673 | -22.7673
2025-07-19 16:00:00 | 17.52 | 30.9098 | 0 | 0 | 310.5652 | -13.3898 | -13.3898
2025-07-19 17:00:00 | 17.52 | 20.5176 | 0 | 0 | 310.5652 | -2.9976 | -2.9976
2025-07-19 18:00:00 | 3.78 | 9.7587 | 0 | 0 | 310.5652 | -5.9787 | -5.9787
2025-07-19 19:00:00 | 3 | 0 | 0 | 0 | 310.5652 | 3 | 3
2025-07-19 20:00:00 | 2.94 | 0 | 0 | 0 | 310.5652 | 2.94 | 2.94
2025-07-19 21:00:00 | 3.24 | 0 | 0 | 0 | 310.5652 | 3.24 | 3.24
2025-07-19 22:00:00 | 3.3 | 0 | 0 | 0 | 310.5652 | 3.3 | 3.3
2025-07-19 23:00:00 | 3.06 | 0 | 0 | 0 | 310.5652 | 3.06 | 3.06
2025-07-20 00:00:00 | 3 | 0 | 0 | 0 | 310.5652 | 3 | 3
2025-07-20 01:00:00 | 3.12 | 0 | 0 | 0 | 310.5652 | 3.12 | 3.12
2025-07-20 02:00:00 | 3.18 | 0 | 0 | 0 | 310.5652 | 3.18 | 3.18
2025-07-20 03:00:00 | 2.94 | 0 | 0 | 0 | 310.5652 | 2.94 | 2.94
2025-07-20 04:00:00 | 3.06 | 0 | 0 | 0 | 310.5652 | 3.06 | 3.06
2025-07-20 05:00:00 | 2.88 | 9.6209 | 0 | 0 | 310.5652 | -6.7409 | -6.7409
2025-07-20 06:00:00 | 3 | 20.3932 | 0 | 0 | 310.5652 | -17.3932 | -17.3932
2025-07-20 07:00:00 | 2.94 | 30.7984 | 0 | 0 | 310.5652 | -27.8584 | -27.8584
2025-07-20 08:00:00 | 3.06 | 40.1274 | 0 | 0 | 310.5652 | -37.0674 | -37.0674
2025-07-20 09:00:00 | 3.06 | 47.7446 | 0 | 0 | 310.5652 | -44.6846 | -44.6846
2025-07-20 10:00:00 | 2.94 | 53.1307 | 0 | 0 | 310.5652 | -50.1907 | -50.1907
2025-07-20 11:00:00 | 3 | 55.9188 | 0 | 0 | 310.5652 | -52.9188 | -52.9188
2025-07-20 12:00:00 | 3.06 | 55.9188 | 0 | 0 | 310.5652 | -52.8588 | -52.8588
2025-07-20 13:00:00 | 3.06 | 53.1307 | 0 | 0 | 310.5652 | -50.0707 | -50.0707
2025-07-20 14:00:00 | 3.18 | 47.7446 | 0 | 0 | 310.5652 | -44.5646 | -44.5646
2025-07-20 15:00:00 | 3 | 40.1274 | 0 | 0 | 310.5652 | -37.1274 | -37.1274
2025-07-20 16:00:00 | 3.3 | 30.7984 | 0 | 0 | 310.5652 | -27.4984 | -27.4984
2025-07-20 17:00:00 | 3 | 20.3932 | 0 | 0 | 310.5652 | -17.3932 | -17.3932
2025-07-20 18:00:00 | 3.24 | 9.6209 | 0 | 0 | 310.5652 | -6.3809 | -6.3809
2025-07-20 19:00:00 | 3.06 | 0 | 0 | 0 | 310.5652 | 3.06 | 3.06
2025-07-20 20:00:00 | 3 | 0 | 0 | 0 | 310.5652 | 3 | 3
2025-07-20 21:00:00 | 3.12 | 0 | 0 | 0 | 310.5652 | 3.12 | 3.12
2025-07-20 22:00:00 | 3.06 | 0 | 0 | 0 | 310.5652 | 3.06 | 3.06
2025-07-20 23:00:00 | 3.06 | 0 | 0 | 0 | 310.5652 | 3.06 | 3.06
2025-07-21 00:00:00 | 3.12 | 0 | 0 | 0 | 310.5652 | 3.12 | 3.12
2025-07-21 01:00:00 | 3 | 0 | 0 | 0 | 310.5652 | 3 | 3
2025-07-21 02:00:00 | 3.06 | 0 | 0 | 0 | 310.5652 | 3.06 | 3.06
2025-07-21 03:00:00 | 3.12 | 0 | 0 | 0 | 310.5652 | 3.12 | 3.12
2025-07-21 04:00:00 | 3.12 | 0 | 0 | 0 | 310.5652 | 3.12 | 3.12
2025-07-21 05:00:00 | 3.42 | 9.4785 | 0 | 0 | 310.5652 | -6.0585 | -6.0585
2025-07-21 06:00:00 | 4.56 | 20.2645 | 0 | 0 | 310.5652 | -15.7045 | -15.7045
2025-07-21 07:00:00 | 4.98 | 30.6829 | 0 | 0 | 310.5652 | -25.7029 | -25.7029
2025-07-21 08:00:00 | 5.34 | 40.0239 | 0 | 0 | 310.5652 | -34.6839 | -34.6839
2025-07-21 09:00:00 | 5.16 | 47.6507 | 0 | 0 | 310.5652 | -42.4907 | -42.4907
2025-07-21 10:00:00 | 5.46 | 53.0437 | 0 | 0 | 310.5652 | -47.5837 | -47.5837
2025-07-21 11:00:00 | 5.52 | 55.8354 | 0 | 0 | 310.5652 | -50.3154 | -50.3154
2025-07-21 12:00:00 | 5.4 | 55.8354 | 0 | 0 | 310.5652 | -50.4354 | -50.4354
2025-07-21 13:00:00 | 5.58 | 53.0437 | 0 | 0 | 310.5652 | -47.4637 | -47.4637
2025-07-21 14:00:00 | 5.82 | 47.6507 | 0 | 0 | 310.5652 | -41.8307 | -41.8307
2025-07-21 15:00:00 | 4.2 | 40.0239 | 0 | 0 | 310.5652 | -35.8239 | -35.8239
2025-07-21 16:00:00 | 8.58 | 30.6829 | 0 | 0 | 310.5652 | -22.1029 | -22.1029
2025-07-21 17:00:00 | 8.04 | 20.2645 | 0 | 0 | 310.5652 | -12.2245 | -12.2245
2025-07-21 18:00:00 | 3.12 | 9.4785 | 0 | 0 | 310.5652 | -6.3585 | -6.3585
2025-07-21 19:00:00 | 3 | 0 | 0 | 0 | 310.5652 | 3 | 3
2025-07-21 20:00:00 | 3.42 | 0 | 0 | 0 | 310.5652 | 3.42 | 3.42
2025-07-21 21:00:00 | 3.18 | 0 | 0 | 0 | 310.5652 | 3.18 | 3.18
2025-07-21 22:00:00 | 3.18 | 0 | 0 | 0 | 310.5652 | 3.18 | 3.18
2025-07-21 23:00:00 | 3.3 | 0 | 0 | 0 | 310.5652 | 3.3 | 3.3
2025-07-22 00:00:00 | 3.36 | 0 | 0 | 0 | 310.5652 | 3.36 | 3.36
2025-07-22 01:00:00 | 3.66 | 0 | 0 | 0 | 310.5652 | 3.66 | 3.66
2025-07-22 02:00:00 | 3.84 | 0 | 0 | 0 | 310.5652 | 3.84 | 3.84
2025-07-22 03:00:00 | 4.2 | 0 | 0 | 0 | 310.5652 | 4.2 | 4.2
2025-07-22 04:00:00 | 4.08 | 0 | 0 | 0 | 310.5652 | 4.08 | 4.08
2025-07-22 05:00:00 | 3.78 | 9.3315 | 0 | 0 | 310.5652 | -5.5515 | -5.5515
2025-07-22 06:00:00 | 4.56 | 20.1315 | 0 | 0 | 310.5652 | -15.5715 | -15.5715
2025-07-22 07:00:00 | 5.22 | 30.5636 | 0 | 0 | 310.5652 | -25.3436 | -25.3436
2025-07-22 08:00:00 | 5.4 | 39.9166 | 0 | 0 | 310.5652 | -34.5166 | -34.5166
2025-07-22 09:00:00 | 5.34 | 47.5534 | 0 | 0 | 310.5652 | -42.2134 | -42.2134
2025-07-22 10:00:00 | 5.28 | 52.9534 | 0 | 0 | 310.5652 | -47.6734 | -47.6734
2025-07-22 11:00:00 | 5.64 | 55.7487 | 0 | 0 | 310.5652 | -50.1087 | -50.1087
2025-07-22 12:00:00 | 5.1 | 55.7487 | 0 | 0 | 310.5652 | -50.6487 | -50.6487
2025-07-22 13:00:00 | 5.82 | 52.9534 | 0 | 0 | 310.5652 | -47.1334 | -47.1334
2025-07-22 14:00:00 | 5.88 | 47.5534 | 0 | 0 | 310.5652 | -41.6734 | -41.6734
2025-07-22 15:00:00 | 5.4 | 39.9166 | 0 | 0 | 310.5652 | -34.5166 | -34.5166
2025-07-22 16:00:00 | 4.02 | 30.5636 | 0 | 0 | 310.5652 | -26.5436 | -26.5436
2025-07-22 17:00:00 | 3.3 | 20.1315 | 0 | 0 | 310.5652 | -16.8315 | -16.8315
2025-07-22 18:00:00 | 3.36 | 9.3315 | 0 | 0 | 310.5652 | -5.9715 | -5.9715
2025-07-22 19:00:00 | 3.06 | 0 | 0 | 0 | 310.5652 | 3.06 | 3.06
2025-07-22 20:00:00 | 3.06 | 0 | 0 | 0 | 310.5652 | 3.06 | 3.06
2025-07-22 21:00:00 | 3.36 | 0 | 0 | 0 | 310.5652 | 3.36 | 3.36
2025-07-22 22:00:00 | 8.34 | 0 | 0 | 0 | 310.5652 | 8.34 | 8.34
2025-07-22 23:00:00 | 9.6 | 0 | 0 | 0 | 310.5652 | 9.6 | 9.6
2025-07-23 00:00:00 | 9.72 | 0 | 0 | 0 | 310.5652 | 9.72 | 9.72
2025-07-23 01:00:00 | 9.54 | 0 | 0 | 0 | 310.5652 | 9.54 | 9.54
2025-07-23 02:00:00 | 9.66 | 0 | 0 | 0 | 310.5652 | 9.66 | 9.66
2025-07-23 03:00:00 | 9.84 | 0 | 0 | 0 | 310.5652 | 9.84 | 9.84
2025-07-23 04:00:00 | 9.78 | 0 | 0 | 0 | 310.5652 | 9.78 | 9.78
2025-07-23 05:00:00 | 3.24 | 9.1801 | 0 | 0 | 310.5652 | -5.9401 | -5.9401
2025-07-23 06:00:00 | 4.26 | 19.9944 | 0 | 0 | 310.5652 | -15.7344 | -15.7344
2025-07-23 07:00:00 | 4.08 | 30.4402 | 0 | 0 | 310.5652 | -26.3602 | -26.3602
2025-07-23 08:00:00 | 4.14 | 39.8057 | 0 | 0 | 310.5652 | -35.6657 | -35.6657
2025-07-23 09:00:00 | 4.56 | 47.4526 | 0 | 0 | 310.5652 | -42.8926 | -42.8926
2025-07-23 10:00:00 | 4.38 | 52.8597 | 0 | 0 | 310.5652 | -48.4797 | -48.4797
2025-07-23 11:00:00 | 4.38 | 55.6587 | 0 | 0 | 310.5652 | -51.2787 | -51.2787
2025-07-23 12:00:00 | 4.92 | 55.6587 | 0 | 0 | 310.5652 | -50.7387 | -50.7387
2025-07-23 13:00:00 | 5.52 | 52.8597 | 0 | 0 | 310.5652 | -47.3397 | -47.3397
2025-07-23 14:00:00 | 5.64 | 47.4526 | 0 | 0 | 310.5652 | -41.8126 | -41.8126
2025-07-23 15:00:00 | 5.22 | 39.8057 | 0 | 0 | 310.5652 | -34.5857 | -34.5857
2025-07-23 16:00:00 | 4.2 | 30.4402 | 0 | 0 | 310.5652 | -26.2402 | -26.2402
2025-07-23 17:00:00 | 4.14 | 19.9944 | 0 | 0 | 310.5652 | -15.8544 | -15.8544
2025-07-23 18:00:00 | 4.5 | 9.1801 | 0 | 0 | 310.5652 | -4.6801 | -4.6801
2025-07-23 19:00:00 | 3.84 | 0 | 0 | 0 | 310.5652 | 3.84 | 3.84
2025-07-23 20:00:00 | 4.14 | 0 | 0 | 0 | 310.5652 | 4.14 | 4.14
2025-07-23 21:00:00 | 4.44 | 0 | 0 | 0 | 310.5652 | 4.44 | 4.44
2025-07-23 22:00:00 | 4.5 | 0 | 0 | 0 | 310.5652 | 4.5 | 4.5
2025-07-23 23:00:00 | 4.5 | 0 | 0 | 0 | 310.5652 | 4.5 | 4.5
2025-07-24 00:00:00 | 4.5 | 0 | 0 | 0 | 310.5652 | 4.5 | 4.5
2025-07-24 01:00:00 | 4.56 | 0 | 0 | 0 | 310.5652 | 4.56 | 4.56
2025-07-24 02:00:00 | 4.38 | 0 | 0 | 0 | 310.5652 | 4.38 | 4.38
2025-07-24 03:00:00 | 4.38 | 0 | 0 | 0 | 310.5652 | 4.38 | 4.38
2025-07-24 04:00:00 | 4.32 | 0 | 0 | 0 | 310.5652 | 4.32 | 4.32
2025-07-24 05:00:00 | 4.44 | 9.0241 | 0 | 0 | 310.5652 | -4.5841 | -4.5841
2025-07-24 06:00:00 | 4.44 | 19.853 | 0 | 0 | 310.5652 | -15.413 | -15.413
2025-07-24 07:00:00 | 4.8 | 30.3129 | 0 | 0 | 310.5652 | -25.5129 | -25.5129
2025-07-24 08:00:00 | 5.22 | 39.691 | 0 | 0 | 310.5652 | -34.471 | -34.471
2025-07-24 09:00:00 | 5.1 | 47.3482 | 0 | 0 | 310.5652 | -42.2482 | -42.2482
2025-07-24 10:00:00 | 4.8 | 52.7626 | 0 | 0 | 310.5652 | -47.9626 | -47.9626
2025-07-24 11:00:00 | 4.86 | 55.5654 | 0 | 0 | 310.5652 | -50.7054 | -50.7054
2025-07-24 12:00:00 | 5.76 | 55.5654 | 0 | 0 | 310.5652 | -49.8054 | -49.8054
2025-07-24 13:00:00 | 6.06 | 52.7626 | 0 | 0 | 310.5652 | -46.7026 | -46.7026
2025-07-24 14:00:00 | 5.52 | 47.3482 | 0 | 0 | 310.5652 | -41.8282 | -41.8282
2025-07-24 15:00:00 | 4.74 | 39.691 | 0 | 0 | 310.5652 | -34.951 | -34.951
2025-07-24 16:00:00 | 4.32 | 30.3129 | 0 | 0 | 310.5652 | -25.9929 | -25.9929
2025-07-24 17:00:00 | 4.02 | 19.853 | 0 | 0 | 310.5652 | -15.833 | -15.833
2025-07-24 18:00:00 | 3.84 | 9.0241 | 0 | 0 | 310.5652 | -5.1841 | -5.1841
2025-07-24 19:00:00 | 3.78 | 0 | 0 | 0 | 310.5652 | 3.78 | 3.78
2025-07-24 20:00:00 | 3.84 | 0 | 0 | 0 | 310.5652 | 3.84 | 3.84
2025-07-24 21:00:00 | 4.26 | 0 | 0 | 0 | 310.5652 | 4.26 | 4.26
2025-07-24 22:00:00 | 4.56 | 0 | 0 | 0 | 310.5652 | 4.56 | 4.56
2025-07-24 23:00:00 | 4.92 | 0 | 0 | 0 | 310.5652 | 4.92 | 4.92
2025-07-25 00:00:00 | 4.38 | 0 | 0 | 0 | 310.5652 | 4.38 | 4.38
2025-07-25 01:00:00 | 4.5 | 0 | 0 | 0 | 310.5652 | 4.5 | 4.5
2025-07-25 02:00:00 | 4.5 | 0 | 0 | 0 | 310.5652 | 4.5 | 4.5
2025-07-25 03:00:00 | 4.68 | 0 | 0 | 0 | 310.5652 | 4.68 | 4.68
2025-07-25 04:00:00 | 4.56 | 0 | 0 | 0 | 310.5652 | 4.56 | 4.56
2025-07-25 05:00:00 | 4.44 | 8.8637 | 0 | 0 | 310.5652 | -4.4237 | -4.4237
2025-07-25 06:00:00 | 4.74 | 19.7075 | 0 | 0 | 310.5652 | -14.9675 | -14.9675
2025-07-25 07:00:00 | 5.46 | 30.1817 | 0 | 0 | 310.5652 | -24.7217 | -24.7217
2025-07-25 08:00:00 | 5.16 | 39.5726 | 0 | 0 | 310.5652 | -34.4126 | -34.4126
2025-07-25 09:00:00 | 5.34 | 47.2403 | 0 | 0 | 310.5652 | -41.9003 | -41.9003
2025-07-25 10:00:00 | 6 | 52.6621 | 0 | 0 | 310.5652 | -46.6621 | -46.6621
2025-07-25 11:00:00 | 6.18 | 55.4687 | 0 | 0 | 310.5652 | -49.2887 | -49.2887
2025-07-25 12:00:00 | 5.64 | 55.4687 | 0 | 0 | 310.5652 | -49.8287 | -49.8287
2025-07-25 13:00:00 | 6 | 52.6621 | 0 | 0 | 310.5652 | -46.6621 | -46.6621
2025-07-25 14:00:00 | 6.78 | 47.2403 | 0 | 0 | 310.5652 | -40.4603 | -40.4603
2025-07-25 15:00:00 | 6.48 | 39.5726 | 0 | 0 | 310.5652 | -33.0926 | -33.0926
2025-07-25 16:00:00 | 5.34 | 30.1817 | 0 | 0 | 310.5652 | -24.8417 | -24.8417
2025-07-25 17:00:00 | 5.34 | 19.7075 | 0 | 0 | 310.5652 | -14.3675 | -14.3675
2025-07-25 18:00:00 | 5.16 | 8.8637 | 0 | 0 | 310.5652 | -3.7037 | -3.7037
2025-07-25 19:00:00 | 5.04 | 0 | 0 | 0 | 310.5652 | 5.04 | 5.04
2025-07-25 20:00:00 | 5.28 | 0 | 0 | 0 | 310.5652 | 5.28 | 5.28
2025-07-25 21:00:00 | 5.7 | 0 | 0 | 0 | 310.5652 | 5.7 | 5.7
2025-07-25 22:00:00 | 5.16 | 0 | 0 | 0 | 310.5652 | 5.16 | 5.16
2025-07-25 23:00:00 | 5.7 | 0 | 0 | 0 | 310.5652 | 5.7 | 5.7
2025-07-26 00:00:00 | 5.16 | 0 | 0 | 0 | 310.5652 | 5.16 | 5.16
2025-07-26 01:00:00 | 5.16 | 0 | 0 | 0 | 310.5652 | 5.16 | 5.16
2025-07-26 02:00:00 | 5.22 | 0 | 0 | 0 | 310.5652 | 5.22 | 5.22
2025-07-26 03:00:00 | 5.4 | 0 | 0 | 0 | 310.5652 | 5.4 | 5.4
2025-07-26 04:00:00 | 5.46 | 0 | 0 | 0 | 310.5652 | 5.46 | 5.46
2025-07-26 05:00:00 | 4.98 | 8.699 | 0 | 0 | 310.5652 | -3.719 | -3.719
2025-07-26 06:00:00 | 5.04 | 19.5577 | 0 | 0 | 310.5652 | -14.5177 | -14.5177
2025-07-26 07:00:00 | 5.16 | 30.0465 | 0 | 0 | 310.5652 | -24.8865 | -24.8865
2025-07-26 08:00:00 | 4.98 | 39.4504 | 0 | 0 | 310.5652 | -34.4704 | -34.4704
2025-07-26 09:00:00 | 5.46 | 47.1287 | 0 | 0 | 310.5652 | -41.6687 | -41.6687
2025-07-26 10:00:00 | 5.16 | 52.5581 | 0 | 0 | 310.5652 | -47.3981 | -47.3981
2025-07-26 11:00:00 | 5.28 | 55.3686 | 0 | 0 | 310.5652 | -50.0886 | -50.0886
2025-07-26 12:00:00 | 15.48 | 55.3686 | 0 | 0 | 310.5652 | -39.8886 | -39.8886
2025-07-26 13:00:00 | 18.78 | 52.5581 | 0 | 0 | 310.5652 | -33.7781 | -33.7781
2025-07-26 14:00:00 | 15.42 | 47.1287 | 0 | 0 | 310.5652 | -31.7087 | -31.7087
2025-07-26 15:00:00 | 19.92 | 39.4504 | 0 | 0 | 310.5652 | -19.5304 | -19.5304
2025-07-26 16:00:00 | 8.58 | 30.0465 | 0 | 0 | 310.5652 | -21.4665 | -21.4665
2025-07-26 17:00:00 | 5.34 | 19.5577 | 0 | 0 | 310.5652 | -14.2177 | -14.2177
2025-07-26 18:00:00 | 5.4 | 8.699 | 0 | 0 | 310.5652 | -3.299 | -3.299
2025-07-26 19:00:00 | 5.7 | 0 | 0 | 0 | 310.5652 | 5.7 | 5.7
2025-07-26 20:00:00 | 5.58 | 0 | 0 | 0 | 310.5652 | 5.58 | 5.58
2025-07-26 21:00:00 | 5.34 | 0 | 0 | 0 | 310.5652 | 5.34 | 5.34
2025-07-26 22:00:00 | 5.52 | 0 | 0 | 0 | 310.5652 | 5.52 | 5.52
2025-07-26 23:00:00 | 5.4 | 0 | 0 | 0 | 310.5652 | 5.4 | 5.4
2025-07-27 00:00:00 | 5.58 | 0 | 0 | 0 | 310.5652 | 5.58 | 5.58
2025-07-27 01:00:00 | 5.4 | 0 | 0 | 0 | 310.5652 | 5.4 | 5.4
2025-07-27 02:00:00 | 5.34 | 0 | 0 | 0 | 310.5652 | 5.34 | 5.34
2025-07-27 03:00:00 | 5.16 | 0 | 0 | 0 | 310.5652 | 5.16 | 5.16
2025-07-27 04:00:00 | 5.52 | 0 | 0 | 0 | 310.5652 | 5.52 | 5.52
2025-07-27 05:00:00 | 5.4 | 8.5299 | 0 | 0 | 310.5652 | -3.1299 | -3.1299
2025-07-27 06:00:00 | 5.22 | 19.4039 | 0 | 0 | 310.5652 | -14.1839 | -14.1839
2025-07-27 07:00:00 | 5.22 | 29.9073 | 0 | 0 | 310.5652 | -24.6873 | -24.6873
2025-07-27 08:00:00 | 14.64 | 39.3245 | 0 | 0 | 310.5652 | -24.6845 | -24.6845
2025-07-27 09:00:00 | 19.26 | 47.0136 | 0 | 0 | 310.5652 | -27.7536 | -27.7536
2025-07-27 10:00:00 | 19.44 | 52.4506 | 0 | 0 | 310.5652 | -33.0106 | -33.0106
2025-07-27 11:00:00 | 18.3 | 55.265 | 0 | 0 | 310.5652 | -36.965 | -36.965
2025-07-27 12:00:00 | 11.34 | 55.265 | 0 | 0 | 310.5652 | -43.925 | -43.925
2025-07-27 13:00:00 | 5.46 | 52.4506 | 0 | 0 | 310.5652 | -46.9906 | -46.9906
2025-07-27 14:00:00 | 5.28 | 47.0136 | 0 | 0 | 310.5652 | -41.7336 | -41.7336
2025-07-27 15:00:00 | 5.28 | 39.3245 | 0 | 0 | 310.5652 | -34.0445 | -34.0445
2025-07-27 16:00:00 | 5.1 | 29.9073 | 0 | 0 | 310.5652 | -24.8073 | -24.8073
2025-07-27 17:00:00 | 5.46 | 19.4039 | 0 | 0 | 310.5652 | -13.9439 | -13.9439
2025-07-27 18:00:00 | 5.34 | 8.5299 | 0 | 0 | 310.5652 | -3.1899 | -3.1899
2025-07-27 19:00:00 | 4.98 | 0 | 0 | 0 | 310.5652 | 4.98 | 4.98
2025-07-27 20:00:00 | 5.4 | 0 | 0 | 0 | 310.5652 | 5.4 | 5.4
2025-07-27 21:00:00 | 5.28 | 0 | 0 | 0 | 310.5652 | 5.28 | 5.28
2025-07-27 22:00:00 | 5.46 | 0 | 0 | 0 | 310.5652 | 5.46 | 5.46
2025-07-27 23:00:00 | 5.4 | 0 | 0 | 0 | 310.5652 | 5.4 | 5.4
2025-07-28 00:00:00 | 5.7 | 0 | 0 | 0 | 310.5652 | 5.7 | 5.7
2025-07-28 01:00:00 | 5.16 | 0 | 0 | 0 | 310.5652 | 5.16 | 5.16
2025-07-28 02:00:00 | 5.28 | 0 | 0 | 0 | 310.5652 | 5.28 | 5.28
2025-07-28 03:00:00 | 5.4 | 0 | 0 | 0 | 310.5652 | 5.4 | 5.4
2025-07-28 04:00:00 | 5.88 | 0 | 0 | 0 | 310.5652 | 5.88 | 5.88
2025-07-28 05:00:00 | 7.2 | 8.3564 | 0 | 0 | 310.5652 | -1.1564 | -1.1564
2025-07-28 06:00:00 | 6.54 | 19.2459 | 0 | 0 | 310.5652 | -12.7059 | -12.7059
2025-07-28 07:00:00 | 6.48 | 29.7643 | 0 | 0 | 310.5652 | -23.2843 | -23.2843
2025-07-28 08:00:00 | 7.32 | 39.1948 | 0 | 0 | 310.5652 | -31.8748 | -31.8748
2025-07-28 09:00:00 | 7.8 | 46.8948 | 0 | 0 | 310.5652 | -39.0948 | -39.0948
2025-07-28 10:00:00 | 7.56 | 52.3396 | 0 | 0 | 310.5652 | -44.7796 | -44.7796
2025-07-28 11:00:00 | 7.44 | 55.158 | 0 | 0 | 310.5652 | -47.718 | -47.718
2025-07-28 12:00:00 | 8.22 | 55.158 | 0 | 0 | 310.5652 | -46.938 | -46.938
2025-07-28 13:00:00 | 7.44 | 52.3396 | 0 | 0 | 310.5652 | -44.8996 | -44.8996
2025-07-28 14:00:00 | 6.9 | 46.8948 | 0 | 0 | 310.5652 | -39.9948 | -39.9948
2025-07-28 15:00:00 | 5.4 | 39.1948 | 0 | 0 | 310.5652 | -33.7948 | -33.7948
2025-07-28 16:00:00 | 5.34 | 29.7643 | 0 | 0 | 310.5652 | -24.4243 | -24.4243
2025-07-28 17:00:00 | 4.74 | 19.2459 | 0 | 0 | 310.5652 | -14.5059 | -14.5059
2025-07-28 18:00:00 | 4.86 | 8.3564 | 0 | 0 | 310.5652 | -3.4964 | -3.4964
2025-07-28 19:00:00 | 4.86 | 0 | 0 | 0 | 310.5652 | 4.86 | 4.86
2025-07-28 20:00:00 | 4.8 | 0 | 0 | 0 | 310.5652 | 4.8 | 4.8
2025-07-28 21:00:00 | 4.68 | 0 | 0 | 0 | 310.5652 | 4.68 | 4.68
2025-07-28 22:00:00 | 4.68 | 0 | 0 | 0 | 310.5652 | 4.68 | 4.68
2025-07-28 23:00:00 | 4.26 | 0 | 0 | 0 | 310.5652 | 4.26 | 4.26
2025-07-29 00:00:00 | 4.92 | 0 | 0 | 0 | 310.5652 | 4.92 | 4.92
2025-07-29 01:00:00 | 4.44 | 0 | 0 | 0 | 310.5652 | 4.44 | 4.44
2025-07-29 02:00:00 | 4.32 | 0 | 0 | 0 | 310.5652 | 4.32 | 4.32
2025-07-29 03:00:00 | 4.38 | 0 | 0 | 0 | 310.5652 | 4.38 | 4.38
2025-07-29 04:00:00 | 4.38 | 0 | 0 | 0 | 310.5652 | 4.38 | 4.38
2025-07-29 05:00:00 | 4.68 | 8.1787 | 0 | 0 | 310.5652 | -3.4987 | -3.4987
2025-07-29 06:00:00 | 5.58 | 19.0838 | 0 | 0 | 310.5652 | -13.5038 | -13.5038
2025-07-29 07:00:00 | 6.96 | 29.6173 | 0 | 0 | 310.5652 | -22.6573 | -22.6573
2025-07-29 08:00:00 | 7.02 | 39.0614 | 0 | 0 | 310.5652 | -32.0414 | -32.0414
2025-07-29 09:00:00 | 7.56 | 46.7724 | 0 | 0 | 310.5652 | -39.2124 | -39.2124
2025-07-29 10:00:00 | 8.4 | 52.225 | 0 | 0 | 310.5652 | -43.825 | -43.825
2025-07-29 11:00:00 | 7.56 | 55.0474 | 0 | 0 | 310.5652 | -47.4874 | -47.4874
2025-07-29 12:00:00 | 8.1 | 55.0474 | 0 | 0 | 310.5652 | -46.9474 | -46.9474
2025-07-29 13:00:00 | 12.78 | 52.225 | 0 | 0 | 310.5652 | -39.445 | -39.445
2025-07-29 14:00:00 | 12.96 | 46.7724 | 0 | 0 | 310.5652 | -33.8124 | -33.8124
2025-07-29 15:00:00 | 12.48 | 39.0614 | 0 | 0 | 310.5652 | -26.5814 | -26.5814
2025-07-29 16:00:00 | 11.16 | 29.6173 | 0 | 0 | 310.5652 | -18.4573 | -18.4573
2025-07-29 17:00:00 | 10.68 | 19.0838 | 0 | 0 | 310.5652 | -8.4038 | -8.4038
2025-07-29 18:00:00 | 9.78 | 8.1787 | 0 | 1.6013 | 308.9639 | 1.3323e-15 | 1.6013
2025-07-29 19:00:00 | 9.48 | 0 | 0 | 0 | 308.9639 | 9.48 | 9.48
2025-07-29 20:00:00 | 4.14 | 0 | 0 | 0 | 308.9639 | 4.14 | 4.14
2025-07-29 21:00:00 | 3.54 | 0 | 0 | 0 | 308.9639 | 3.54 | 3.54
2025-07-29 22:00:00 | 3.18 | 0 | 0 | 0 | 308.9639 | 3.18 | 3.18
2025-07-29 23:00:00 | 3.3 | 0 | 0 | 0 | 308.9639 | 3.3 | 3.3
2025-07-30 00:00:00 | 3.3 | 0 | 0 | 0 | 308.9639 | 3.3 | 3.3
2025-07-30 01:00:00 | 3.48 | 0 | 0 | 0 | 308.9639 | 3.48 | 3.48
2025-07-30 02:00:00 | 3.36 | 0 | 0 | 0 | 308.9639 | 3.36 | 3.36
2025-07-30 03:00:00 | 3.06 | 0 | 0 | 0 | 308.9639 | 3.06 | 3.06
2025-07-30 04:00:00 | 3.18 | 0 | 0 | 0 | 308.9639 | 3.18 | 3.18
2025-07-30 05:00:00 | 3.24 | 7.9968 | 0 | 0 | 308.9639 | -4.7568 | -4.7568
2025-07-30 06:00:00 | 3.78 | 18.9177 | 0 | 0 | 308.9639 | -15.1377 | -15.1377
2025-07-30 07:00:00 | 4.02 | 29.4664 | 0 | 0 | 308.9639 | -25.4464 | -25.4464
2025-07-30 08:00:00 | 4.74 | 38.9242 | 0 | 0 | 308.9639 | -34.1842 | -34.1842
2025-07-30 09:00:00 | 5.94 | 46.6464 | 0 | 0 | 308.9639 | -40.7064 | -40.7064
2025-07-30 10:00:00 | 6.72 | 52.1068 | 0 | 0 | 308.9639 | -45.3868 | -45.3868
2025-07-30 11:00:00 | 7.2 | 54.9333 | 0 | 0 | 308.9639 | -47.7333 | -47.7333
2025-07-30 12:00:00 | 17.34 | 54.9333 | 0 | 0 | 308.9639 | -37.5933 | -37.5933
2025-07-30 13:00:00 | 21.3 | 52.1068 | 0 | 0 | 308.9639 | -30.8068 | -30.8068
2025-07-30 14:00:00 | 8.88 | 46.6464 | 0 | 0 | 308.9639 | -37.7664 | -37.7664
2025-07-30 15:00:00 | 6.24 | 38.9242 | 0 | 0 | 308.9639 | -32.6842 | -32.6842
2025-07-30 16:00:00 | 4.5 | 29.4664 | 0 | 0 | 308.9639 | -24.9664 | -24.9664
2025-07-30 17:00:00 | 3.48 | 18.9177 | 0 | 0 | 308.9639 | -15.4377 | -15.4377
2025-07-30 18:00:00 | 3.12 | 7.9968 | 0 | 0 | 308.9639 | -4.8768 | -4.8768
2025-07-30 19:00:00 | 11.34 | 0 | 0 | 0 | 308.9639 | 11.34 | 11.34
2025-07-30 20:00:00 | 3.24 | 0 | 0 | 0 | 308.9639 | 3.24 | 3.24
2025-07-30 21:00:00 | 3.18 | 0 | 0 | 0 | 308.9639 | 3.18 | 3.18
2025-07-30 22:00:00 | 2.94 | 0 | 0 | 0 | 308.9639 | 2.94 | 2.94
2025-07-30 23:00:00 | 2.94 | 0 | 0 | 0 | 308.9639 | 2.94 | 2.94
2025-07-31 00:00:00 | 3 | 0 | 0 | 0 | 308.9639 | 3 | 3
2025-07-31 01:00:00 | 3.06 | 0 | 0 | 0 | 308.9639 | 3.06 | 3.06
2025-07-31 02:00:00 | 2.94 | 0 | 0 | 0 | 308.9639 | 2.94 | 2.94
2025-07-31 03:00:00 | 2.94 | 0 | 0 | 0 | 308.9639 | 2.94 | 2.94
2025-07-31 04:00:00 | 3.12 | 0 | 0 | 0 | 308.9639 | 3.12 | 3.12
2025-07-31 05:00:00 | 5.58 | 7.8107 | 0 | 0 | 308.9639 | -2.2307 | -2.2307
2025-07-31 06:00:00 | 19.14 | 18.7475 | 0 | 0 | 308.9639 | 0.39251 | 0.39251
2025-07-31 07:00:00 | 19.98 | 29.3116 | 0 | 0 | 308.9639 | -9.3316 | -9.3316
2025-07-31 08:00:00 | 19.86 | 38.7832 | 0 | 0 | 308.9639 | -18.9232 | -18.9232
2025-07-31 09:00:00 | 20.04 | 46.5166 | 0 | 0 | 308.9639 | -26.4766 | -26.4766
2025-07-31 10:00:00 | 11.04 | 51.985 | 0 | 0 | 308.9639 | -40.945 | -40.945
2025-07-31 11:00:00 | 5.76 | 54.8157 | 0 | 0 | 308.9639 | -49.0557 | -49.0557
2025-07-31 12:00:00 | 4.98 | 54.8157 | 0 | 0 | 308.9639 | -49.8357 | -49.8357
2025-07-31 13:00:00 | 4.38 | 51.985 | 0 | 0 | 308.9639 | -47.605 | -47.605
2025-07-31 14:00:00 | 4.38 | 46.5166 | 0 | 0 | 308.9639 | -42.1366 | -42.1366
2025-07-31 15:00:00 | 3.42 | 38.7832 | 0 | 0 | 308.9639 | -35.3632 | -35.3632
2025-07-31 16:00:00 | 4.92 | 29.3116 | 0 | 0 | 308.9639 | -24.3916 | -24.3916
2025-07-31 17:00:00 | 9.9 | 18.7475 | 0 | 0 | 308.9639 | -8.8475 | -8.8475
2025-07-31 18:00:00 | 3.36 | 7.8107 | 0 | 0 | 308.9639 | -4.4507 | -4.4507
2025-07-31 19:00:00 | 3.54 | 0 | 0 | 0 | 308.9639 | 3.54 | 3.54
2025-07-31 20:00:00 | 3.3 | 0 | 0 | 0 | 308.9639 | 3.3 | 3.3
2025-07-31 21:00:00 | 3.54 | 0 | 14.16 | 0 | 321.4247 | 17.7 | 3.54
2025-07-31 22:00:00 | 3.42 | 0 | 4.0628 | 0 | 325 | 7.4828 | 3.42
2025-07-31 23:00:00 | 3.6 | 0 | 0 | 0 | 325 | 3.6 | 3.6
2025-08-01 00:00:00 | 3.42 | 0 | 0 | 0 | 325 | 3.42 | 3.42
2025-08-01 01:00:00 | 3.66 | 0 | 0 | 0 | 325 | 3.66 | 3.66
2025-08-01 02:00:00 | 3.78 | 0 | 0 | 0 | 325 | 3.78 | 3.78
2025-08-01 03:00:00 | 4.32 | 0 | 0 | 0 | 325 | 4.32 | 4.32
2025-08-01 04:00:00 | 3.66 | 0 | 0 | 0 | 325 | 3.66 | 3.66
2025-08-01 05:00:00 | 4.02 | 6.9171 | 0 | 0 | 325 | -2.8971 | -2.8971
2025-08-01 06:00:00 | 3.54 | 16.8589 | 0 | 0 | 325 | -13.3189 | -13.3189
2025-08-01 07:00:00 | 3.9 | 26.4619 | 0 | 0 | 325 | -22.5619 | -22.5619
2025-08-01 08:00:00 | 3.24 | 35.0718 | 0 | 0 | 325 | -31.8318 | -31.8318
2025-08-01 09:00:00 | 3.36 | 42.1017 | 0 | 0 | 325 | -38.7417 | -38.7417
2025-08-01 10:00:00 | 3.24 | 47.0726 | 0 | 0 | 325 | -43.8326 | -43.8326
2025-08-01 11:00:00 | 3.48 | 49.6457 | 0 | 0 | 325 | -46.1657 | -46.1657
2025-08-01 12:00:00 | 12.42 | 49.6457 | 0 | 0 | 325 | -37.2257 | -37.2257
2025-08-01 13:00:00 | 17.4 | 47.0726 | 0 | 0 | 325 | -29.6726 | -29.6726
2025-08-01 14:00:00 | 22.02 | 42.1017 | 0 | 0 | 325 | -20.0817 | -20.0817
2025-08-01 15:00:00 | 24 | 35.0718 | 0 | 0 | 325 | -11.0718 | -11.0718
2025-08-01 16:00:00 | 19.38 | 26.4619 | 0 | 0 | 325 | -7.0819 | -7.0819
2025-08-01 17:00:00 | 16.92 | 16.8589 | 0 | 0.061145 | 324.9389 | -4.1633e-17 | 0.061145
2025-08-01 18:00:00 | 16.86 | 6.9171 | 0 | 9.9429 | 314.9959 | 0 | 9.9429
2025-08-01 19:00:00 | 8.82 | 0 | 0 | 0 | 314.9959 | 8.82 | 8.82
2025-08-01 20:00:00 | 6.9 | 0 | 0 | 0 | 314.9959 | 6.9 | 6.9
2025-08-01 21:00:00 | 10.08 | 0 | 0 | 0 | 314.9959 | 10.08 | 10.08
2025-08-01 22:00:00 | 10.02 | 0 | 0 | 0 | 314.9959 | 10.02 | 10.02
2025-08-01 23:00:00 | 10.02 | 0 | 0 | 0 | 314.9959 | 10.02 | 10.02
2025-08-02 00:00:00 | 10.08 | 0 | 0 | 0 | 314.9959 | 10.08 | 10.08
2025-08-02 01:00:00 | 10.5 | 0 | 0 | 0 | 314.9959 | 10.5 | 10.5
2025-08-02 02:00:00 | 10.62 | 0 | 0 | 0 | 314.9959 | 10.62 | 10.62
2025-08-02 03:00:00 | 10.68 | 0 | 0 | 0 | 314.9959 | 10.68 | 10.68
2025-08-02 04:00:00 | 10.74 | 0 | 0 | 0 | 314.9959 | 10.74 | 10.74
2025-08-02 05:00:00 | 10.92 | 6.7407 | 0 | 0 | 314.9959 | 4.1793 | 4.1793
2025-08-02 06:00:00 | 10.62 | 16.6971 | 0 | 0 | 314.9959 | -6.0771 | -6.0771
2025-08-02 07:00:00 | 3.9 | 26.3143 | 0 | 0 | 314.9959 | -22.4143 | -22.4143
2025-08-02 08:00:00 | 3.24 | 34.9369 | 0 | 0 | 314.9959 | -31.6969 | -31.6969
2025-08-02 09:00:00 | 3.18 | 41.9772 | 0 | 0 | 314.9959 | -38.7972 | -38.7972
2025-08-02 10:00:00 | 3.66 | 46.9554 | 0 | 0 | 314.9959 | -43.2954 | -43.2954
2025-08-02 11:00:00 | 3.12 | 49.5323 | 0 | 0 | 314.9959 | -46.4123 | -46.4123
2025-08-02 12:00:00 | 3.06 | 49.5323 | 0 | 0 | 314.9959 | -46.4723 | -46.4723
2025-08-02 13:00:00 | 3.12 | 46.9554 | 0 | 0 | 314.9959 | -43.8354 | -43.8354
2025-08-02 14:00:00 | 3.24 | 41.9772 | 0 | 0 | 314.9959 | -38.7372 | -38.7372
2025-08-02 15:00:00 | 3.42 | 34.9369 | 0 | 0 | 314.9959 | -31.5169 | -31.5169
2025-08-02 16:00:00 | 3.24 | 26.3143 | 0 | 0 | 314.9959 | -23.0743 | -23.0743
2025-08-02 17:00:00 | 3.06 | 16.6971 | 0 | 0 | 314.9959 | -13.6371 | -13.6371
2025-08-02 18:00:00 | 3.18 | 6.7407 | 0 | 0 | 314.9959 | -3.5607 | -3.5607
2025-08-02 19:00:00 | 3.24 | 0 | 0 | 0 | 314.9959 | 3.24 | 3.24
2025-08-02 20:00:00 | 3.96 | 0 | 0 | 0 | 314.9959 | 3.96 | 3.96
2025-08-02 21:00:00 | 3.36 | 0 | 0 | 0 | 314.9959 | 3.36 | 3.36
2025-08-02 22:00:00 | 3.36 | 0 | 0 | 0 | 314.9959 | 3.36 | 3.36
2025-08-02 23:00:00 | 3.36 | 0 | 0 | 0 | 314.9959 | 3.36 | 3.36
2025-08-03 00:00:00 | 3.3 | 0 | 0 | 0 | 314.9959 | 3.3 | 3.3
2025-08-03 01:00:00 | 3.36 | 0 | 0 | 0 | 314.9959 | 3.36 | 3.36
2025-08-03 02:00:00 | 3.84 | 0 | 0 | 0 | 314.9959 | 3.84 | 3.84
2025-08-03 03:00:00 | 3.48 | 0 | 0 | 0 | 314.9959 | 3.48 | 3.48
2025-08-03 04:00:00 | 3.6 | 0 | 0 | 0 | 314.9959 | 3.6 | 3.6
2025-08-03 05:00:00 | 3.42 | 6.5607 | 0 | 0 | 314.9959 | -3.1407 | -3.1407
2025-08-03 06:00:00 | 3.42 | 16.5319 | 0 | 0 | 314.9959 | -13.1119 | -13.1119
2025-08-03 07:00:00 | 3.6 | 26.1633 | 0 | 0 | 314.9959 | -22.5633 | -22.5633
2025-08-03 08:00:00 | 3.18 | 34.7986 | 0 | 0 | 314.9959 | -31.6186 | -31.6186
2025-08-03 09:00:00 | 3.3 | 41.8493 | 0 | 0 | 314.9959 | -38.5493 | -38.5493
2025-08-03 10:00:00 | 3.18 | 46.8349 | 0 | 0 | 314.9959 | -43.6549 | -43.6549
2025-08-03 11:00:00 | 3.06 | 49.4156 | 0 | 0 | 314.9959 | -46.3556 | -46.3556
2025-08-03 12:00:00 | 5.04 | 49.4156 | 0 | 0 | 314.9959 | -44.3756 | -44.3756
2025-08-03 13:00:00 | 9.72 | 46.8349 | 0 | 0 | 314.9959 | -37.1149 | -37.1149
2025-08-03 14:00:00 | 6 | 41.8493 | 0 | 0 | 314.9959 | -35.8493 | -35.8493
2025-08-03 15:00:00 | 3.48 | 34.7986 | 0 | 0 | 314.9959 | -31.3186 | -31.3186
2025-08-03 16:00:00 | 3.36 | 26.1633 | 0 | 0 | 314.9959 | -22.8033 | -22.8033
2025-08-03 17:00:00 | 3.54 | 16.5319 | 0 | 0 | 314.9959 | -12.9919 | -12.9919
2025-08-03 18:00:00 | 3.36 | 6.5607 | 0 | 0 | 314.9959 | -3.2007 | -3.2007
2025-08-03 19:00:00 | 3.42 | 0 | 0 | 0 | 314.9959 | 3.42 | 3.42
2025-08-03 20:00:00 | 3.24 | 0 | 0 | 0 | 314.9959 | 3.24 | 3.24
2025-08-03 21:00:00 | 3.24 | 0 | 0 | 0 | 314.9959 | 3.24 | 3.24
2025-08-03 22:00:00 | 3.54 | 0 | 0 | 0 | 314.9959 | 3.54 | 3.54
2025-08-03 23:00:00 | 3.36 | 0 | 0 | 0 | 314.9959 | 3.36 | 3.36
2025-08-04 00:00:00 | 3.24 | 0 | 0 | 0 | 314.9959 | 3.24 | 3.24
2025-08-04 01:00:00 | 3.42 | 0 | 0 | 0 | 314.9959 | 3.42 | 3.42
2025-08-04 02:00:00 | 3.48 | 0 | 0 | 0 | 314.9959 | 3.48 | 3.48
2025-08-04 03:00:00 | 3.42 | 0 | 0 | 0 | 314.9959 | 3.42 | 3.42
2025-08-04 04:00:00 | 3.36 | 0 | 0 | 0 | 314.9959 | 3.36 | 3.36
2025-08-04 05:00:00 | 3.18 | 6.3771 | 0 | 0 | 314.9959 | -3.1971 | -3.1971
2025-08-04 06:00:00 | 3.24 | 16.363 | 0 | 0 | 314.9959 | -13.123 | -13.123
2025-08-04 07:00:00 | 3.42 | 26.0087 | 0 | 0 | 314.9959 | -22.5887 | -22.5887
2025-08-04 08:00:00 | 3.12 | 34.6569 | 0 | 0 | 314.9959 | -31.5369 | -31.5369
2025-08-04 09:00:00 | 3.18 | 41.718 | 0 | 0 | 314.9959 | -38.538 | -38.538
2025-08-04 10:00:00 | 3.12 | 46.711 | 0 | 0 | 314.9959 | -43.591 | -43.591
2025-08-04 11:00:00 | 3.12 | 49.2956 | 0 | 0 | 314.9959 | -46.1756 | -46.1756
2025-08-04 12:00:00 | 3.66 | 49.2956 | 0 | 0 | 314.9959 | -45.6356 | -45.6356
2025-08-04 13:00:00 | 3.3 | 46.711 | 0 | 0 | 314.9959 | -43.411 | -43.411
2025-08-04 14:00:00 | 3.48 | 41.718 | 0 | 0 | 314.9959 | -38.238 | -38.238
2025-08-04 15:00:00 | 3.54 | 34.6569 | 0 | 0 | 314.9959 | -31.1169 | -31.1169
2025-08-04 16:00:00 | 3.48 | 26.0087 | 0 | 0 | 314.9959 | -22.5287 | -22.5287
2025-08-04 17:00:00 | 3.36 | 16.363 | 0 | 0 | 314.9959 | -13.003 | -13.003
2025-08-04 18:00:00 | 3.72 | 6.3771 | 0 | 0 | 314.9959 | -2.6571 | -2.6571
2025-08-04 19:00:00 | 3.24 | 0 | 0 | 0 | 314.9959 | 3.24 | 3.24
2025-08-04 20:00:00 | 3.42 | 0 | 0 | 0 | 314.9959 | 3.42 | 3.42
2025-08-04 21:00:00 | 3.6 | 0 | 0 | 0 | 314.9959 | 3.6 | 3.6
2025-08-04 22:00:00 | 3.24 | 0 | 0 | 0 | 314.9959 | 3.24 | 3.24
2025-08-04 23:00:00 | 3.48 | 0 | 0 | 0 | 314.9959 | 3.48 | 3.48
2025-08-05 00:00:00 | 3.24 | 0 | 0 | 0 | 314.9959 | 3.24 | 3.24
2025-08-05 01:00:00 | 3.24 | 0 | 0 | 0 | 314.9959 | 3.24 | 3.24
2025-08-05 02:00:00 | 3.36 | 0 | 0 | 0 | 314.9959 | 3.36 | 3.36
2025-08-05 03:00:00 | 3.36 | 0 | 0 | 0 | 314.9959 | 3.36 | 3.36
2025-08-05 04:00:00 | 3.48 | 0 | 0 | 0 | 314.9959 | 3.48 | 3.48
2025-08-05 05:00:00 | 3.3 | 6.1899 | 0 | 0 | 314.9959 | -2.8899 | -2.8899
2025-08-05 06:00:00 | 4.44 | 16.1907 | 0 | 0 | 314.9959 | -11.7507 | -11.7507
2025-08-05 07:00:00 | 4.5 | 25.8507 | 0 | 0 | 314.9959 | -21.3507 | -21.3507
2025-08-05 08:00:00 | 4.2 | 34.5117 | 0 | 0 | 314.9959 | -30.3117 | -30.3117
2025-08-05 09:00:00 | 4.14 | 41.5833 | 0 | 0 | 314.9959 | -37.4433 | -37.4433
2025-08-05 10:00:00 | 4.2 | 46.5837 | 0 | 0 | 314.9959 | -42.3837 | -42.3837
2025-08-05 11:00:00 | 3.3 | 49.1721 | 0 | 0 | 314.9959 | -45.8721 | -45.8721
2025-08-05 12:00:00 | 3.6 | 49.1721 | 0 | 0 | 314.9959 | -45.5721 | -45.5721
2025-08-05 13:00:00 | 5.88 | 46.5837 | 0 | 0 | 314.9959 | -40.7037 | -40.7037
2025-08-05 14:00:00 | 17.52 | 41.5833 | 0 | 0 | 314.9959 | -24.0633 | -24.0633
2025-08-05 15:00:00 | 16.5 | 34.5117 | 0 | 0 | 314.9959 | -18.0117 | -18.0117
2025-08-05 16:00:00 | 3.66 | 25.8507 | 0 | 0 | 314.9959 | -22.1907 | -22.1907
2025-08-05 17:00:00 | 3.6 | 16.1907 | 0 | 0 | 314.9959 | -12.5907 | -12.5907
2025-08-05 18:00:00 | 3.66 | 6.1899 | 0 | 0 | 314.9959 | -2.5299 | -2.5299
2025-08-05 19:00:00 | 3.24 | 0 | 0 | 0 | 314.9959 | 3.24 | 3.24
2025-08-05 20:00:00 | 3.42 | 0 | 0 | 0 | 314.9959 | 3.42 | 3.42
2025-08-05 21:00:00 | 3.54 | 0 | 0 | 0 | 314.9959 | 3.54 | 3.54
2025-08-05 22:00:00 | 3.42 | 0 | 0 | 0 | 314.9959 | 3.42 | 3.42
2025-08-05 23:00:00 | 3.18 | 0 | 0 | 0 | 314.9959 | 3.18 | 3.18
2025-08-06 00:00:00 | 3.48 | 0 | 0 | 0 | 314.9959 | 3.48 | 3.48
2025-08-06 01:00:00 | 3.48 | 0 | 0 | 0 | 314.9959 | 3.48 | 3.48
2025-08-06 02:00:00 | 3.3 | 0 | 0 | 0 | 314.9959 | 3.3 | 3.3
2025-08-06 03:00:00 | 3.66 | 0 | 0 | 0 | 314.9959 | 3.66 | 3.66
2025-08-06 04:00:00 | 3.18 | 0 | 0 | 0 | 314.9959 | 3.18 | 3.18
2025-08-06 05:00:00 | 3.42 | 5.9992 | 0 | 0 | 314.9959 | -2.5792 | -2.5792
2025-08-06 06:00:00 | 3.18 | 16.0149 | 0 | 0 | 314.9959 | -12.8349 | -12.8349
2025-08-06 07:00:00 | 3.54 | 25.6892 | 0 | 0 | 314.9959 | -22.1492 | -22.1492
2025-08-06 08:00:00 | 3.42 | 34.3631 | 0 | 0 | 314.9959 | -30.9431 | -30.9431
2025-08-06 09:00:00 | 3.3 | 41.4452 | 0 | 0 | 314.9959 | -38.1452 | -38.1452
2025-08-06 10:00:00 | 3.36 | 46.453 | 0 | 0 | 314.9959 | -43.093 | -43.093
2025-08-06 11:00:00 | 4.8 | 49.0453 | 0 | 0 | 314.9959 | -44.2453 | -44.2453
2025-08-06 12:00:00 | 4.44 | 49.0453 | 0 | 0 | 314.9959 | -44.6053 | -44.6053
2025-08-06 13:00:00 | 10.8 | 46.453 | 0 | 0 | 314.9959 | -35.653 | -35.653
2025-08-06 14:00:00 | 17.94 | 41.4452 | 0 | 0 | 314.9959 | -23.5052 | -23.5052
2025-08-06 15:00:00 | 17.58 | 34.3631 | 0 | 0 | 314.9959 | -16.7831 | -16.7831
2025-08-06 16:00:00 | 17.22 | 25.6892 | 0 | 0 | 314.9959 | -8.4692 | -8.4692
2025-08-06 17:00:00 | 17.4 | 16.0149 | 0 | 1.3851 | 313.6108 | -9.1038e-15 | 1.3851
2025-08-06 18:00:00 | 17.16 | 5.9992 | 0 | 11.1608 | 302.45 | 3.1974e-14 | 11.1608
2025-08-06 19:00:00 | 4.14 | 0 | 0 | 0 | 302.45 | 4.14 | 4.14
2025-08-06 20:00:00 | 3.78 | 0 | 0 | 0 | 302.45 | 3.78 | 3.78
2025-08-06 21:00:00 | 3.54 | 0 | 0 | 0 | 302.45 | 3.54 | 3.54
2025-08-06 22:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-06 23:00:00 | 3.72 | 0 | 0 | 0 | 302.45 | 3.72 | 3.72
2025-08-07 00:00:00 | 3.48 | 0 | 0 | 0 | 302.45 | 3.48 | 3.48
2025-08-07 01:00:00 | 3.24 | 0 | 0 | 0 | 302.45 | 3.24 | 3.24
2025-08-07 02:00:00 | 3.66 | 0 | 0 | 0 | 302.45 | 3.66 | 3.66
2025-08-07 03:00:00 | 3.36 | 0 | 0 | 0 | 302.45 | 3.36 | 3.36
2025-08-07 04:00:00 | 3.42 | 0 | 0 | 0 | 302.45 | 3.42 | 3.42
2025-08-07 05:00:00 | 3.42 | 5.8051 | 0 | 0 | 302.45 | -2.3851 | -2.3851
2025-08-07 06:00:00 | 3.36 | 15.8356 | 0 | 0 | 302.45 | -12.4756 | -12.4756
2025-08-07 07:00:00 | 3.3 | 25.5243 | 0 | 0 | 302.45 | -22.2243 | -22.2243
2025-08-07 08:00:00 | 4.02 | 34.211 | 0 | 0 | 302.45 | -30.191 | -30.191
2025-08-07 09:00:00 | 4.08 | 41.3037 | 0 | 0 | 302.45 | -37.2237 | -37.2237
2025-08-07 10:00:00 | 3.9 | 46.3189 | 0 | 0 | 302.45 | -42.4189 | -42.4189
2025-08-07 11:00:00 | 3.78 | 48.915 | 0 | 0 | 302.45 | -45.135 | -45.135
2025-08-07 12:00:00 | 3.06 | 48.915 | 0 | 0 | 302.45 | -45.855 | -45.855
2025-08-07 13:00:00 | 3.48 | 46.3189 | 0 | 0 | 302.45 | -42.8389 | -42.8389
2025-08-07 14:00:00 | 3 | 41.3037 | 0 | 0 | 302.45 | -38.3037 | -38.3037
2025-08-07 15:00:00 | 3.3 | 34.211 | 0 | 0 | 302.45 | -30.911 | -30.911
2025-08-07 16:00:00 | 2.94 | 25.5243 | 0 | 0 | 302.45 | -22.5843 | -22.5843
2025-08-07 17:00:00 | 3 | 15.8356 | 0 | 0 | 302.45 | -12.8356 | -12.8356
2025-08-07 18:00:00 | 3.18 | 5.8051 | 0 | 0 | 302.45 | -2.6251 | -2.6251
2025-08-07 19:00:00 | 3 | 0 | 0 | 0 | 302.45 | 3 | 3
2025-08-07 20:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-07 21:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-07 22:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-07 23:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-08 00:00:00 | 3.06 | 0 | 0 | 0 | 302.45 | 3.06 | 3.06
2025-08-08 01:00:00 | 2.82 | 0 | 0 | 0 | 302.45 | 2.82 | 2.82
2025-08-08 02:00:00 | 3.12 | 0 | 0 | 0 | 302.45 | 3.12 | 3.12
2025-08-08 03:00:00 | 2.82 | 0 | 0 | 0 | 302.45 | 2.82 | 2.82
2025-08-08 04:00:00 | 3 | 0 | 0 | 0 | 302.45 | 3 | 3
2025-08-08 05:00:00 | 2.64 | 5.6076 | 0 | 0 | 302.45 | -2.9676 | -2.9676
2025-08-08 06:00:00 | 2.94 | 15.6529 | 0 | 0 | 302.45 | -12.7129 | -12.7129
2025-08-08 07:00:00 | 2.82 | 25.356 | 0 | 0 | 302.45 | -22.536 | -22.536
2025-08-08 08:00:00 | 3.42 | 34.0555 | 0 | 0 | 302.45 | -30.6355 | -30.6355
2025-08-08 09:00:00 | 4.2 | 41.1587 | 0 | 0 | 302.45 | -36.9587 | -36.9587
2025-08-08 10:00:00 | 4.5 | 46.1813 | 0 | 0 | 302.45 | -41.6813 | -41.6813
2025-08-08 11:00:00 | 4.14 | 48.7813 | 0 | 0 | 302.45 | -44.6413 | -44.6413
2025-08-08 12:00:00 | 4.62 | 48.7813 | 0 | 0 | 302.45 | -44.1613 | -44.1613
2025-08-08 13:00:00 | 4.68 | 46.1813 | 0 | 0 | 302.45 | -41.5013 | -41.5013
2025-08-08 14:00:00 | 4.44 | 41.1587 | 0 | 0 | 302.45 | -36.7187 | -36.7187
2025-08-08 15:00:00 | 3.96 | 34.0555 | 0 | 0 | 302.45 | -30.0955 | -30.0955
2025-08-08 16:00:00 | 3.72 | 25.356 | 0 | 0 | 302.45 | -21.636 | -21.636
2025-08-08 17:00:00 | 3.42 | 15.6529 | 0 | 0 | 302.45 | -12.2329 | -12.2329
2025-08-08 18:00:00 | 3.48 | 5.6076 | 0 | 0 | 302.45 | -2.1276 | -2.1276
2025-08-08 19:00:00 | 3.54 | 0 | 0 | 0 | 302.45 | 3.54 | 3.54
2025-08-08 20:00:00 | 3.6 | 0 | 0 | 0 | 302.45 | 3.6 | 3.6
2025-08-08 21:00:00 | 3.6 | 0 | 0 | 0 | 302.45 | 3.6 | 3.6
2025-08-08 22:00:00 | 3.54 | 0 | 0 | 0 | 302.45 | 3.54 | 3.54
2025-08-08 23:00:00 | 3.12 | 0 | 0 | 0 | 302.45 | 3.12 | 3.12
2025-08-09 00:00:00 | 3.6 | 0 | 0 | 0 | 302.45 | 3.6 | 3.6
2025-08-09 01:00:00 | 3.36 | 0 | 0 | 0 | 302.45 | 3.36 | 3.36
2025-08-09 02:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-09 03:00:00 | 3.42 | 0 | 0 | 0 | 302.45 | 3.42 | 3.42
2025-08-09 04:00:00 | 3.48 | 0 | 0 | 0 | 302.45 | 3.48 | 3.48
2025-08-09 05:00:00 | 3.12 | 5.4067 | 0 | 0 | 302.45 | -2.2867 | -2.2867
2025-08-09 06:00:00 | 3.24 | 15.4669 | 0 | 0 | 302.45 | -12.2269 | -12.2269
2025-08-09 07:00:00 | 3 | 25.1843 | 0 | 0 | 302.45 | -22.1843 | -22.1843
2025-08-09 08:00:00 | 3.18 | 33.8966 | 0 | 0 | 302.45 | -30.7166 | -30.7166
2025-08-09 09:00:00 | 3.6 | 41.0102 | 0 | 0 | 302.45 | -37.4102 | -37.4102
2025-08-09 10:00:00 | 3.6 | 46.0403 | 0 | 0 | 302.45 | -42.4403 | -42.4403
2025-08-09 11:00:00 | 4.68 | 48.6441 | 0 | 0 | 302.45 | -43.9641 | -43.9641
2025-08-09 12:00:00 | 17.76 | 48.6441 | 0 | 0 | 302.45 | -30.8841 | -30.8841
2025-08-09 13:00:00 | 17.82 | 46.0403 | 0 | 0 | 302.45 | -28.2203 | -28.2203
2025-08-09 14:00:00 | 17.82 | 41.0102 | 0 | 0 | 302.45 | -23.1902 | -23.1902
2025-08-09 15:00:00 | 5.58 | 33.8966 | 0 | 0 | 302.45 | -28.3166 | -28.3166
2025-08-09 16:00:00 | 3.78 | 25.1843 | 0 | 0 | 302.45 | -21.4043 | -21.4043
2025-08-09 17:00:00 | 3.6 | 15.4669 | 0 | 0 | 302.45 | -11.8669 | -11.8669
2025-08-09 18:00:00 | 4.08 | 5.4067 | 0 | 0 | 302.45 | -1.3267 | -1.3267
2025-08-09 19:00:00 | 3.6 | 0 | 0 | 0 | 302.45 | 3.6 | 3.6
2025-08-09 20:00:00 | 3.6 | 0 | 0 | 0 | 302.45 | 3.6 | 3.6
2025-08-09 21:00:00 | 3.36 | 0 | 0 | 0 | 302.45 | 3.36 | 3.36
2025-08-09 22:00:00 | 3.6 | 0 | 0 | 0 | 302.45 | 3.6 | 3.6
2025-08-09 23:00:00 | 3.6 | 0 | 0 | 0 | 302.45 | 3.6 | 3.6
2025-08-10 00:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-10 01:00:00 | 3.42 | 0 | 0 | 0 | 302.45 | 3.42 | 3.42
2025-08-10 02:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-10 03:00:00 | 3.36 | 0 | 0 | 0 | 302.45 | 3.36 | 3.36
2025-08-10 04:00:00 | 3.48 | 0 | 0 | 0 | 302.45 | 3.48 | 3.48
2025-08-10 05:00:00 | 3.18 | 5.2026 | 0 | 0 | 302.45 | -2.0226 | -2.0226
2025-08-10 06:00:00 | 3.3 | 15.2775 | 0 | 0 | 302.45 | -11.9775 | -11.9775
2025-08-10 07:00:00 | 3.18 | 25.0092 | 0 | 0 | 302.45 | -21.8292 | -21.8292
2025-08-10 08:00:00 | 3.24 | 33.7343 | 0 | 0 | 302.45 | -30.4943 | -30.4943
2025-08-10 09:00:00 | 3.6 | 40.8584 | 0 | 0 | 302.45 | -37.2584 | -37.2584
2025-08-10 10:00:00 | 3.48 | 45.8958 | 0 | 0 | 302.45 | -42.4158 | -42.4158
2025-08-10 11:00:00 | 3.6 | 48.5034 | 0 | 0 | 302.45 | -44.9034 | -44.9034
2025-08-10 12:00:00 | 3.66 | 48.5034 | 0 | 0 | 302.45 | -44.8434 | -44.8434
2025-08-10 13:00:00 | 3.84 | 45.8958 | 0 | 0 | 302.45 | -42.0558 | -42.0558
2025-08-10 14:00:00 | 4.26 | 40.8584 | 0 | 0 | 302.45 | -36.5984 | -36.5984
2025-08-10 15:00:00 | 3.96 | 33.7343 | 0 | 0 | 302.45 | -29.7743 | -29.7743
2025-08-10 16:00:00 | 3.84 | 25.0092 | 0 | 0 | 302.45 | -21.1692 | -21.1692
2025-08-10 17:00:00 | 3.84 | 15.2775 | 0 | 0 | 302.45 | -11.4375 | -11.4375
2025-08-10 18:00:00 | 3.84 | 5.2026 | 0 | 0 | 302.45 | -1.3626 | -1.3626
2025-08-10 19:00:00 | 3.78 | 0 | 0 | 0 | 302.45 | 3.78 | 3.78
2025-08-10 20:00:00 | 3.78 | 0 | 0 | 0 | 302.45 | 3.78 | 3.78
2025-08-10 21:00:00 | 3.36 | 0 | 0 | 0 | 302.45 | 3.36 | 3.36
2025-08-10 22:00:00 | 3.6 | 0 | 0 | 0 | 302.45 | 3.6 | 3.6
2025-08-10 23:00:00 | 3.36 | 0 | 0 | 0 | 302.45 | 3.36 | 3.36
2025-08-11 00:00:00 | 3.24 | 0 | 0 | 0 | 302.45 | 3.24 | 3.24
2025-08-11 01:00:00 | 3.78 | 0 | 0 | 0 | 302.45 | 3.78 | 3.78
2025-08-11 02:00:00 | 3.24 | 0 | 0 | 0 | 302.45 | 3.24 | 3.24
2025-08-11 03:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-11 04:00:00 | 3.24 | 0 | 0 | 0 | 302.45 | 3.24 | 3.24
2025-08-11 05:00:00 | 3.42 | 4.9953 | 0 | 0 | 302.45 | -1.5753 | -1.5753
2025-08-11 06:00:00 | 3.78 | 15.0849 | 0 | 0 | 302.45 | -11.3049 | -11.3049
2025-08-11 07:00:00 | 4.32 | 24.8307 | 0 | 0 | 302.45 | -20.5107 | -20.5107
2025-08-11 08:00:00 | 4.5 | 33.5686 | 0 | 0 | 302.45 | -29.0686 | -29.0686
2025-08-11 09:00:00 | 4.44 | 40.703 | 0 | 0 | 302.45 | -36.263 | -36.263
2025-08-11 10:00:00 | 4.5 | 45.7479 | 0 | 0 | 302.45 | -41.2479 | -41.2479
2025-08-11 11:00:00 | 4.68 | 48.3592 | 0 | 0 | 302.45 | -43.6792 | -43.6792
2025-08-11 12:00:00 | 4.86 | 48.3592 | 0 | 0 | 302.45 | -43.4992 | -43.4992
2025-08-11 13:00:00 | 5.16 | 45.7479 | 0 | 0 | 302.45 | -40.5879 | -40.5879
2025-08-11 14:00:00 | 5.28 | 40.703 | 0 | 0 | 302.45 | -35.423 | -35.423
2025-08-11 15:00:00 | 4.74 | 33.5686 | 0 | 0 | 302.45 | -28.8286 | -28.8286
2025-08-11 16:00:00 | 3.78 | 24.8307 | 0 | 0 | 302.45 | -21.0507 | -21.0507
2025-08-11 17:00:00 | 4.26 | 15.0849 | 0 | 0 | 302.45 | -10.8249 | -10.8249
2025-08-11 18:00:00 | 3.54 | 4.9953 | 0 | 0 | 302.45 | -1.4553 | -1.4553
2025-08-11 19:00:00 | 4.8 | 0 | 0 | 0 | 302.45 | 4.8 | 4.8
2025-08-11 20:00:00 | 10.2 | 0 | 0 | 0 | 302.45 | 10.2 | 10.2
2025-08-11 21:00:00 | 10.44 | 0 | 0 | 0 | 302.45 | 10.44 | 10.44
2025-08-11 22:00:00 | 9.84 | 0 | 0 | 0 | 302.45 | 9.84 | 9.84
2025-08-11 23:00:00 | 10.2 | 0 | 0 | 0 | 302.45 | 10.2 | 10.2
2025-08-12 00:00:00 | 10.08 | 0 | 0 | 0 | 302.45 | 10.08 | 10.08
2025-08-12 01:00:00 | 10.26 | 0 | 0 | 0 | 302.45 | 10.26 | 10.26
2025-08-12 02:00:00 | 10.02 | 0 | 0 | 0 | 302.45 | 10.02 | 10.02
2025-08-12 03:00:00 | 10.14 | 0 | 0 | 0 | 302.45 | 10.14 | 10.14
2025-08-12 04:00:00 | 9.96 | 0 | 0 | 0 | 302.45 | 9.96 | 9.96
2025-08-12 05:00:00 | 9.96 | 4.7848 | 0 | 0 | 302.45 | 5.1752 | 5.1752
2025-08-12 06:00:00 | 9.84 | 14.889 | 0 | 0 | 302.45 | -5.049 | -5.049
2025-08-12 07:00:00 | 9.96 | 24.649 | 0 | 0 | 302.45 | -14.689 | -14.689
2025-08-12 08:00:00 | 5.88 | 33.3995 | 0 | 0 | 302.45 | -27.5195 | -27.5195
2025-08-12 09:00:00 | 4.68 | 40.5443 | 0 | 0 | 302.45 | -35.8643 | -35.8643
2025-08-12 10:00:00 | 3.72 | 45.5964 | 0 | 0 | 302.45 | -41.8764 | -41.8764
2025-08-12 11:00:00 | 4.38 | 48.2116 | 0 | 0 | 302.45 | -43.8316 | -43.8316
2025-08-12 12:00:00 | 4.26 | 48.2116 | 0 | 0 | 302.45 | -43.9516 | -43.9516
2025-08-12 13:00:00 | 4.38 | 45.5964 | 0 | 0 | 302.45 | -41.2164 | -41.2164
2025-08-12 14:00:00 | 4.5 | 40.5443 | 0 | 0 | 302.45 | -36.0443 | -36.0443
2025-08-12 15:00:00 | 4.2 | 33.3995 | 0 | 0 | 302.45 | -29.1995 | -29.1995
2025-08-12 16:00:00 | 3.3 | 24.649 | 0 | 0 | 302.45 | -21.349 | -21.349
2025-08-12 17:00:00 | 2.94 | 14.889 | 0 | 0 | 302.45 | -11.949 | -11.949
2025-08-12 18:00:00 | 3.18 | 4.7848 | 0 | 0 | 302.45 | -1.6048 | -1.6048
2025-08-12 19:00:00 | 3.18 | 0 | 0 | 0 | 302.45 | 3.18 | 3.18
2025-08-12 20:00:00 | 3.12 | 0 | 0 | 0 | 302.45 | 3.12 | 3.12
2025-08-12 21:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-12 22:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-12 23:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-13 00:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-13 01:00:00 | 2.7 | 0 | 0 | 0 | 302.45 | 2.7 | 2.7
2025-08-13 02:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-13 03:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-13 04:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-13 05:00:00 | 2.88 | 4.5712 | 0 | 0 | 302.45 | -1.6912 | -1.6912
2025-08-13 06:00:00 | 3.9 | 14.6899 | 0 | 0 | 302.45 | -10.7899 | -10.7899
2025-08-13 07:00:00 | 3.78 | 24.4639 | 0 | 0 | 302.45 | -20.6839 | -20.6839
2025-08-13 08:00:00 | 3.84 | 33.227 | 0 | 0 | 302.45 | -29.387 | -29.387
2025-08-13 09:00:00 | 4.14 | 40.382 | 0 | 0 | 302.45 | -36.242 | -36.242
2025-08-13 10:00:00 | 3.9 | 45.4414 | 0 | 0 | 302.45 | -41.5414 | -41.5414
2025-08-13 11:00:00 | 3.9 | 48.0604 | 0 | 0 | 302.45 | -44.1604 | -44.1604
2025-08-13 12:00:00 | 3.96 | 48.0604 | 0 | 0 | 302.45 | -44.1004 | -44.1004
2025-08-13 13:00:00 | 4.38 | 45.4414 | 0 | 0 | 302.45 | -41.0614 | -41.0614
2025-08-13 14:00:00 | 3.9 | 40.382 | 0 | 0 | 302.45 | -36.482 | -36.482
2025-08-13 15:00:00 | 4.26 | 33.227 | 0 | 0 | 302.45 | -28.967 | -28.967
2025-08-13 16:00:00 | 3.48 | 24.4639 | 0 | 0 | 302.45 | -20.9839 | -20.9839
2025-08-13 17:00:00 | 3.18 | 14.6899 | 0 | 0 | 302.45 | -11.5099 | -11.5099
2025-08-13 18:00:00 | 3.18 | 4.5712 | 0 | 0 | 302.45 | -1.3912 | -1.3912
2025-08-13 19:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-13 20:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-13 21:00:00 | 3.18 | 0 | 0 | 0 | 302.45 | 3.18 | 3.18
2025-08-13 22:00:00 | 2.82 | 0 | 0 | 0 | 302.45 | 2.82 | 2.82
2025-08-13 23:00:00 | 3.3 | 0 | 0 | 0 | 302.45 | 3.3 | 3.3
2025-08-14 00:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-14 01:00:00 | 2.82 | 0 | 0 | 0 | 302.45 | 2.82 | 2.82
2025-08-14 02:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-14 03:00:00 | 3.12 | 0 | 0 | 0 | 302.45 | 3.12 | 3.12
2025-08-14 04:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-14 05:00:00 | 2.76 | 4.3546 | 0 | 0 | 302.45 | -1.5946 | -1.5946
2025-08-14 06:00:00 | 3.84 | 14.4877 | 0 | 0 | 302.45 | -10.6477 | -10.6477
2025-08-14 07:00:00 | 4.02 | 24.2756 | 0 | 0 | 302.45 | -20.2556 | -20.2556
2025-08-14 08:00:00 | 4.02 | 33.0512 | 0 | 0 | 302.45 | -29.0312 | -29.0312
2025-08-14 09:00:00 | 3.66 | 40.2164 | 0 | 0 | 302.45 | -36.5564 | -36.5564
2025-08-14 10:00:00 | 3.48 | 45.283 | 0 | 0 | 302.45 | -41.803 | -41.803
2025-08-14 11:00:00 | 4.08 | 47.9056 | 0 | 0 | 302.45 | -43.8256 | -43.8256
2025-08-14 12:00:00 | 3.9 | 47.9056 | 0 | 0 | 302.45 | -44.0056 | -44.0056
2025-08-14 13:00:00 | 3.84 | 45.283 | 0 | 0 | 302.45 | -41.443 | -41.443
2025-08-14 14:00:00 | 3.96 | 40.2164 | 0 | 0 | 302.45 | -36.2564 | -36.2564
2025-08-14 15:00:00 | 3.24 | 33.0512 | 0 | 0 | 302.45 | -29.8112 | -29.8112
2025-08-14 16:00:00 | 3 | 24.2756 | 0 | 0 | 302.45 | -21.2756 | -21.2756
2025-08-14 17:00:00 | 3.12 | 14.4877 | 0 | 0 | 302.45 | -11.3677 | -11.3677
2025-08-14 18:00:00 | 2.88 | 4.3546 | 0 | 0 | 302.45 | -1.4746 | -1.4746
2025-08-14 19:00:00 | 3.18 | 0 | 0 | 0 | 302.45 | 3.18 | 3.18
2025-08-14 20:00:00 | 3.18 | 0 | 0 | 0 | 302.45 | 3.18 | 3.18
2025-08-14 21:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-14 22:00:00 | 3.06 | 0 | 0 | 0 | 302.45 | 3.06 | 3.06
2025-08-14 23:00:00 | 2.82 | 0 | 0 | 0 | 302.45 | 2.82 | 2.82
2025-08-15 00:00:00 | 3.18 | 0 | 0 | 0 | 302.45 | 3.18 | 3.18
2025-08-15 01:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-15 02:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-15 03:00:00 | 3 | 0 | 0 | 0 | 302.45 | 3 | 3
2025-08-15 04:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-15 05:00:00 | 3.06 | 4.135 | 0 | 0 | 302.45 | -1.075 | -1.075
2025-08-15 06:00:00 | 3.78 | 14.2824 | 0 | 0 | 302.45 | -10.5024 | -10.5024
2025-08-15 07:00:00 | 3.84 | 24.084 | 0 | 0 | 302.45 | -20.244 | -20.244
2025-08-15 08:00:00 | 3.78 | 32.872 | 0 | 0 | 302.45 | -29.092 | -29.092
2025-08-15 09:00:00 | 4.44 | 40.0473 | 0 | 0 | 302.45 | -35.6073 | -35.6073
2025-08-15 10:00:00 | 3.12 | 45.121 | 0 | 0 | 302.45 | -42.001 | -42.001
2025-08-15 11:00:00 | 4.14 | 47.7473 | 0 | 0 | 302.45 | -43.6073 | -43.6073
2025-08-15 12:00:00 | 4.02 | 47.7473 | 0 | 0 | 302.45 | -43.7273 | -43.7273
2025-08-15 13:00:00 | 4.2 | 45.121 | 0 | 0 | 302.45 | -40.921 | -40.921
2025-08-15 14:00:00 | 4.08 | 40.0473 | 0 | 0 | 302.45 | -35.9673 | -35.9673
2025-08-15 15:00:00 | 3.3 | 32.872 | 0 | 0 | 302.45 | -29.572 | -29.572
2025-08-15 16:00:00 | 3.24 | 24.084 | 0 | 0 | 302.45 | -20.844 | -20.844
2025-08-15 17:00:00 | 3.06 | 14.2824 | 0 | 0 | 302.45 | -11.2224 | -11.2224
2025-08-15 18:00:00 | 3.24 | 4.135 | 0 | 0 | 302.45 | -0.89496 | -0.89496
2025-08-15 19:00:00 | 3.12 | 0 | 0 | 0 | 302.45 | 3.12 | 3.12
2025-08-15 20:00:00 | 3.06 | 0 | 0 | 0 | 302.45 | 3.06 | 3.06
2025-08-15 21:00:00 | 3.24 | 0 | 0 | 0 | 302.45 | 3.24 | 3.24
2025-08-15 22:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-15 23:00:00 | 3 | 0 | 0 | 0 | 302.45 | 3 | 3
2025-08-16 00:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-16 01:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-16 02:00:00 | 3.12 | 0 | 0 | 0 | 302.45 | 3.12 | 3.12
2025-08-16 03:00:00 | 3 | 0 | 0 | 0 | 302.45 | 3 | 3
2025-08-16 04:00:00 | 2.76 | 0 | 0 | 0 | 302.45 | 2.76 | 2.76
2025-08-16 05:00:00 | 2.82 | 3.9125 | 0 | 0 | 302.45 | -1.0925 | -1.0925
2025-08-16 06:00:00 | 2.82 | 14.074 | 0 | 0 | 302.45 | -11.254 | -11.254
2025-08-16 07:00:00 | 3 | 23.8893 | 0 | 0 | 302.45 | -20.8893 | -20.8893
2025-08-16 08:00:00 | 2.58 | 32.6894 | 0 | 0 | 302.45 | -30.1094 | -30.1094
2025-08-16 09:00:00 | 2.82 | 39.8747 | 0 | 0 | 302.45 | -37.0547 | -37.0547
2025-08-16 10:00:00 | 2.88 | 44.9555 | 0 | 0 | 302.45 | -42.0755 | -42.0755
2025-08-16 11:00:00 | 2.64 | 47.5855 | 0 | 0 | 302.45 | -44.9455 | -44.9455
2025-08-16 12:00:00 | 3 | 47.5855 | 0 | 0 | 302.45 | -44.5855 | -44.5855
2025-08-16 13:00:00 | 2.82 | 44.9555 | 0 | 0 | 302.45 | -42.1355 | -42.1355
2025-08-16 14:00:00 | 2.94 | 39.8747 | 0 | 0 | 302.45 | -36.9347 | -36.9347
2025-08-16 15:00:00 | 3.18 | 32.6894 | 0 | 0 | 302.45 | -29.5094 | -29.5094
2025-08-16 16:00:00 | 2.88 | 23.8893 | 0 | 0 | 302.45 | -21.0093 | -21.0093
2025-08-16 17:00:00 | 3 | 14.074 | 0 | 0 | 302.45 | -11.074 | -11.074
2025-08-16 18:00:00 | 3.12 | 3.9125 | 0 | 0 | 302.45 | -0.79247 | -0.79247
2025-08-16 19:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-16 20:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-16 21:00:00 | 2.7 | 0 | 0 | 0 | 302.45 | 2.7 | 2.7
2025-08-16 22:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-16 23:00:00 | 2.76 | 0 | 0 | 0 | 302.45 | 2.76 | 2.76
2025-08-17 00:00:00 | 2.58 | 0 | 0 | 0 | 302.45 | 2.58 | 2.58
2025-08-17 01:00:00 | 2.64 | 0 | 0 | 0 | 302.45 | 2.64 | 2.64
2025-08-17 02:00:00 | 2.58 | 0 | 0 | 0 | 302.45 | 2.58 | 2.58
2025-08-17 03:00:00 | 2.58 | 0 | 0 | 0 | 302.45 | 2.58 | 2.58
2025-08-17 04:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-17 05:00:00 | 2.58 | 3.6871 | 0 | 0 | 302.45 | -1.1071 | -1.1071
2025-08-17 06:00:00 | 2.34 | 13.8626 | 0 | 0 | 302.45 | -11.5226 | -11.5226
2025-08-17 07:00:00 | 2.58 | 23.6914 | 0 | 0 | 302.45 | -21.1114 | -21.1114
2025-08-17 08:00:00 | 2.34 | 32.5036 | 0 | 0 | 302.45 | -30.1636 | -30.1636
2025-08-17 09:00:00 | 3 | 39.6987 | 0 | 0 | 302.45 | -36.6987 | -36.6987
2025-08-17 10:00:00 | 2.46 | 44.7865 | 0 | 0 | 302.45 | -42.3265 | -42.3265
2025-08-17 11:00:00 | 2.76 | 47.4201 | 0 | 0 | 302.45 | -44.6601 | -44.6601
2025-08-17 12:00:00 | 2.52 | 47.4201 | 0 | 0 | 302.45 | -44.9001 | -44.9001
2025-08-17 13:00:00 | 2.76 | 44.7865 | 0 | 0 | 302.45 | -42.0265 | -42.0265
2025-08-17 14:00:00 | 2.82 | 39.6987 | 0 | 0 | 302.45 | -36.8787 | -36.8787
2025-08-17 15:00:00 | 2.82 | 32.5036 | 0 | 0 | 302.45 | -29.6836 | -29.6836
2025-08-17 16:00:00 | 2.46 | 23.6914 | 0 | 0 | 302.45 | -21.2314 | -21.2314
2025-08-17 17:00:00 | 2.58 | 13.8626 | 0 | 0 | 302.45 | -11.2826 | -11.2826
2025-08-17 18:00:00 | 2.4 | 3.6871 | 0 | 0 | 302.45 | -1.2871 | -1.2871
2025-08-17 19:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-17 20:00:00 | 2.58 | 0 | 0 | 0 | 302.45 | 2.58 | 2.58
2025-08-17 21:00:00 | 2.46 | 0 | 0 | 0 | 302.45 | 2.46 | 2.46
2025-08-17 22:00:00 | 2.64 | 0 | 0 | 0 | 302.45 | 2.64 | 2.64
2025-08-17 23:00:00 | 2.58 | 0 | 0 | 0 | 302.45 | 2.58 | 2.58
2025-08-18 00:00:00 | 2.82 | 0 | 0 | 0 | 302.45 | 2.82 | 2.82
2025-08-18 01:00:00 | 2.58 | 0 | 0 | 0 | 302.45 | 2.58 | 2.58
2025-08-18 02:00:00 | 2.64 | 0 | 0 | 0 | 302.45 | 2.64 | 2.64
2025-08-18 03:00:00 | 2.82 | 0 | 0 | 0 | 302.45 | 2.82 | 2.82
2025-08-18 04:00:00 | 3.48 | 0 | 0 | 0 | 302.45 | 3.48 | 3.48
2025-08-18 05:00:00 | 4.14 | 3.4591 | 0 | 0 | 302.45 | 0.68093 | 0.68093
2025-08-18 06:00:00 | 5.1 | 13.6483 | 0 | 0 | 302.45 | -8.5483 | -8.5483
2025-08-18 07:00:00 | 5.16 | 23.4903 | 0 | 0 | 302.45 | -18.3303 | -18.3303
2025-08-18 08:00:00 | 5.22 | 32.3144 | 0 | 0 | 302.45 | -27.0944 | -27.0944
2025-08-18 09:00:00 | 5.04 | 39.5193 | 0 | 0 | 302.45 | -34.4793 | -34.4793
2025-08-18 10:00:00 | 4.98 | 44.6139 | 0 | 0 | 302.45 | -39.6339 | -39.6339
2025-08-18 11:00:00 | 4.62 | 47.2511 | 0 | 0 | 302.45 | -42.6311 | -42.6311
2025-08-18 12:00:00 | 5.22 | 47.2511 | 0 | 0 | 302.45 | -42.0311 | -42.0311
2025-08-18 13:00:00 | 4.62 | 44.6139 | 0 | 0 | 302.45 | -39.9939 | -39.9939
2025-08-18 14:00:00 | 2.64 | 39.5193 | 0 | 0 | 302.45 | -36.8793 | -36.8793
2025-08-18 15:00:00 | 2.58 | 32.3144 | 0 | 0 | 302.45 | -29.7344 | -29.7344
2025-08-18 16:00:00 | 2.76 | 23.4903 | 0 | 0 | 302.45 | -20.7303 | -20.7303
2025-08-18 17:00:00 | 2.52 | 13.6483 | 0 | 0 | 302.45 | -11.1283 | -11.1283
2025-08-18 18:00:00 | 2.52 | 3.4591 | 0 | 0 | 302.45 | -0.93907 | -0.93907
2025-08-18 19:00:00 | 2.52 | 0 | 0 | 0 | 302.45 | 2.52 | 2.52
2025-08-18 20:00:00 | 3 | 0 | 0 | 0 | 302.45 | 3 | 3
2025-08-18 21:00:00 | 2.7 | 0 | 0 | 0 | 302.45 | 2.7 | 2.7
2025-08-18 22:00:00 | 2.82 | 0 | 0 | 0 | 302.45 | 2.82 | 2.82
2025-08-18 23:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-19 00:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-19 01:00:00 | 3.18 | 0 | 0 | 0 | 302.45 | 3.18 | 3.18
2025-08-19 02:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-19 03:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-19 04:00:00 | 3.06 | 0 | 0 | 0 | 302.45 | 3.06 | 3.06
2025-08-19 05:00:00 | 7.68 | 3.2283 | 0 | 0 | 302.45 | 4.4517 | 4.4517
2025-08-19 06:00:00 | 9.54 | 13.4311 | 0 | 0 | 302.45 | -3.8911 | -3.8911
2025-08-19 07:00:00 | 12.36 | 23.2862 | 0 | 0 | 302.45 | -10.9262 | -10.9262
2025-08-19 08:00:00 | 12.18 | 32.1221 | 0 | 0 | 302.45 | -19.9421 | -19.9421
2025-08-19 09:00:00 | 11.94 | 39.3365 | 0 | 0 | 302.45 | -27.3965 | -27.3965
2025-08-19 10:00:00 | 12.12 | 44.4379 | 0 | 0 | 302.45 | -32.3179 | -32.3179
2025-08-19 11:00:00 | 11.52 | 47.0786 | 0 | 0 | 302.45 | -35.5586 | -35.5586
2025-08-19 12:00:00 | 11.7 | 47.0786 | 0 | 0 | 302.45 | -35.3786 | -35.3786
2025-08-19 13:00:00 | 6.9 | 44.4379 | 0 | 0 | 302.45 | -37.5379 | -37.5379
2025-08-19 14:00:00 | 5.22 | 39.3365 | 0 | 0 | 302.45 | -34.1165 | -34.1165
2025-08-19 15:00:00 | 4.8 | 32.1221 | 0 | 0 | 302.45 | -27.3221 | -27.3221
2025-08-19 16:00:00 | 2.88 | 23.2862 | 0 | 0 | 302.45 | -20.4062 | -20.4062
2025-08-19 17:00:00 | 2.58 | 13.4311 | 0 | 0 | 302.45 | -10.8511 | -10.8511
2025-08-19 18:00:00 | 2.7 | 3.2283 | 0 | 0 | 302.45 | -0.52829 | -0.52829
2025-08-19 19:00:00 | 3.24 | 0 | 0 | 0 | 302.45 | 3.24 | 3.24
2025-08-19 20:00:00 | 2.76 | 0 | 0 | 0 | 302.45 | 2.76 | 2.76
2025-08-19 21:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-19 22:00:00 | 3.18 | 0 | 0 | 0 | 302.45 | 3.18 | 3.18
2025-08-19 23:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-20 00:00:00 | 2.88 | 0 | 0 | 0 | 302.45 | 2.88 | 2.88
2025-08-20 01:00:00 | 3 | 0 | 0 | 0 | 302.45 | 3 | 3
2025-08-20 02:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-20 03:00:00 | 2.64 | 0 | 0 | 0 | 302.45 | 2.64 | 2.64
2025-08-20 04:00:00 | 2.94 | 0 | 0 | 0 | 302.45 | 2.94 | 2.94
2025-08-20 05:00:00 | 2.7 | 2.9949 | 0 | 0 | 302.45 | -0.29491 | -0.29491
2025-08-20 06:00:00 | 3 | 13.211 | 0 | 0 | 302.45 | -10.211 | -10.211
2025-08-20 07:00:00 | 3.48 | 23.079 | 0 | 0 | 302.45 | -19.599 | -19.599
2025-08-20 08:00:00 | 4.38 | 31.9264 | 0 | 0 | 302.45 | -27.5464 | -27.5464
2025-08-20 09:00:00 | 3.96 | 39.1503 | 0 | 0 | 302.45 | -35.1903 | -35.1903
2025-08-20 10:00:00 | 3.6 | 44.2584 | 0 | 0 | 302.45 | -40.6584 | -40.6584
2025-08-20 11:00:00 | 3.42 | 46.9025 | 0 | 0 | 302.45 | -43.4825 | -43.4825
2025-08-20 12:00:00 | 4.08 | 46.9025 | 0 | 0 | 302.45 | -42.8225 | -42.8225
2025-08-20 13:00:00 | 3.3 | 44.2584 | 0 | 0 | 302.45 | -40.9584 | -40.9584
2025-08-20 14:00:00 | 3.66 | 39.1503 | 0 | 0 | 302.45 | -35.4903 | -35.4903
2025-08-20 15:00:00 | 3.54 | 31.9264 | 0 | 0 | 302.45 | -28.3864 | -28.3864
2025-08-20 16:00:00 | 3.18 | 23.079 | 0 | 0 | 302.45 | -19.899 | -19.899
2025-08-20 17:00:00 | 9 | 13.211 | 0 | 0 | 302.45 | -4.211 | -4.211
2025-08-20 18:00:00 | 8.82 | 2.9949 | 0 | 5.8251 | 296.6249 | 7.9048e-14 | 5.8251
2025-08-20 19:00:00 | 9.18 | 0 | 0 | 0 | 296.6249 | 9.18 | 9.18
2025-08-20 20:00:00 | 9.72 | 0 | 0 | 0 | 296.6249 | 9.72 | 9.72
2025-08-20 21:00:00 | 9.3 | 0 | 0 | 0 | 296.6249 | 9.3 | 9.3
2025-08-20 22:00:00 | 9.48 | 0 | 0 | 0 | 296.6249 | 9.48 | 9.48
2025-08-20 23:00:00 | 8.34 | 0 | 0 | 0 | 296.6249 | 8.34 | 8.34
2025-08-21 00:00:00 | 3.24 | 0 | 0 | 0 | 296.6249 | 3.24 | 3.24
2025-08-21 01:00:00 | 3.12 | 0 | 0 | 0 | 296.6249 | 3.12 | 3.12
2025-08-21 02:00:00 | 3.18 | 0 | 0 | 0 | 296.6249 | 3.18 | 3.18
2025-08-21 03:00:00 | 3.48 | 0 | 0 | 0 | 296.6249 | 3.48 | 3.48
2025-08-21 04:00:00 | 3.48 | 0 | 0 | 0 | 296.6249 | 3.48 | 3.48
2025-08-21 05:00:00 | 3.36 | 2.759 | 0 | 0 | 296.6249 | 0.60103 | 0.60103
2025-08-21 06:00:00 | 3.12 | 12.9882 | 0 | 0 | 296.6249 | -9.8682 | -9.8682
2025-08-21 07:00:00 | 4.44 | 22.8688 | 0 | 0 | 296.6249 | -18.4288 | -18.4288
2025-08-21 08:00:00 | 3.9 | 31.7276 | 0 | 0 | 296.6249 | -27.8276 | -27.8276
2025-08-21 09:00:00 | 3.72 | 38.9607 | 0 | 0 | 296.6249 | -35.2407 | -35.2407
2025-08-21 10:00:00 | 3.9 | 44.0753 | 0 | 0 | 296.6249 | -40.1753 | -40.1753
2025-08-21 11:00:00 | 3.72 | 46.7228 | 0 | 0 | 296.6249 | -43.0028 | -43.0028
2025-08-21 12:00:00 | 3.36 | 46.7228 | 0 | 0 | 296.6249 | -43.3628 | -43.3628
2025-08-21 13:00:00 | 3.3 | 44.0753 | 0 | 0 | 296.6249 | -40.7753 | -40.7753
2025-08-21 14:00:00 | 3.12 | 38.9607 | 0 | 0 | 296.6249 | -35.8407 | -35.8407
2025-08-21 15:00:00 | 2.52 | 31.7276 | 0 | 0 | 296.6249 | -29.2076 | -29.2076
2025-08-21 16:00:00 | 2.52 | 22.8688 | 0 | 0 | 296.6249 | -20.3488 | -20.3488
2025-08-21 17:00:00 | 2.52 | 12.9882 | 0 | 0 | 296.6249 | -10.4682 | -10.4682
2025-08-21 18:00:00 | 2.7 | 2.759 | 0 | 0 | 296.6249 | -0.058974 | -0.058974
2025-08-21 19:00:00 | 2.52 | 0 | 0 | 0 | 296.6249 | 2.52 | 2.52
2025-08-21 20:00:00 | 2.64 | 0 | 0 | 0 | 296.6249 | 2.64 | 2.64
2025-08-21 21:00:00 | 2.82 | 0 | 0 | 0 | 296.6249 | 2.82 | 2.82
2025-08-21 22:00:00 | 2.52 | 0 | 0 | 0 | 296.6249 | 2.52 | 2.52
2025-08-21 23:00:00 | 2.58 | 0 | 0 | 0 | 296.6249 | 2.58 | 2.58
2025-08-22 00:00:00 | 2.94 | 0 | 0 | 0 | 296.6249 | 2.94 | 2.94
2025-08-22 01:00:00 | 3.36 | 0 | 0 | 0 | 296.6249 | 3.36 | 3.36
2025-08-22 02:00:00 | 3.12 | 0 | 0 | 0 | 296.6249 | 3.12 | 3.12
2025-08-22 03:00:00 | 3.42 | 0 | 0 | 0 | 296.6249 | 3.42 | 3.42
2025-08-22 04:00:00 | 3.36 | 0 | 0 | 0 | 296.6249 | 3.36 | 3.36
2025-08-22 05:00:00 | 3.3 | 2.5206 | 0 | 0 | 296.6249 | 0.77943 | 0.77943
2025-08-22 06:00:00 | 4.38 | 12.7626 | 0 | 0 | 296.6249 | -8.3826 | -8.3826
2025-08-22 07:00:00 | 4.98 | 22.6557 | 0 | 0 | 296.6249 | -17.6757 | -17.6757
2025-08-22 08:00:00 | 6.24 | 31.5256 | 0 | 0 | 296.6249 | -25.2856 | -25.2856
2025-08-22 09:00:00 | 3.72 | 38.7678 | 0 | 0 | 296.6249 | -35.0478 | -35.0478
2025-08-22 10:00:00 | 3.66 | 43.8888 | 0 | 0 | 296.6249 | -40.2288 | -40.2288
2025-08-22 11:00:00 | 3.72 | 46.5397 | 0 | 0 | 296.6249 | -42.8197 | -42.8197
2025-08-22 12:00:00 | 3.42 | 46.5397 | 0 | 0 | 296.6249 | -43.1197 | -43.1197
2025-08-22 13:00:00 | 3.66 | 43.8888 | 0 | 0 | 296.6249 | -40.2288 | -40.2288
2025-08-22 14:00:00 | 3.3 | 38.7678 | 0 | 0 | 296.6249 | -35.4678 | -35.4678
2025-08-22 15:00:00 | 2.88 | 31.5256 | 0 | 0 | 296.6249 | -28.6456 | -28.6456
2025-08-22 16:00:00 | 2.94 | 22.6557 | 0 | 0 | 296.6249 | -19.7157 | -19.7157
2025-08-22 17:00:00 | 2.76 | 12.7626 | 0 | 0 | 296.6249 | -10.0026 | -10.0026
2025-08-22 18:00:00 | 2.46 | 2.5206 | 0 | 0 | 296.6249 | -0.060574 | -0.060574
2025-08-22 19:00:00 | 2.64 | 0 | 0 | 0 | 296.6249 | 2.64 | 2.64
2025-08-22 20:00:00 | 6.66 | 0 | 0 | 0 | 296.6249 | 6.66 | 6.66
2025-08-22 21:00:00 | 17.34 | 0 | 0 | 0 | 296.6249 | 17.34 | 17.34
2025-08-22 22:00:00 | 17.22 | 0 | 0 | 0 | 296.6249 | 17.22 | 17.22
2025-08-22 23:00:00 | 17.16 | 0 | 0 | 0 | 296.6249 | 17.16 | 17.16
2025-08-23 00:00:00 | 17.46 | 0 | 0 | 0 | 296.6249 | 17.46 | 17.46
2025-08-23 01:00:00 | 17.16 | 0 | 0 | 0 | 296.6249 | 17.16 | 17.16
2025-08-23 02:00:00 | 17.28 | 0 | 0 | 0 | 296.6249 | 17.28 | 17.28
2025-08-23 03:00:00 | 17.46 | 0 | 0 | 0 | 296.6249 | 17.46 | 17.46
2025-08-23 04:00:00 | 20.16 | 0 | 0 | 0 | 296.6249 | 20.16 | 20.16
2025-08-23 05:00:00 | 18.12 | 2.2798 | 0 | 0 | 296.6249 | 15.8402 | 15.8402
2025-08-23 06:00:00 | 17.16 | 12.5344 | 0 | 0 | 296.6249 | 4.6256 | 4.6256
2025-08-23 07:00:00 | 9.6 | 22.4396 | 0 | 0 | 296.6249 | -12.8396 | -12.8396
2025-08-23 08:00:00 | 2.76 | 31.3204 | 0 | 0 | 296.6249 | -28.5604 | -28.5604
2025-08-23 09:00:00 | 2.58 | 38.5715 | 0 | 0 | 296.6249 | -35.9915 | -35.9915
2025-08-23 10:00:00 | 2.52 | 43.6989 | 0 | 0 | 296.6249 | -41.1789 | -41.1789
2025-08-23 11:00:00 | 2.46 | 46.353 | 0 | 0 | 296.6249 | -43.893 | -43.893
2025-08-23 12:00:00 | 2.82 | 46.353 | 0 | 0 | 296.6249 | -43.533 | -43.533
2025-08-23 13:00:00 | 2.52 | 43.6989 | 0 | 0 | 296.6249 | -41.1789 | -41.1789
2025-08-23 14:00:00 | 2.52 | 38.5715 | 0 | 0 | 296.6249 | -36.0515 | -36.0515
2025-08-23 15:00:00 | 2.52 | 31.3204 | 0 | 0 | 296.6249 | -28.8004 | -28.8004
2025-08-23 16:00:00 | 2.58 | 22.4396 | 0 | 0 | 296.6249 | -19.8596 | -19.8596
2025-08-23 17:00:00 | 2.76 | 12.5344 | 0 | 0 | 296.6249 | -9.7744 | -9.7744
2025-08-23 18:00:00 | 2.46 | 2.2798 | 0 | 0 | 296.6249 | 0.18022 | 0.18022
2025-08-23 19:00:00 | 2.64 | 0 | 0 | 0 | 296.6249 | 2.64 | 2.64
2025-08-23 20:00:00 | 2.58 | 0 | 0 | 0 | 296.6249 | 2.58 | 2.58
2025-08-23 21:00:00 | 3 | 0 | 0 | 0 | 296.6249 | 3 | 3
2025-08-23 22:00:00 | 2.7 | 0 | 0 | 0 | 296.6249 | 2.7 | 2.7
2025-08-23 23:00:00 | 2.64 | 0 | 0 | 0 | 296.6249 | 2.64 | 2.64
2025-08-24 00:00:00 | 2.88 | 0 | 0 | 0 | 296.6249 | 2.88 | 2.88
2025-08-24 01:00:00 | 5.82 | 0 | 0 | 0 | 296.6249 | 5.82 | 5.82
2025-08-24 02:00:00 | 2.88 | 0 | 0 | 0 | 296.6249 | 2.88 | 2.88
2025-08-24 03:00:00 | 2.94 | 0 | 0 | 0 | 296.6249 | 2.94 | 2.94
2025-08-24 04:00:00 | 3 | 0 | 0 | 0 | 296.6249 | 3 | 3
2025-08-24 05:00:00 | 3.54 | 2.0367 | 0 | 0 | 296.6249 | 1.5033 | 1.5033
2025-08-24 06:00:00 | 2.94 | 12.3036 | 0 | 0 | 296.6249 | -9.3636 | -9.3636
2025-08-24 07:00:00 | 4.5 | 22.2207 | 0 | 0 | 296.6249 | -17.7207 | -17.7207
2025-08-24 08:00:00 | 9.3 | 31.1121 | 0 | 0 | 296.6249 | -21.8121 | -21.8121
2025-08-24 09:00:00 | 5.46 | 38.372 | 0 | 0 | 296.6249 | -32.912 | -32.912
2025-08-24 10:00:00 | 2.58 | 43.5054 | 0 | 0 | 296.6249 | -40.9254 | -40.9254
2025-08-24 11:00:00 | 2.52 | 46.1627 | 0 | 0 | 296.6249 | -43.6427 | -43.6427
2025-08-24 12:00:00 | 2.46 | 46.1627 | 0 | 0 | 296.6249 | -43.7027 | -43.7027
2025-08-24 13:00:00 | 2.58 | 43.5054 | 0 | 0 | 296.6249 | -40.9254 | -40.9254
2025-08-24 14:00:00 | 2.64 | 38.372 | 0 | 0 | 296.6249 | -35.732 | -35.732
2025-08-24 15:00:00 | 2.64 | 31.1121 | 0 | 0 | 296.6249 | -28.4721 | -28.4721
2025-08-24 16:00:00 | 2.4 | 22.2207 | 0 | 0 | 296.6249 | -19.8207 | -19.8207
2025-08-24 17:00:00 | 2.64 | 12.3036 | 0 | 0 | 296.6249 | -9.6636 | -9.6636
2025-08-24 18:00:00 | 2.52 | 2.0367 | 0 | 0 | 296.6249 | 0.48332 | 0.48332
2025-08-24 19:00:00 | 2.64 | 0 | 0 | 0 | 296.6249 | 2.64 | 2.64
2025-08-24 20:00:00 | 2.64 | 0 | 0 | 0 | 296.6249 | 2.64 | 2.64
2025-08-24 21:00:00 | 2.64 | 0 | 0 | 0 | 296.6249 | 2.64 | 2.64
2025-08-24 22:00:00 | 5.16 | 0 | 0 | 0 | 296.6249 | 5.16 | 5.16
2025-08-24 23:00:00 | 9.54 | 0 | 0 | 0 | 296.6249 | 9.54 | 9.54
2025-08-25 00:00:00 | 9.72 | 0 | 0 | 0 | 296.6249 | 9.72 | 9.72
2025-08-25 01:00:00 | 10.2 | 0 | 0 | 0 | 296.6249 | 10.2 | 10.2
2025-08-25 02:00:00 | 10.02 | 0 | 0 | 0 | 296.6249 | 10.02 | 10.02
2025-08-25 03:00:00 | 10.62 | 0 | 0 | 0 | 296.6249 | 10.62 | 10.62
2025-08-25 04:00:00 | 9.9 | 0 | 0 | 0 | 296.6249 | 9.9 | 9.9
2025-08-25 05:00:00 | 10.38 | 1.7913 | 0 | 0 | 296.6249 | 8.5887 | 8.5887
2025-08-25 06:00:00 | 11.7 | 12.0703 | 0 | 0 | 296.6249 | -0.37029 | -0.37029
2025-08-25 07:00:00 | 11.4 | 21.999 | 0 | 0 | 296.6249 | -10.599 | -10.599
2025-08-25 08:00:00 | 11.16 | 30.9008 | 0 | 0 | 296.6249 | -19.7408 | -19.7408
2025-08-25 09:00:00 | 11.4 | 38.1691 | 0 | 0 | 296.6249 | -26.7691 | -26.7691
2025-08-25 10:00:00 | 7.32 | 43.3086 | 0 | 0 | 296.6249 | -35.9886 | -35.9886
2025-08-25 11:00:00 | 3.78 | 45.969 | 0 | 0 | 296.6249 | -42.189 | -42.189
2025-08-25 12:00:00 | 3.6 | 45.969 | 0 | 0 | 296.6249 | -42.369 | -42.369
2025-08-25 13:00:00 | 3.78 | 43.3086 | 0 | 0 | 296.6249 | -39.5286 | -39.5286
2025-08-25 14:00:00 | 3.24 | 38.1691 | 0 | 0 | 296.6249 | -34.9291 | -34.9291
2025-08-25 15:00:00 | 2.58 | 30.9008 | 0 | 0 | 296.6249 | -28.3208 | -28.3208
2025-08-25 16:00:00 | 2.58 | 21.999 | 0 | 0 | 296.6249 | -19.419 | -19.419
2025-08-25 17:00:00 | 2.46 | 12.0703 | 0 | 0 | 296.6249 | -9.6103 | -9.6103
2025-08-25 18:00:00 | 2.94 | 1.7913 | 0 | 1.1487 | 295.4762 | -2.2204e-16 | 1.1487
2025-08-25 19:00:00 | 3.3 | 0 | 0 | 0 | 295.4762 | 3.3 | 3.3
2025-08-25 20:00:00 | 3.48 | 0 | 0 | 0 | 295.4762 | 3.48 | 3.48
2025-08-25 21:00:00 | 3.42 | 0 | 0 | 0 | 295.4762 | 3.42 | 3.42
2025-08-25 22:00:00 | 3.72 | 0 | 0 | 0 | 295.4762 | 3.72 | 3.72
2025-08-25 23:00:00 | 3.66 | 0 | 0 | 0 | 295.4762 | 3.66 | 3.66
2025-08-26 00:00:00 | 3.72 | 0 | 0 | 0 | 295.4762 | 3.72 | 3.72
2025-08-26 01:00:00 | 3.72 | 0 | 0 | 0 | 295.4762 | 3.72 | 3.72
2025-08-26 02:00:00 | 4.14 | 0 | 0 | 0 | 295.4762 | 4.14 | 4.14
2025-08-26 03:00:00 | 4.14 | 0 | 0 | 0 | 295.4762 | 4.14 | 4.14
2025-08-26 04:00:00 | 3.96 | 0 | 0 | 0 | 295.4762 | 3.96 | 3.96
2025-08-26 05:00:00 | 4.26 | 1.5439 | 0 | 0 | 295.4762 | 2.7161 | 2.7161
2025-08-26 06:00:00 | 4.14 | 11.8345 | 0 | 0 | 295.4762 | -7.6945 | -7.6945
2025-08-26 07:00:00 | 3.84 | 21.7745 | 0 | 0 | 295.4762 | -17.9345 | -17.9345
2025-08-26 08:00:00 | 3.42 | 30.6864 | 0 | 0 | 295.4762 | -27.2664 | -27.2664
2025-08-26 09:00:00 | 3.66 | 37.963 | 0 | 0 | 295.4762 | -34.303 | -34.303
2025-08-26 10:00:00 | 4.2 | 43.1083 | 0 | 0 | 295.4762 | -38.9083 | -38.9083
2025-08-26 11:00:00 | 3.84 | 45.7717 | 0 | 0 | 295.4762 | -41.9317 | -41.9317
2025-08-26 12:00:00 | 4.62 | 45.7717 | 0 | 0 | 295.4762 | -41.1517 | -41.1517
2025-08-26 13:00:00 | 4.14 | 43.1083 | 0 | 0 | 295.4762 | -38.9683 | -38.9683
2025-08-26 14:00:00 | 4.32 | 37.963 | 0 | 0 | 295.4762 | -33.643 | -33.643
2025-08-26 15:00:00 | 4.26 | 30.6864 | 0 | 0 | 295.4762 | -26.4264 | -26.4264
2025-08-26 16:00:00 | 3.3 | 21.7745 | 0 | 0 | 295.4762 | -18.4745 | -18.4745
2025-08-26 17:00:00 | 2.94 | 11.8345 | 0 | 0 | 295.4762 | -8.8945 | -8.8945
2025-08-26 18:00:00 | 3.36 | 1.5439 | 0 | 1.8161 | 293.6601 | -7.9936e-15 | 1.8161
2025-08-26 19:00:00 | 3.9 | 0 | 0 | 0 | 293.6601 | 3.9 | 3.9
2025-08-26 20:00:00 | 3.54 | 0 | 0 | 0 | 293.6601 | 3.54 | 3.54
2025-08-26 21:00:00 | 4.02 | 0 | 0 | 0 | 293.6601 | 4.02 | 4.02
2025-08-26 22:00:00 | 4.2 | 0 | 0 | 0 | 293.6601 | 4.2 | 4.2
2025-08-26 23:00:00 | 3.78 | 0 | 0 | 0 | 293.6601 | 3.78 | 3.78
2025-08-27 00:00:00 | 4.32 | 0 | 0 | 0 | 293.6601 | 4.32 | 4.32
2025-08-27 01:00:00 | 4.62 | 0 | 0 | 0 | 293.6601 | 4.62 | 4.62
2025-08-27 02:00:00 | 4.32 | 0 | 0 | 0 | 293.6601 | 4.32 | 4.32
2025-08-27 03:00:00 | 4.26 | 0 | 0 | 0 | 293.6601 | 4.26 | 4.26
2025-08-27 04:00:00 | 4.62 | 0 | 0 | 0 | 293.6601 | 4.62 | 4.62
2025-08-27 05:00:00 | 4.5 | 1.2943 | 0 | 0 | 293.6601 | 3.2057 | 3.2057
2025-08-27 06:00:00 | 5.46 | 11.5963 | 0 | 0 | 293.6601 | -6.1363 | -6.1363
2025-08-27 07:00:00 | 5.76 | 21.5473 | 0 | 0 | 293.6601 | -15.7873 | -15.7873
2025-08-27 08:00:00 | 4.98 | 30.4691 | 0 | 0 | 293.6601 | -25.4891 | -25.4891
2025-08-27 09:00:00 | 4.98 | 37.7537 | 0 | 0 | 293.6601 | -32.7737 | -32.7737
2025-08-27 10:00:00 | 4.14 | 42.9047 | 0 | 0 | 293.6601 | -38.7647 | -38.7647
2025-08-27 11:00:00 | 4.44 | 45.571 | 0 | 0 | 293.6601 | -41.131 | -41.131
2025-08-27 12:00:00 | 3.72 | 45.571 | 0 | 0 | 293.6601 | -41.851 | -41.851
2025-08-27 13:00:00 | 3.78 | 42.9047 | 0 | 0 | 293.6601 | -39.1247 | -39.1247
2025-08-27 14:00:00 | 3.12 | 37.7537 | 0 | 0 | 293.6601 | -34.6337 | -34.6337
2025-08-27 15:00:00 | 2.7 | 30.4691 | 0 | 0 | 293.6601 | -27.7691 | -27.7691
2025-08-27 16:00:00 | 2.94 | 21.5473 | 0 | 0 | 293.6601 | -18.6073 | -18.6073
2025-08-27 17:00:00 | 2.46 | 11.5963 | 0 | 0 | 293.6601 | -9.1363 | -9.1363
2025-08-27 18:00:00 | 2.58 | 1.2943 | 0 | 1.2857 | 292.3744 | -1.1768e-14 | 1.2857
2025-08-27 19:00:00 | 3.12 | 0 | 0 | 0 | 292.3744 | 3.12 | 3.12
2025-08-27 20:00:00 | 3.36 | 0 | 0 | 0 | 292.3744 | 3.36 | 3.36
2025-08-27 21:00:00 | 3.66 | 0 | 0 | 0 | 292.3744 | 3.66 | 3.66
2025-08-27 22:00:00 | 3.72 | 0 | 0 | 0 | 292.3744 | 3.72 | 3.72
2025-08-27 23:00:00 | 4.02 | 0 | 0 | 0 | 292.3744 | 4.02 | 4.02
2025-08-28 00:00:00 | 3.78 | 0 | 0 | 0 | 292.3744 | 3.78 | 3.78
2025-08-28 01:00:00 | 4.14 | 0 | 0 | 0 | 292.3744 | 4.14 | 4.14
2025-08-28 02:00:00 | 4.2 | 0 | 0 | 0 | 292.3744 | 4.2 | 4.2
2025-08-28 03:00:00 | 4.08 | 0 | 0 | 0 | 292.3744 | 4.08 | 4.08
2025-08-28 04:00:00 | 4.26 | 0 | 0 | 0 | 292.3744 | 4.26 | 4.26
2025-08-28 05:00:00 | 4.26 | 1.0427 | 0 | 0 | 292.3744 | 3.2173 | 3.2173
2025-08-28 06:00:00 | 6.72 | 11.3558 | 0 | 0 | 292.3744 | -4.6358 | -4.6358
2025-08-28 07:00:00 | 6.24 | 21.3174 | 0 | 0 | 292.3744 | -15.0774 | -15.0774
2025-08-28 08:00:00 | 6.06 | 30.2487 | 0 | 0 | 292.3744 | -24.1887 | -24.1887
2025-08-28 09:00:00 | 6.54 | 37.5412 | 0 | 0 | 292.3744 | -31.0012 | -31.0012
2025-08-28 10:00:00 | 5.58 | 42.6977 | 0 | 0 | 292.3744 | -37.1177 | -37.1177
2025-08-28 11:00:00 | 6 | 45.3669 | 0 | 0 | 292.3744 | -39.3669 | -39.3669
2025-08-28 12:00:00 | 5.94 | 45.3669 | 0 | 0 | 292.3744 | -39.4269 | -39.4269
2025-08-28 13:00:00 | 5.76 | 42.6977 | 0 | 0 | 292.3744 | -36.9377 | -36.9377
2025-08-28 14:00:00 | 4.92 | 37.5412 | 0 | 0 | 292.3744 | -32.6212 | -32.6212
2025-08-28 15:00:00 | 3.66 | 30.2487 | 0 | 0 | 292.3744 | -26.5887 | -26.5887
2025-08-28 16:00:00 | 2.7 | 21.3174 | 0 | 0 | 292.3744 | -18.6174 | -18.6174
2025-08-28 17:00:00 | 3.06 | 11.3558 | 0 | 0 | 292.3744 | -8.2958 | -8.2958
2025-08-28 18:00:00 | 3.36 | 1.0427 | 0 | 2.3173 | 290.0571 | -6.6613e-15 | 2.3173
2025-08-28 19:00:00 | 3.36 | 0 | 0 | 0 | 290.0571 | 3.36 | 3.36
2025-08-28 20:00:00 | 3.96 | 0 | 0 | 0 | 290.0571 | 3.96 | 3.96
2025-08-28 21:00:00 | 4.08 | 0 | 0 | 0 | 290.0571 | 4.08 | 4.08
2025-08-28 22:00:00 | 4.14 | 0 | 0 | 0 | 290.0571 | 4.14 | 4.14
2025-08-28 23:00:00 | 4.44 | 0 | 0 | 0 | 290.0571 | 4.44 | 4.44
2025-08-29 00:00:00 | 4.62 | 0 | 0 | 0 | 290.0571 | 4.62 | 4.62
2025-08-29 01:00:00 | 4.44 | 0 | 0 | 0 | 290.0571 | 4.44 | 4.44
2025-08-29 02:00:00 | 4.62 | 0 | 0 | 0 | 290.0571 | 4.62 | 4.62
2025-08-29 03:00:00 | 4.68 | 0 | 0 | 0 | 290.0571 | 4.68 | 4.68
2025-08-29 04:00:00 | 5.1 | 0 | 0 | 0 | 290.0571 | 5.1 | 5.1
2025-08-29 05:00:00 | 4.86 | 0.78929 | 0 | 0 | 290.0571 | 4.0707 | 4.0707
2025-08-29 06:00:00 | 6 | 11.113 | 0 | 0 | 290.0571 | -5.113 | -5.113
2025-08-29 07:00:00 | 5.94 | 21.0849 | 0 | 0 | 290.0571 | -15.1449 | -15.1449
2025-08-29 08:00:00 | 3.18 | 30.0255 | 0 | 0 | 290.0571 | -26.8455 | -26.8455
2025-08-29 09:00:00 | 0 | 37.3255 | 0 | 0 | 290.0571 | -37.3255 | -37.3255
2025-08-29 10:00:00 | 0 | 42.4873 | 0 | 0 | 290.0571 | -42.4873 | -42.4873
2025-08-29 11:00:00 | 0 | 45.1593 | 0 | 0 | 290.0571 | -45.1593 | -45.1593
2025-08-29 12:00:00 | 4.44 | 45.1593 | 0 | 0 | 290.0571 | -40.7193 | -40.7193
2025-08-29 13:00:00 | 4.62 | 42.4873 | 0 | 0 | 290.0571 | -37.8673 | -37.8673
2025-08-29 14:00:00 | 3.72 | 37.3255 | 0 | 0 | 290.0571 | -33.6055 | -33.6055
2025-08-29 15:00:00 | 3.42 | 30.0255 | 0 | 0 | 290.0571 | -26.6055 | -26.6055
2025-08-29 16:00:00 | 3.36 | 21.0849 | 0 | 0 | 290.0571 | -17.7249 | -17.7249
2025-08-29 17:00:00 | 3.42 | 11.113 | 0 | 0 | 290.0571 | -7.693 | -7.693
2025-08-29 18:00:00 | 3.9 | 0.78929 | 0 | 3.1107 | 286.9464 | -1.2879e-14 | 3.1107
2025-08-29 19:00:00 | 3.72 | 0 | 0 | 0 | 286.9464 | 3.72 | 3.72
2025-08-29 20:00:00 | 4.5 | 0 | 0 | 0 | 286.9464 | 4.5 | 4.5
2025-08-29 21:00:00 | 4.32 | 0 | 0 | 0 | 286.9464 | 4.32 | 4.32
2025-08-29 22:00:00 | 4.38 | 0 | 0 | 0 | 286.9464 | 4.38 | 4.38
2025-08-29 23:00:00 | 4.74 | 0 | 0 | 0 | 286.9464 | 4.74 | 4.74
2025-08-30 00:00:00 | 4.74 | 0 | 0 | 0 | 286.9464 | 4.74 | 4.74
2025-08-30 01:00:00 | 4.5 | 0 | 0 | 0 | 286.9464 | 4.5 | 4.5
2025-08-30 02:00:00 | 5.04 | 0 | 0 | 0 | 286.9464 | 5.04 | 5.04
2025-08-30 03:00:00 | 4.86 | 0 | 0 | 0 | 286.9464 | 4.86 | 4.86
2025-08-30 04:00:00 | 4.62 | 0 | 0 | 0 | 286.9464 | 4.62 | 4.62
2025-08-30 05:00:00 | 4.56 | 0.53402 | 0 | 0 | 286.9464 | 4.026 | 4.026
2025-08-30 06:00:00 | 4.92 | 10.868 | 0 | 0 | 286.9464 | -5.948 | -5.948
2025-08-30 07:00:00 | 4.26 | 20.8499 | 0 | 0 | 286.9464 | -16.5899 | -16.5899
2025-08-30 08:00:00 | 3.9 | 29.7994 | 0 | 0 | 286.9464 | -25.8994 | -25.8994
2025-08-30 09:00:00 | 4.08 | 37.1067 | 0 | 0 | 286.9464 | -33.0267 | -33.0267
2025-08-30 10:00:00 | 3.24 | 42.2737 | 0 | 0 | 286.9464 | -39.0337 | -39.0337
2025-08-30 11:00:00 | 3.18 | 44.9483 | 0 | 0 | 286.9464 | -41.7683 | -41.7683
2025-08-30 12:00:00 | 2.82 | 44.9483 | 0 | 0 | 286.9464 | -42.1283 | -42.1283
2025-08-30 13:00:00 | 2.7 | 42.2737 | 0 | 0 | 286.9464 | -39.5737 | -39.5737
2025-08-30 14:00:00 | 2.52 | 37.1067 | 0 | 0 | 286.9464 | -34.5867 | -34.5867
2025-08-30 15:00:00 | 2.7 | 29.7994 | 0 | 0 | 286.9464 | -27.0994 | -27.0994
2025-08-30 16:00:00 | 2.82 | 20.8499 | 0 | 0 | 286.9464 | -18.0299 | -18.0299
2025-08-30 17:00:00 | 8.52 | 10.868 | 0 | 0 | 286.9464 | -2.348 | -2.348
2025-08-30 18:00:00 | 9.6 | 0.53402 | 0 | 0 | 286.9464 | 9.066 | 9.066
2025-08-30 19:00:00 | 10.32 | 0 | 0 | 0 | 286.9464 | 10.32 | 10.32
2025-08-30 20:00:00 | 10.08 | 0 | 0 | 0 | 286.9464 | 10.08 | 10.08
2025-08-30 21:00:00 | 10.62 | 0 | 0 | 0 | 286.9464 | 10.62 | 10.62
2025-08-30 22:00:00 | 10.44 | 0 | 0 | 0 | 286.9464 | 10.44 | 10.44
2025-08-30 23:00:00 | 10.98 | 0 | 0 | 0 | 286.9464 | 10.98 | 10.98
2025-08-31 00:00:00 | 10.98 | 0 | 0 | 0 | 286.9464 | 10.98 | 10.98
2025-08-31 01:00:00 | 10.98 | 0 | 0 | 0 | 286.9464 | 10.98 | 10.98
2025-08-31 02:00:00 | 11.52 | 0 | 0 | 0 | 286.9464 | 11.52 | 11.52
2025-08-31 03:00:00 | 11.22 | 0 | 0 | 0 | 286.9464 | 11.22 | 11.22
2025-08-31 04:00:00 | 11.16 | 0 | 0 | 0 | 286.9464 | 11.16 | 11.16
2025-08-31 05:00:00 | 10.98 | 0.27701 | 0 | 0 | 286.9464 | 10.703 | 10.703
2025-08-31 06:00:00 | 11.16 | 10.621 | 0 | 0 | 286.9464 | 0.53905 | 0.53905
2025-08-31 07:00:00 | 10.92 | 20.6124 | 0 | 0 | 286.9464 | -9.6924 | -9.6924
2025-08-31 08:00:00 | 7.26 | 29.5706 | 0 | 0 | 286.9464 | -22.3106 | -22.3106
2025-08-31 09:00:00 | 3.3 | 36.8848 | 0 | 0 | 286.9464 | -33.5848 | -33.5848
2025-08-31 10:00:00 | 3.36 | 42.0568 | 0 | 0 | 286.9464 | -38.6968 | -38.6968
2025-08-31 11:00:00 | 2.7 | 44.734 | 0 | 0 | 286.9464 | -42.034 | -42.034
2025-08-31 12:00:00 | 2.7 | 44.734 | 0 | 0 | 286.9464 | -42.034 | -42.034
2025-08-31 13:00:00 | 2.58 | 42.0568 | 0 | 0 | 286.9464 | -39.4768 | -39.4768
2025-08-31 14:00:00 | 2.94 | 36.8848 | 0 | 0 | 286.9464 | -33.9448 | -33.9448
2025-08-31 15:00:00 | 2.64 | 29.5706 | 0 | 0 | 286.9464 | -26.9306 | -26.9306
2025-08-31 16:00:00 | 2.7 | 20.6124 | 0 | 0 | 286.9464 | -17.9124 | -17.9124
2025-08-31 17:00:00 | 2.82 | 10.621 | 0 | 0 | 286.9464 | -7.801 | -7.801
2025-08-31 18:00:00 | 2.52 | 0.27701 | 0 | 0 | 286.9464 | 2.243 | 2.243
2025-08-31 19:00:00 | 2.82 | 0 | 0 | 0 | 286.9464 | 2.82 | 2.82
2025-08-31 20:00:00 | 2.76 | 0 | 0 | 0 | 286.9464 | 2.76 | 2.76
2025-08-31 21:00:00 | 3.54 | 0 | 16.62 | 0 | 301.572 | 20.16 | 3.54
2025-08-31 22:00:00 | 3.42 | 0 | 16.74 | 0 | 316.3032 | 20.16 | 3.42
2025-08-31 23:00:00 | 3.9 | 0 | 9.8827 | 0 | 325 | 13.7827 | 3.9
2025-09-01 00:00:00 | 3.84 | 0 | 0 | 0 | 325 | 3.84 | 3.84
2025-09-01 01:00:00 | 4.14 | 0 | 0 | 0 | 325 | 4.14 | 4.14
2025-09-01 02:00:00 | 3.96 | 0 | 0 | 0 | 325 | 3.96 | 3.96
2025-09-01 03:00:00 | 4.08 | 0 | 0 | 0 | 325 | 4.08 | 4.08
2025-09-01 04:00:00 | 4.38 | 0 | 0 | 0 | 325 | 4.38 | 4.38
2025-09-01 05:00:00 | 4.14 | 0.014776 | 0 | 0 | 325 | 4.1252 | 4.1252
2025-09-01 06:00:00 | 3.72 | 8.3502 | 0 | 0 | 325 | -4.6302 | -4.6302
2025-09-01 07:00:00 | 4.08 | 16.4016 | 0 | 0 | 325 | -12.3216 | -12.3216
2025-09-01 08:00:00 | 3.12 | 23.6203 | 0 | 0 | 325 | -20.5003 | -20.5003
2025-09-01 09:00:00 | 3.12 | 29.5144 | 0 | 0 | 325 | -26.3944 | -26.3944
2025-09-01 10:00:00 | 2.52 | 33.6821 | 0 | 0 | 325 | -31.1621 | -31.1621
2025-09-01 11:00:00 | 2.88 | 35.8394 | 0 | 0 | 325 | -32.9594 | -32.9594
2025-09-01 12:00:00 | 2.58 | 35.8394 | 0 | 0 | 325 | -33.2594 | -33.2594
2025-09-01 13:00:00 | 2.64 | 33.6821 | 0 | 0 | 325 | -31.0421 | -31.0421
2025-09-01 14:00:00 | 2.88 | 29.5144 | 0 | 0 | 325 | -26.6344 | -26.6344
2025-09-01 15:00:00 | 2.46 | 23.6203 | 0 | 0 | 325 | -21.1603 | -21.1603
2025-09-01 16:00:00 | 2.64 | 16.4016 | 0 | 0 | 325 | -13.7616 | -13.7616
2025-09-01 17:00:00 | 2.4 | 8.3502 | 0 | 0 | 325 | -5.9502 | -5.9502
2025-09-01 18:00:00 | 3 | 0.014776 | 0 | 0 | 325 | 2.9852 | 2.9852
2025-09-01 19:00:00 | 2.88 | 0 | 0 | 0 | 325 | 2.88 | 2.88
2025-09-01 20:00:00 | 2.64 | 0 | 0 | 0 | 325 | 2.64 | 2.64
2025-09-01 21:00:00 | 2.82 | 0 | 0 | 0 | 325 | 2.82 | 2.82
2025-09-01 22:00:00 | 3.42 | 0 | 0 | 0 | 325 | 3.42 | 3.42
2025-09-01 23:00:00 | 3.42 | 0 | 0 | 0 | 325 | 3.42 | 3.42
2025-09-02 00:00:00 | 3.66 | 0 | 0 | 0 | 325 | 3.66 | 3.66
2025-09-02 01:00:00 | 3.6 | 0 | 0 | 0 | 325 | 3.6 | 3.6
2025-09-02 02:00:00 | 3.96 | 0 | 0 | 0 | 325 | 3.96 | 3.96
2025-09-02 03:00:00 | 3.84 | 0 | 0 | 0 | 325 | 3.84 | 3.84
2025-09-02 04:00:00 | 4.08 | 0 | 0 | 0 | 325 | 4.08 | 4.08
2025-09-02 05:00:00 | 3.6 | 0 | 0 | 0 | 325 | 3.6 | 3.6
2025-09-02 06:00:00 | 5.28 | 8.1481 | 0 | 0 | 325 | -2.8681 | -2.8681
2025-09-02 07:00:00 | 4.44 | 16.2066 | 0 | 0 | 325 | -11.7666 | -11.7666
2025-09-02 08:00:00 | 4.44 | 23.4317 | 0 | 0 | 325 | -18.9917 | -18.9917
2025-09-02 09:00:00 | 3.48 | 29.3309 | 0 | 0 | 325 | -25.8509 | -25.8509
2025-09-02 10:00:00 | 3.36 | 33.5023 | 0 | 0 | 325 | -30.1423 | -30.1423
2025-09-02 11:00:00 | 3.9 | 35.6616 | 0 | 0 | 325 | -31.7616 | -31.7616
2025-09-02 12:00:00 | 3.36 | 35.6616 | 0 | 0 | 325 | -32.3016 | -32.3016
2025-09-02 13:00:00 | 3.24 | 33.5023 | 0 | 0 | 325 | -30.2623 | -30.2623
2025-09-02 14:00:00 | 3.24 | 29.3309 | 0 | 0 | 325 | -26.0909 | -26.0909
2025-09-02 15:00:00 | 3 | 23.4317 | 0 | 0 | 325 | -20.4317 | -20.4317
2025-09-02 16:00:00 | 3.18 | 16.2066 | 0 | 0 | 325 | -13.0266 | -13.0266
2025-09-02 17:00:00 | 2.52 | 8.1481 | 0 | 0 | 325 | -5.6281 | -5.6281
2025-09-02 18:00:00 | 5.28 | 0 | 0 | 5.28 | 319.72 | 0 | 5.28
2025-09-02 19:00:00 | 9.48 | 0 | 0 | 0 | 319.72 | 9.48 | 9.48
2025-09-02 20:00:00 | 9 | 0 | 0 | 0 | 319.72 | 9 | 9
2025-09-02 21:00:00 | 9 | 0 | 0 | 0 | 319.72 | 9 | 9
2025-09-02 22:00:00 | 9.6 | 0 | 0 | 0 | 319.72 | 9.6 | 9.6
2025-09-02 23:00:00 | 7.8 | 0 | 0 | 0 | 319.72 | 7.8 | 7.8
2025-09-03 00:00:00 | 3.6 | 0 | 0 | 0 | 319.72 | 3.6 | 3.6
2025-09-03 01:00:00 | 3.54 | 0 | 0 | 0 | 319.72 | 3.54 | 3.54
2025-09-03 02:00:00 | 3.78 | 0 | 0 | 0 | 319.72 | 3.78 | 3.78
2025-09-03 03:00:00 | 6.9 | 0 | 0 | 0 | 319.72 | 6.9 | 6.9
2025-09-03 04:00:00 | 4.02 | 0 | 0 | 0 | 319.72 | 4.02 | 4.02
2025-09-03 05:00:00 | 4.14 | 0 | 0 | 0 | 319.72 | 4.14 | 4.14
2025-09-03 06:00:00 | 4.74 | 7.9444 | 0 | 0 | 319.72 | -3.2044 | -3.2044
2025-09-03 07:00:00 | 4.98 | 16.0097 | 0 | 0 | 319.72 | -11.0297 | -11.0297
2025-09-03 08:00:00 | 4.98 | 23.2409 | 0 | 0 | 319.72 | -18.2609 | -18.2609
2025-09-03 09:00:00 | 3.9 | 29.1451 | 0 | 0 | 319.72 | -25.2451 | -25.2451
2025-09-03 10:00:00 | 3.72 | 33.32 | 0 | 0 | 319.72 | -29.6 | -29.6
2025-09-03 11:00:00 | 3.72 | 35.4811 | 0 | 0 | 319.72 | -31.7611 | -31.7611
2025-09-03 12:00:00 | 3.72 | 35.4811 | 0 | 0 | 319.72 | -31.7611 | -31.7611
2025-09-03 13:00:00 | 3.6 | 33.32 | 0 | 0 | 319.72 | -29.72 | -29.72
2025-09-03 14:00:00 | 3.6 | 29.1451 | 0 | 0 | 319.72 | -25.5451 | -25.5451
2025-09-03 15:00:00 | 2.52 | 23.2409 | 0 | 0 | 319.72 | -20.7209 | -20.7209
2025-09-03 16:00:00 | 2.82 | 16.0097 | 0 | 0 | 319.72 | -13.1897 | -13.1897
2025-09-03 17:00:00 | 2.76 | 7.9444 | 0 | 0 | 319.72 | -5.1844 | -5.1844
2025-09-03 18:00:00 | 2.88 | 0 | 0 | 2.88 | 316.84 | 0 | 2.88
2025-09-03 19:00:00 | 3 | 0 | 0 | 0 | 316.84 | 3 | 3
2025-09-03 20:00:00 | 2.76 | 0 | 0 | 0 | 316.84 | 2.76 | 2.76
2025-09-03 21:00:00 | 2.82 | 0 | 0 | 0 | 316.84 | 2.82 | 2.82
2025-09-03 22:00:00 | 3.36 | 0 | 0 | 0 | 316.84 | 3.36 | 3.36
2025-09-03 23:00:00 | 3.06 | 0 | 0 | 0 | 316.84 | 3.06 | 3.06
2025-09-04 00:00:00 | 3.12 | 0 | 0 | 0 | 316.84 | 3.12 | 3.12
2025-09-04 01:00:00 | 3.18 | 0 | 0 | 0 | 316.84 | 3.18 | 3.18
2025-09-04 02:00:00 | 3.48 | 0 | 0 | 0 | 316.84 | 3.48 | 3.48
2025-09-04 03:00:00 | 3.78 | 0 | 0 | 0 | 316.84 | 3.78 | 3.78
2025-09-04 04:00:00 | 3.24 | 0 | 0 | 0 | 316.84 | 3.24 | 3.24
2025-09-04 05:00:00 | 3.66 | 0 | 0 | 0 | 316.84 | 3.66 | 3.66
2025-09-04 06:00:00 | 4.92 | 7.7393 | 0 | 0 | 316.84 | -2.8193 | -2.8193
2025-09-04 07:00:00 | 4.86 | 15.8111 | 0 | 0 | 316.84 | -10.9511 | -10.9511
2025-09-04 08:00:00 | 5.28 | 23.048 | 0 | 0 | 316.84 | -17.768 | -17.768
2025-09-04 09:00:00 | 4.92 | 28.957 | 0 | 0 | 316.84 | -24.037 | -24.037
2025-09-04 10:00:00 | 4.8 | 33.1352 | 0 | 0 | 316.84 | -28.3352 | -28.3352
2025-09-04 11:00:00 | 4.14 | 35.298 | 0 | 0 | 316.84 | -31.158 | -31.158
2025-09-04 12:00:00 | 4.26 | 35.298 | 0 | 0 | 316.84 | -31.038 | -31.038
2025-09-04 13:00:00 | 3.72 | 33.1352 | 0 | 0 | 316.84 | -29.4152 | -29.4152
2025-09-04 14:00:00 | 3.06 | 28.957 | 0 | 0 | 316.84 | -25.897 | -25.897
2025-09-04 15:00:00 | 2.82 | 23.048 | 0 | 0 | 316.84 | -20.228 | -20.228
2025-09-04 16:00:00 | 2.88 | 15.8111 | 0 | 0 | 316.84 | -12.9311 | -12.9311
2025-09-04 17:00:00 | 2.88 | 7.7393 | 0 | 0 | 316.84 | -4.8593 | -4.8593
2025-09-04 18:00:00 | 3.24 | 0 | 0 | 3.24 | 313.6 | 0 | 3.24
2025-09-04 19:00:00 | 3.9 | 0 | 0 | 0 | 313.6 | 3.9 | 3.9
2025-09-04 20:00:00 | 4.02 | 0 | 0 | 0 | 313.6 | 4.02 | 4.02
2025-09-04 21:00:00 | 4.38 | 0 | 0 | 0 | 313.6 | 4.38 | 4.38
2025-09-04 22:00:00 | 4.38 | 0 | 0 | 0 | 313.6 | 4.38 | 4.38
2025-09-04 23:00:00 | 4.38 | 0 | 0 | 0 | 313.6 | 4.38 | 4.38
2025-09-05 00:00:00 | 4.68 | 0 | 0 | 0 | 313.6 | 4.68 | 4.68
2025-09-05 01:00:00 | 4.5 | 0 | 0 | 0 | 313.6 | 4.5 | 4.5
2025-09-05 02:00:00 | 4.74 | 0 | 0 | 0 | 313.6 | 4.74 | 4.74
2025-09-05 03:00:00 | 4.8 | 0 | 0 | 0 | 313.6 | 4.8 | 4.8
2025-09-05 04:00:00 | 4.68 | 0 | 0 | 0 | 313.6 | 4.68 | 4.68
2025-09-05 05:00:00 | 4.5 | 0 | 0 | 0 | 313.6 | 4.5 | 4.5
2025-09-05 06:00:00 | 5.82 | 7.5328 | 0 | 0 | 313.6 | -1.7128 | -1.7128
2025-09-05 07:00:00 | 5.28 | 15.6107 | 0 | 0 | 313.6 | -10.3307 | -10.3307
2025-09-05 08:00:00 | 5.34 | 22.8531 | 0 | 0 | 313.6 | -17.5131 | -17.5131
2025-09-05 09:00:00 | 4.74 | 28.7665 | 0 | 0 | 313.6 | -24.0265 | -24.0265
2025-09-05 10:00:00 | 4.8 | 32.948 | 0 | 0 | 313.6 | -28.148 | -28.148
2025-09-05 11:00:00 | 4.32 | 35.1124 | 0 | 0 | 313.6 | -30.7924 | -30.7924
2025-09-05 12:00:00 | 3.66 | 35.1124 | 0 | 0 | 313.6 | -31.4524 | -31.4524
2025-09-05 13:00:00 | 3.9 | 32.948 | 0 | 0 | 313.6 | -29.048 | -29.048
2025-09-05 14:00:00 | 3.3 | 28.7665 | 0 | 0 | 313.6 | -25.4665 | -25.4665
2025-09-05 15:00:00 | 2.82 | 22.8531 | 0 | 0 | 313.6 | -20.0331 | -20.0331
2025-09-05 16:00:00 | 3 | 15.6107 | 0 | 0 | 313.6 | -12.6107 | -12.6107
2025-09-05 17:00:00 | 5.52 | 7.5328 | 0 | 0 | 313.6 | -2.0128 | -2.0128
2025-09-05 18:00:00 | 9.78 | 0 | 0 | 9.78 | 303.82 | 0 | 9.78
2025-09-05 19:00:00 | 10.26 | 0 | 0 | 0 | 303.82 | 10.26 | 10.26
2025-09-05 20:00:00 | 10.32 | 0 | 0 | 0 | 303.82 | 10.32 | 10.32
2025-09-05 21:00:00 | 10.8 | 0 | 0 | 0 | 303.82 | 10.8 | 10.8
2025-09-05 22:00:00 | 10.98 | 0 | 0 | 0 | 303.82 | 10.98 | 10.98
2025-09-05 23:00:00 | 11.1 | 0 | 0 | 0 | 303.82 | 11.1 | 11.1
2025-09-06 00:00:00 | 11.22 | 0 | 0 | 0 | 303.82 | 11.22 | 11.22
2025-09-06 01:00:00 | 11.22 | 0 | 0 | 0 | 303.82 | 11.22 | 11.22
2025-09-06 02:00:00 | 11.58 | 0 | 0 | 0 | 303.82 | 11.58 | 11.58
2025-09-06 03:00:00 | 11.46 | 0 | 0 | 0 | 303.82 | 11.46 | 11.46
2025-09-06 04:00:00 | 11.22 | 0 | 0 | 0 | 303.82 | 11.22 | 11.22
2025-09-06 05:00:00 | 11.28 | 0 | 0 | 0 | 303.82 | 11.28 | 11.28
2025-09-06 06:00:00 | 11.52 | 7.325 | 0 | 0 | 303.82 | 4.195 | 4.195
2025-09-06 07:00:00 | 11.1 | 15.4087 | 0 | 0 | 303.82 | -4.3087 | -4.3087
2025-09-06 08:00:00 | 10.98 | 22.6563 | 0 | 0 | 303.82 | -11.6763 | -11.6763
2025-09-06 09:00:00 | 10.62 | 28.5739 | 0 | 0 | 303.82 | -17.9539 | -17.9539
2025-09-06 10:00:00 | 10.38 | 32.7583 | 0 | 0 | 303.82 | -22.3783 | -22.3783
2025-09-06 11:00:00 | 9.84 | 34.9243 | 0 | 0 | 303.82 | -25.0843 | -25.0843
2025-09-06 12:00:00 | 7.56 | 34.9243 | 0 | 0 | 303.82 | -27.3643 | -27.3643
2025-09-06 13:00:00 | 3.12 | 32.7583 | 0 | 0 | 303.82 | -29.6383 | -29.6383
2025-09-06 14:00:00 | 2.88 | 28.5739 | 0 | 0 | 303.82 | -25.6939 | -25.6939
2025-09-06 15:00:00 | 3.12 | 22.6563 | 0 | 0 | 303.82 | -19.5363 | -19.5363
2025-09-06 16:00:00 | 3.24 | 15.4087 | 0 | 0 | 303.82 | -12.1687 | -12.1687
2025-09-06 17:00:00 | 3.36 | 7.325 | 0 | 0 | 303.82 | -3.965 | -3.965
2025-09-06 18:00:00 | 3.78 | 0 | 0 | 0 | 303.82 | 3.78 | 3.78
2025-09-06 19:00:00 | 3.78 | 0 | 0 | 0 | 303.82 | 3.78 | 3.78
2025-09-06 20:00:00 | 3.96 | 0 | 0 | 0 | 303.82 | 3.96 | 3.96
2025-09-06 21:00:00 | 4.26 | 0 | 0 | 0 | 303.82 | 4.26 | 4.26
2025-09-06 22:00:00 | 4.26 | 0 | 0 | 0 | 303.82 | 4.26 | 4.26
2025-09-06 23:00:00 | 4.2 | 0 | 0 | 0 | 303.82 | 4.2 | 4.2
2025-09-07 00:00:00 | 4.68 | 0 | 0 | 0 | 303.82 | 4.68 | 4.68
2025-09-07 01:00:00 | 4.14 | 0 | 0 | 0 | 303.82 | 4.14 | 4.14
2025-09-07 02:00:00 | 4.32 | 0 | 0 | 0 | 303.82 | 4.32 | 4.32
2025-09-07 03:00:00 | 4.86 | 0 | 0 | 0 | 303.82 | 4.86 | 4.86
2025-09-07 04:00:00 | 4.74 | 0 | 0 | 0 | 303.82 | 4.74 | 4.74
2025-09-07 05:00:00 | 4.56 | 0 | 0 | 0 | 303.82 | 4.56 | 4.56
2025-09-07 06:00:00 | 4.44 | 7.1159 | 0 | 0 | 303.82 | -2.6759 | -2.6759
2025-09-07 07:00:00 | 4.92 | 15.205 | 0 | 0 | 303.82 | -10.285 | -10.285
2025-09-07 08:00:00 | 4.14 | 22.4575 | 0 | 0 | 303.82 | -18.3175 | -18.3175
2025-09-07 09:00:00 | 3.84 | 28.3791 | 0 | 0 | 303.82 | -24.5391 | -24.5391
2025-09-07 10:00:00 | 3.48 | 32.5663 | 0 | 0 | 303.82 | -29.0863 | -29.0863
2025-09-07 11:00:00 | 3.48 | 34.7338 | 0 | 0 | 303.82 | -31.2538 | -31.2538
2025-09-07 12:00:00 | 3.3 | 34.7338 | 0 | 0 | 303.82 | -31.4338 | -31.4338
2025-09-07 13:00:00 | 3.3 | 32.5663 | 0 | 0 | 303.82 | -29.2663 | -29.2663
2025-09-07 14:00:00 | 2.76 | 28.3791 | 0 | 0 | 303.82 | -25.6191 | -25.6191
2025-09-07 15:00:00 | 3 | 22.4575 | 0 | 0 | 303.82 | -19.4575 | -19.4575
2025-09-07 16:00:00 | 3.24 | 15.205 | 0 | 0 | 303.82 | -11.965 | -11.965
2025-09-07 17:00:00 | 3.36 | 7.1159 | 0 | 0 | 303.82 | -3.7559 | -3.7559
2025-09-07 18:00:00 | 3.72 | 0 | 0 | 0 | 303.82 | 3.72 | 3.72
2025-09-07 19:00:00 | 3.96 | 0 | 0 | 0 | 303.82 | 3.96 | 3.96
2025-09-07 20:00:00 | 4.26 | 0 | 0 | 0 | 303.82 | 4.26 | 4.26
2025-09-07 21:00:00 | 4.26 | 0 | 0 | 0 | 303.82 | 4.26 | 4.26
2025-09-07 22:00:00 | 4.74 | 0 | 0 | 0 | 303.82 | 4.74 | 4.74
2025-09-07 23:00:00 | 4.8 | 0 | 0 | 0 | 303.82 | 4.8 | 4.8
2025-09-08 00:00:00 | 5.04 | 0 | 0 | 0 | 303.82 | 5.04 | 5.04
2025-09-08 01:00:00 | 4.74 | 0 | 0 | 0 | 303.82 | 4.74 | 4.74
2025-09-08 02:00:00 | 5.22 | 0 | 0 | 0 | 303.82 | 5.22 | 5.22
2025-09-08 03:00:00 | 5.34 | 0 | 0 | 0 | 303.82 | 5.34 | 5.34
2025-09-08 04:00:00 | 5.58 | 0 | 0 | 0 | 303.82 | 5.58 | 5.58
2025-09-08 05:00:00 | 4.92 | 0 | 0 | 0 | 303.82 | 4.92 | 4.92
2025-09-08 06:00:00 | 6.48 | 6.9057 | 0 | 0 | 303.82 | -0.42568 | -0.42568
2025-09-08 07:00:00 | 6.18 | 14.9998 | 0 | 0 | 303.82 | -8.8198 | -8.8198
2025-09-08 08:00:00 | 6.36 | 22.2568 | 0 | 0 | 303.82 | -15.8968 | -15.8968
2025-09-08 09:00:00 | 5.82 | 28.1821 | 0 | 0 | 303.82 | -22.3621 | -22.3621
2025-09-08 10:00:00 | 6.18 | 32.372 | 0 | 0 | 303.82 | -26.192 | -26.192
2025-09-08 11:00:00 | 5.4 | 34.5408 | 0 | 0 | 303.82 | -29.1408 | -29.1408
2025-09-08 12:00:00 | 5.4 | 34.5408 | 0 | 0 | 303.82 | -29.1408 | -29.1408
2025-09-08 13:00:00 | 4.38 | 32.372 | 0 | 0 | 303.82 | -27.992 | -27.992
2025-09-08 14:00:00 | 4.32 | 28.1821 | 0 | 0 | 303.82 | -23.8621 | -23.8621
2025-09-08 15:00:00 | 4.14 | 22.2568 | 0 | 0 | 303.82 | -18.1168 | -18.1168
2025-09-08 16:00:00 | 3.48 | 14.9998 | 0 | 0 | 303.82 | -11.5198 | -11.5198
2025-09-08 17:00:00 | 2.94 | 6.9057 | 0 | 0 | 303.82 | -3.9657 | -3.9657
2025-09-08 18:00:00 | 3.42 | 0 | 0 | 3.42 | 300.4 | 0 | 3.42
2025-09-08 19:00:00 | 4.26 | 0 | 0 | 0 | 300.4 | 4.26 | 4.26
2025-09-08 20:00:00 | 4.14 | 0 | 0 | 0 | 300.4 | 4.14 | 4.14
2025-09-08 21:00:00 | 4.68 | 0 | 0 | 0 | 300.4 | 4.68 | 4.68
2025-09-08 22:00:00 | 4.5 | 0 | 0 | 0 | 300.4 | 4.5 | 4.5
2025-09-08 23:00:00 | 4.86 | 0 | 0 | 0 | 300.4 | 4.86 | 4.86
2025-09-09 00:00:00 | 5.04 | 0 | 0 | 0 | 300.4 | 5.04 | 5.04
2025-09-09 01:00:00 | 4.8 | 0 | 0 | 0 | 300.4 | 4.8 | 4.8
2025-09-09 02:00:00 | 4.98 | 0 | 0 | 0 | 300.4 | 4.98 | 4.98
2025-09-09 03:00:00 | 5.76 | 0 | 0 | 0 | 300.4 | 5.76 | 5.76
2025-09-09 04:00:00 | 5.7 | 0 | 0 | 0 | 300.4 | 5.7 | 5.7
2025-09-09 05:00:00 | 4.92 | 0 | 0 | 0 | 300.4 | 4.92 | 4.92
2025-09-09 06:00:00 | 6.12 | 6.6943 | 0 | 0 | 300.4 | -0.57429 | -0.57429
2025-09-09 07:00:00 | 6.42 | 14.7931 | 0 | 0 | 300.4 | -8.3731 | -8.3731
2025-09-09 08:00:00 | 6.78 | 22.0543 | 0 | 0 | 300.4 | -15.2743 | -15.2743
2025-09-09 09:00:00 | 6.42 | 27.9831 | 0 | 0 | 300.4 | -21.5631 | -21.5631
2025-09-09 10:00:00 | 5.1 | 32.1754 | 0 | 0 | 300.4 | -27.0754 | -27.0754
2025-09-09 11:00:00 | 4.32 | 34.3454 | 0 | 0 | 300.4 | -30.0254 | -30.0254
2025-09-09 12:00:00 | 4.26 | 34.3454 | 0 | 0 | 300.4 | -30.0854 | -30.0854
2025-09-09 13:00:00 | 3.96 | 32.1754 | 0 | 0 | 300.4 | -28.2154 | -28.2154
2025-09-09 14:00:00 | 3.78 | 27.9831 | 0 | 0 | 300.4 | -24.2031 | -24.2031
2025-09-09 15:00:00 | 3.66 | 22.0543 | 0 | 0 | 300.4 | -18.3943 | -18.3943
2025-09-09 16:00:00 | 3.12 | 14.7931 | 0 | 0 | 300.4 | -11.6731 | -11.6731
2025-09-09 17:00:00 | 2.58 | 6.6943 | 0 | 0 | 300.4 | -4.1143 | -4.1143
2025-09-09 18:00:00 | 2.64 | 0 | 0 | 2.64 | 297.76 | 0 | 2.64
2025-09-09 19:00:00 | 3.18 | 0 | 0 | 0 | 297.76 | 3.18 | 3.18
2025-09-09 20:00:00 | 5.52 | 0 | 0 | 0 | 297.76 | 5.52 | 5.52
2025-09-09 21:00:00 | 10.26 | 0 | 0 | 0 | 297.76 | 10.26 | 10.26
2025-09-09 22:00:00 | 10.26 | 0 | 0 | 0 | 297.76 | 10.26 | 10.26
2025-09-09 23:00:00 | 10.8 | 0 | 0 | 0 | 297.76 | 10.8 | 10.8
2025-09-10 00:00:00 | 10.5 | 0 | 0 | 0 | 297.76 | 10.5 | 10.5
2025-09-10 01:00:00 | 10.62 | 0 | 0 | 0 | 297.76 | 10.62 | 10.62
2025-09-10 02:00:00 | 10.62 | 0 | 0 | 0 | 297.76 | 10.62 | 10.62
2025-09-10 03:00:00 | 10.74 | 0 | 0 | 0 | 297.76 | 10.74 | 10.74
2025-09-10 04:00:00 | 10.92 | 0 | 0 | 0 | 297.76 | 10.92 | 10.92
2025-09-10 05:00:00 | 10.74 | 0 | 0 | 0 | 297.76 | 10.74 | 10.74
2025-09-10 06:00:00 | 11.82 | 6.4819 | 0 | 0 | 297.76 | 5.3381 | 5.3381
2025-09-10 07:00:00 | 5.28 | 14.585 | 0 | 0 | 297.76 | -9.305 | -9.305
2025-09-10 08:00:00 | 4.92 | 21.8501 | 0 | 0 | 297.76 | -16.9301 | -16.9301
2025-09-10 09:00:00 | 4.38 | 27.782 | 0 | 0 | 297.76 | -23.402 | -23.402
2025-09-10 10:00:00 | 3.9 | 31.9765 | 0 | 0 | 297.76 | -28.0765 | -28.0765
2025-09-10 11:00:00 | 4.32 | 34.1478 | 0 | 0 | 297.76 | -29.8278 | -29.8278
2025-09-10 12:00:00 | 10.32 | 34.1478 | 0 | 0 | 297.76 | -23.8278 | -23.8278
2025-09-10 13:00:00 | 10.44 | 31.9765 | 0 | 0 | 297.76 | -21.5365 | -21.5365
2025-09-10 14:00:00 | 10.62 | 27.782 | 0 | 0 | 297.76 | -17.162 | -17.162
2025-09-10 15:00:00 | 10.02 | 21.8501 | 0 | 0 | 297.76 | -11.8301 | -11.8301
2025-09-10 16:00:00 | 9.42 | 14.585 | 0 | 0 | 297.76 | -5.165 | -5.165
2025-09-10 17:00:00 | 9.24 | 6.4819 | 0 | 2.7581 | 295.0019 | 4.885e-15 | 2.7581
2025-09-10 18:00:00 | 9.54 | 0 | 0 | 9.54 | 285.4619 | 0 | 9.54
2025-09-10 19:00:00 | 9.42 | 0 | 0 | 0 | 285.4619 | 9.42 | 9.42
2025-09-10 20:00:00 | 9.42 | 0 | 0 | 0 | 285.4619 | 9.42 | 9.42
2025-09-10 21:00:00 | 4.92 | 0 | 0 | 0 | 285.4619 | 4.92 | 4.92
2025-09-10 22:00:00 | 2.88 | 0 | 0 | 0 | 285.4619 | 2.88 | 2.88
2025-09-10 23:00:00 | 3 | 0 | 0 | 0 | 285.4619 | 3 | 3
2025-09-11 00:00:00 | 3 | 0 | 0 | 0 | 285.4619 | 3 | 3
2025-09-11 01:00:00 | 3.18 | 0 | 0 | 0 | 285.4619 | 3.18 | 3.18
2025-09-11 02:00:00 | 3.06 | 0 | 0 | 0 | 285.4619 | 3.06 | 3.06
2025-09-11 03:00:00 | 3.06 | 0 | 0 | 0 | 285.4619 | 3.06 | 3.06
2025-09-11 04:00:00 | 3.24 | 0 | 0 | 0 | 285.4619 | 3.24 | 3.24
2025-09-11 05:00:00 | 3.12 | 0 | 0 | 0 | 285.4619 | 3.12 | 3.12
2025-09-11 06:00:00 | 5.1 | 6.2684 | 0 | 0 | 285.4619 | -1.1684 | -1.1684
2025-09-11 07:00:00 | 4.8 | 14.3756 | 0 | 0 | 285.4619 | -9.5756 | -9.5756
2025-09-11 08:00:00 | 4.2 | 21.6442 | 0 | 0 | 285.4619 | -17.4442 | -17.4442
2025-09-11 09:00:00 | 3.72 | 27.579 | 0 | 0 | 285.4619 | -23.859 | -23.859
2025-09-11 10:00:00 | 3.66 | 31.7756 | 0 | 0 | 285.4619 | -28.1156 | -28.1156
2025-09-11 11:00:00 | 3.66 | 33.9479 | 0 | 0 | 285.4619 | -30.2879 | -30.2879
2025-09-11 12:00:00 | 3.72 | 33.9479 | 0 | 0 | 285.4619 | -30.2279 | -30.2279
2025-09-11 13:00:00 | 3.9 | 31.7756 | 0 | 0 | 285.4619 | -27.8756 | -27.8756
2025-09-11 14:00:00 | 3.96 | 27.579 | 0 | 0 | 285.4619 | -23.619 | -23.619
2025-09-11 15:00:00 | 3.9 | 21.6442 | 0 | 0 | 285.4619 | -17.7442 | -17.7442
2025-09-11 16:00:00 | 2.52 | 14.3756 | 0 | 0 | 285.4619 | -11.8556 | -11.8556
2025-09-11 17:00:00 | 2.52 | 6.2684 | 0 | 0 | 285.4619 | -3.7484 | -3.7484
2025-09-11 18:00:00 | 2.52 | 0 | 0 | 2.52 | 282.9419 | 0 | 2.52
2025-09-11 19:00:00 | 2.58 | 0 | 0 | 0 | 282.9419 | 2.58 | 2.58
2025-09-11 20:00:00 | 7.86 | 0 | 0 | 0 | 282.9419 | 7.86 | 7.86
2025-09-11 21:00:00 | 9.9 | 0 | 0 | 0 | 282.9419 | 9.9 | 9.9
2025-09-11 22:00:00 | 10.32 | 0 | 0 | 0 | 282.9419 | 10.32 | 10.32
2025-09-11 23:00:00 | 10.14 | 0 | 0 | 0 | 282.9419 | 10.14 | 10.14
2025-09-12 00:00:00 | 10.38 | 0 | 0 | 0 | 282.9419 | 10.38 | 10.38
2025-09-12 01:00:00 | 10.32 | 0 | 0 | 0 | 282.9419 | 10.32 | 10.32
2025-09-12 02:00:00 | 10.44 | 0 | 0 | 0 | 282.9419 | 10.44 | 10.44
2025-09-12 03:00:00 | 10.2 | 0 | 0 | 0 | 282.9419 | 10.2 | 10.2
2025-09-12 04:00:00 | 10.32 | 0 | 0 | 0 | 282.9419 | 10.32 | 10.32
2025-09-12 05:00:00 | 10.44 | 0 | 0 | 0 | 282.9419 | 10.44 | 10.44
2025-09-12 06:00:00 | 10.08 | 6.0541 | 0 | 0 | 282.9419 | 4.0259 | 4.0259
2025-09-12 07:00:00 | 4.5 | 14.1648 | 0 | 0 | 282.9419 | -9.6648 | -9.6648
2025-09-12 08:00:00 | 4.32 | 21.4366 | 0 | 0 | 282.9419 | -17.1166 | -17.1166
2025-09-12 09:00:00 | 4.74 | 27.3741 | 0 | 0 | 282.9419 | -22.6341 | -22.6341
2025-09-12 10:00:00 | 4.8 | 31.5725 | 0 | 0 | 282.9419 | -26.7725 | -26.7725
2025-09-12 11:00:00 | 4.44 | 33.7457 | 0 | 0 | 282.9419 | -29.3057 | -29.3057
2025-09-12 12:00:00 | 4.74 | 33.7457 | 0 | 0 | 282.9419 | -29.0057 | -29.0057
2025-09-12 13:00:00 | 3.84 | 31.5725 | 0 | 0 | 282.9419 | -27.7325 | -27.7325
2025-09-12 14:00:00 | 4.02 | 27.3741 | 0 | 0 | 282.9419 | -23.3541 | -23.3541
2025-09-12 15:00:00 | 2.58 | 21.4366 | 0 | 0 | 282.9419 | -18.8566 | -18.8566
2025-09-12 16:00:00 | 2.34 | 14.1648 | 0 | 0 | 282.9419 | -11.8248 | -11.8248
2025-09-12 17:00:00 | 2.4 | 6.0541 | 0 | 0 | 282.9419 | -3.6541 | -3.6541
2025-09-12 18:00:00 | 2.82 | 0 | 0 | 2.82 | 280.1219 | 0 | 2.82
2025-09-12 19:00:00 | 2.34 | 0 | 0 | 0 | 280.1219 | 2.34 | 2.34
2025-09-12 20:00:00 | 2.4 | 0 | 0 | 0 | 280.1219 | 2.4 | 2.4
2025-09-12 21:00:00 | 2.52 | 0 | 0 | 0 | 280.1219 | 2.52 | 2.52
2025-09-12 22:00:00 | 2.7 | 0 | 0 | 0 | 280.1219 | 2.7 | 2.7
2025-09-12 23:00:00 | 2.52 | 0 | 0 | 0 | 280.1219 | 2.52 | 2.52
2025-09-13 00:00:00 | 2.34 | 0 | 0 | 0 | 280.1219 | 2.34 | 2.34
2025-09-13 01:00:00 | 2.82 | 0 | 0 | 0 | 280.1219 | 2.82 | 2.82
2025-09-13 02:00:00 | 2.34 | 0 | 0 | 0 | 280.1219 | 2.34 | 2.34
2025-09-13 03:00:00 | 2.64 | 0 | 0 | 0 | 280.1219 | 2.64 | 2.64
2025-09-13 04:00:00 | 2.28 | 0 | 0 | 0 | 280.1219 | 2.28 | 2.28
2025-09-13 05:00:00 | 2.82 | 0 | 0 | 0 | 280.1219 | 2.82 | 2.82
2025-09-13 06:00:00 | 2.28 | 5.839 | 0 | 0 | 280.1219 | -3.559 | -3.559
2025-09-13 07:00:00 | 2.4 | 13.9528 | 0 | 0 | 280.1219 | -11.5528 | -11.5528
2025-09-13 08:00:00 | 2.46 | 21.2275 | 0 | 0 | 280.1219 | -18.7675 | -18.7675
2025-09-13 09:00:00 | 2.34 | 27.1673 | 0 | 0 | 280.1219 | -24.8273 | -24.8273
2025-09-13 10:00:00 | 2.34 | 31.3673 | 0 | 0 | 280.1219 | -29.0273 | -29.0273
2025-09-13 11:00:00 | 2.28 | 33.5414 | 0 | 0 | 280.1219 | -31.2614 | -31.2614
2025-09-13 12:00:00 | 2.46 | 33.5414 | 0 | 0 | 280.1219 | -31.0814 | -31.0814
2025-09-13 13:00:00 | 2.34 | 31.3673 | 0 | 0 | 280.1219 | -29.0273 | -29.0273
2025-09-13 14:00:00 | 2.16 | 27.1673 | 0 | 0 | 280.1219 | -25.0073 | -25.0073
2025-09-13 15:00:00 | 2.28 | 21.2275 | 0 | 0 | 280.1219 | -18.9475 | -18.9475
2025-09-13 16:00:00 | 2.34 | 13.9528 | 0 | 0 | 280.1219 | -11.6128 | -11.6128
2025-09-13 17:00:00 | 2.4 | 5.839 | 0 | 0 | 280.1219 | -3.439 | -3.439
2025-09-13 18:00:00 | 2.22 | 0 | 0 | 0 | 280.1219 | 2.22 | 2.22
2025-09-13 19:00:00 | 2.46 | 0 | 0 | 0 | 280.1219 | 2.46 | 2.46
2025-09-13 20:00:00 | 2.52 | 0 | 0 | 0 | 280.1219 | 2.52 | 2.52
2025-09-13 21:00:00 | 2.58 | 0 | 0 | 0 | 280.1219 | 2.58 | 2.58
2025-09-13 22:00:00 | 3.3 | 0 | 0 | 0 | 280.1219 | 3.3 | 3.3
2025-09-13 23:00:00 | 2.4 | 0 | 0 | 0 | 280.1219 | 2.4 | 2.4
2025-09-14 00:00:00 | 2.46 | 0 | 0 | 0 | 280.1219 | 2.46 | 2.46
2025-09-14 01:00:00 | 2.7 | 0 | 0 | 0 | 280.1219 | 2.7 | 2.7
2025-09-14 02:00:00 | 2.4 | 0 | 0 | 0 | 280.1219 | 2.4 | 2.4
2025-09-14 03:00:00 | 2.46 | 0 | 0 | 0 | 280.1219 | 2.46 | 2.46
2025-09-14 04:00:00 | 2.4 | 0 | 0 | 0 | 280.1219 | 2.4 | 2.4
2025-09-14 05:00:00 | 2.52 | 0 | 0 | 0 | 280.1219 | 2.52 | 2.52
2025-09-14 06:00:00 | 2.46 | 5.623 | 0 | 0 | 280.1219 | -3.163 | -3.163
2025-09-14 07:00:00 | 2.46 | 13.7397 | 0 | 0 | 280.1219 | -11.2797 | -11.2797
2025-09-14 08:00:00 | 2.1 | 21.0169 | 0 | 0 | 280.1219 | -18.9169 | -18.9169
2025-09-14 09:00:00 | 2.52 | 26.9587 | 0 | 0 | 280.1219 | -24.4387 | -24.4387
2025-09-14 10:00:00 | 2.4 | 31.1602 | 0 | 0 | 280.1219 | -28.7602 | -28.7602
2025-09-14 11:00:00 | 2.46 | 33.335 | 0 | 0 | 280.1219 | -30.875 | -30.875
2025-09-14 12:00:00 | 2.1 | 33.335 | 0 | 0 | 280.1219 | -31.235 | -31.235
2025-09-14 13:00:00 | 2.28 | 31.1602 | 0 | 0 | 280.1219 | -28.8802 | -28.8802
2025-09-14 14:00:00 | 2.46 | 26.9587 | 0 | 0 | 280.1219 | -24.4987 | -24.4987
2025-09-14 15:00:00 | 2.22 | 21.0169 | 0 | 0 | 280.1219 | -18.7969 | -18.7969
2025-09-14 16:00:00 | 2.46 | 13.7397 | 0 | 0 | 280.1219 | -11.2797 | -11.2797
2025-09-14 17:00:00 | 2.1 | 5.623 | 0 | 0 | 280.1219 | -3.523 | -3.523
2025-09-14 18:00:00 | 2.28 | 0 | 0 | 0 | 280.1219 | 2.28 | 2.28
2025-09-14 19:00:00 | 2.82 | 0 | 0 | 0 | 280.1219 | 2.82 | 2.82
2025-09-14 20:00:00 | 2.34 | 0 | 0 | 0 | 280.1219 | 2.34 | 2.34
2025-09-14 21:00:00 | 2.4 | 0 | 0 | 0 | 280.1219 | 2.4 | 2.4
2025-09-14 22:00:00 | 2.4 | 0 | 0 | 0 | 280.1219 | 2.4 | 2.4
2025-09-14 23:00:00 | 2.88 | 0 | 0 | 0 | 280.1219 | 2.88 | 2.88
2025-09-15 00:00:00 | 2.4 | 0 | 0 | 0 | 280.1219 | 2.4 | 2.4
2025-09-15 01:00:00 | 2.4 | 0 | 0 | 0 | 280.1219 | 2.4 | 2.4
2025-09-15 02:00:00 | 2.58 | 0 | 0 | 0 | 280.1219 | 2.58 | 2.58
2025-09-15 03:00:00 | 2.46 | 0 | 0 | 0 | 280.1219 | 2.46 | 2.46
2025-09-15 04:00:00 | 2.82 | 0 | 0 | 0 | 280.1219 | 2.82 | 2.82
2025-09-15 05:00:00 | 2.46 | 0 | 0 | 0 | 280.1219 | 2.46 | 2.46
2025-09-15 06:00:00 | 3.48 | 5.4064 | 0 | 0 | 280.1219 | -1.9264 | -1.9264
2025-09-15 07:00:00 | 3.42 | 13.5255 | 0 | 0 | 280.1219 | -10.1055 | -10.1055
2025-09-15 08:00:00 | 3.3 | 20.8048 | 0 | 0 | 280.1219 | -17.5048 | -17.5048
2025-09-15 09:00:00 | 3 | 26.7484 | 0 | 0 | 280.1219 | -23.7484 | -23.7484
2025-09-15 10:00:00 | 3.48 | 30.9511 | 0 | 0 | 280.1219 | -27.4711 | -27.4711
2025-09-15 11:00:00 | 3.06 | 33.1266 | 0 | 0 | 280.1219 | -30.0666 | -30.0666
2025-09-15 12:00:00 | 3.18 | 33.1266 | 0 | 0 | 280.1219 | -29.9466 | -29.9466
2025-09-15 13:00:00 | 3.66 | 30.9511 | 0 | 0 | 280.1219 | -27.2911 | -27.2911
2025-09-15 14:00:00 | 2.58 | 26.7484 | 0 | 0 | 280.1219 | -24.1684 | -24.1684
2025-09-15 15:00:00 | 2.16 | 20.8048 | 0 | 0 | 280.1219 | -18.6448 | -18.6448
2025-09-15 16:00:00 | 2.7 | 13.5255 | 0 | 0 | 280.1219 | -10.8255 | -10.8255
2025-09-15 17:00:00 | 2.34 | 5.4064 | 0 | 0 | 280.1219 | -3.0664 | -3.0664
2025-09-15 18:00:00 | 2.22 | 0 | 0 | 2.22 | 277.9019 | 0 | 2.22
2025-09-15 19:00:00 | 2.46 | 0 | 0 | 0 | 277.9019 | 2.46 | 2.46
2025-09-15 20:00:00 | 2.58 | 0 | 0 | 0 | 277.9019 | 2.58 | 2.58
2025-09-15 21:00:00 | 2.46 | 0 | 0 | 0 | 277.9019 | 2.46 | 2.46
2025-09-15 22:00:00 | 2.46 | 0 | 0 | 0 | 277.9019 | 2.46 | 2.46
2025-09-15 23:00:00 | 2.58 | 0 | 0 | 0 | 277.9019 | 2.58 | 2.58
2025-09-16 00:00:00 | 2.34 | 0 | 0 | 0 | 277.9019 | 2.34 | 2.34
2025-09-16 01:00:00 | 2.64 | 0 | 0 | 0 | 277.9019 | 2.64 | 2.64
2025-09-16 02:00:00 | 2.58 | 0 | 0 | 0 | 277.9019 | 2.58 | 2.58
2025-09-16 03:00:00 | 2.34 | 0 | 0 | 0 | 277.9019 | 2.34 | 2.34
2025-09-16 04:00:00 | 2.46 | 0 | 0 | 0 | 277.9019 | 2.46 | 2.46
2025-09-16 05:00:00 | 2.58 | 0 | 0 | 0 | 277.9019 | 2.58 | 2.58
2025-09-16 06:00:00 | 3.3 | 5.1892 | 0 | 0 | 277.9019 | -1.8892 | -1.8892
2025-09-16 07:00:00 | 3.48 | 13.3102 | 0 | 0 | 277.9019 | -9.8302 | -9.8302
2025-09-16 08:00:00 | 3.66 | 20.5914 | 0 | 0 | 277.9019 | -16.9314 | -16.9314
2025-09-16 09:00:00 | 3.06 | 26.5364 | 0 | 0 | 277.9019 | -23.4764 | -23.4764
2025-09-16 10:00:00 | 3.48 | 30.7402 | 0 | 0 | 277.9019 | -27.2602 | -27.2602
2025-09-16 11:00:00 | 3.3 | 32.9162 | 0 | 0 | 277.9019 | -29.6162 | -29.6162
2025-09-16 12:00:00 | 2.7 | 32.9162 | 0 | 0 | 277.9019 | -30.2162 | -30.2162
2025-09-16 13:00:00 | 3.18 | 30.7402 | 0 | 0 | 277.9019 | -27.5602 | -27.5602
2025-09-16 14:00:00 | 3.12 | 26.5364 | 0 | 0 | 277.9019 | -23.4164 | -23.4164
2025-09-16 15:00:00 | 2.46 | 20.5914 | 0 | 0 | 277.9019 | -18.1314 | -18.1314
2025-09-16 16:00:00 | 3.3 | 13.3102 | 0 | 0 | 277.9019 | -10.0102 | -10.0102
2025-09-16 17:00:00 | 2.58 | 5.1892 | 0 | 0 | 277.9019 | -2.6092 | -2.6092
2025-09-16 18:00:00 | 2.34 | 0 | 0 | 2.34 | 275.5619 | 0 | 2.34
2025-09-16 19:00:00 | 2.34 | 0 | 0 | 0 | 275.5619 | 2.34 | 2.34
2025-09-16 20:00:00 | 2.46 | 0 | 0 | 0 | 275.5619 | 2.46 | 2.46
2025-09-16 21:00:00 | 2.76 | 0 | 0 | 0 | 275.5619 | 2.76 | 2.76
2025-09-16 22:00:00 | 2.46 | 0 | 0 | 0 | 275.5619 | 2.46 | 2.46
2025-09-16 23:00:00 | 2.4 | 0 | 0 | 0 | 275.5619 | 2.4 | 2.4
2025-09-17 00:00:00 | 2.34 | 0 | 0 | 0 | 275.5619 | 2.34 | 2.34
2025-09-17 01:00:00 | 2.94 | 0 | 0 | 0 | 275.5619 | 2.94 | 2.94
2025-09-17 02:00:00 | 2.46 | 0 | 0 | 0 | 275.5619 | 2.46 | 2.46
2025-09-17 03:00:00 | 2.4 | 0 | 0 | 0 | 275.5619 | 2.4 | 2.4
2025-09-17 04:00:00 | 2.46 | 0 | 0 | 0 | 275.5619 | 2.46 | 2.46
2025-09-17 05:00:00 | 2.7 | 0 | 0 | 0 | 275.5619 | 2.7 | 2.7
2025-09-17 06:00:00 | 3.78 | 4.9714 | 0 | 0 | 275.5619 | -1.1914 | -1.1914
2025-09-17 07:00:00 | 3.6 | 13.0941 | 0 | 0 | 275.5619 | -9.4941 | -9.4941
2025-09-17 08:00:00 | 3.18 | 20.3766 | 0 | 0 | 275.5619 | -17.1966 | -17.1966
2025-09-17 09:00:00 | 4.44 | 26.3229 | 0 | 0 | 275.5619 | -21.8829 | -21.8829
2025-09-17 10:00:00 | 4.08 | 30.5275 | 0 | 0 | 275.5619 | -26.4475 | -26.4475
2025-09-17 11:00:00 | 4.08 | 32.7039 | 0 | 0 | 275.5619 | -28.6239 | -28.6239
2025-09-17 12:00:00 | 3.42 | 32.7039 | 0 | 0 | 275.5619 | -29.2839 | -29.2839
2025-09-17 13:00:00 | 3.12 | 30.5275 | 0 | 0 | 275.5619 | -27.4075 | -27.4075
2025-09-17 14:00:00 | 2.94 | 26.3229 | 0 | 0 | 275.5619 | -23.3829 | -23.3829
2025-09-17 15:00:00 | 2.46 | 20.3766 | 0 | 0 | 275.5619 | -17.9166 | -17.9166
2025-09-17 16:00:00 | 2.52 | 13.0941 | 0 | 0 | 275.5619 | -10.5741 | -10.5741
2025-09-17 17:00:00 | 2.52 | 4.9714 | 0 | 0 | 275.5619 | -2.4514 | -2.4514
2025-09-17 18:00:00 | 2.52 | 0 | 0 | 2.52 | 273.0419 | 0 | 2.52
2025-09-17 19:00:00 | 2.46 | 0 | 0 | 0 | 273.0419 | 2.46 | 2.46
2025-09-17 20:00:00 | 2.64 | 0 | 0 | 0 | 273.0419 | 2.64 | 2.64
2025-09-17 21:00:00 | 2.58 | 0 | 0 | 0 | 273.0419 | 2.58 | 2.58
2025-09-17 22:00:00 | 2.4 | 0 | 0 | 0 | 273.0419 | 2.4 | 2.4
2025-09-17 23:00:00 | 2.28 | 0 | 0 | 0 | 273.0419 | 2.28 | 2.28
2025-09-18 00:00:00 | 2.7 | 0 | 0 | 0 | 273.0419 | 2.7 | 2.7
2025-09-18 01:00:00 | 2.4 | 0 | 0 | 0 | 273.0419 | 2.4 | 2.4
2025-09-18 02:00:00 | 2.46 | 0 | 0 | 0 | 273.0419 | 2.46 | 2.46
2025-09-18 03:00:00 | 2.34 | 0 | 0 | 0 | 273.0419 | 2.34 | 2.34
2025-09-18 04:00:00 | 2.82 | 0 | 0 | 0 | 273.0419 | 2.82 | 2.82
2025-09-18 05:00:00 | 2.34 | 0 | 0 | 0 | 273.0419 | 2.34 | 2.34
2025-09-18 06:00:00 | 3.06 | 4.7531 | 0 | 0 | 273.0419 | -1.6931 | -1.6931
2025-09-18 07:00:00 | 2.22 | 12.877 | 0 | 0 | 273.0419 | -10.657 | -10.657
2025-09-18 08:00:00 | 2.4 | 20.1607 | 0 | 0 | 273.0419 | -17.7607 | -17.7607
2025-09-18 09:00:00 | 2.52 | 26.1078 | 0 | 0 | 273.0419 | -23.5878 | -23.5878
2025-09-18 10:00:00 | 2.58 | 30.313 | 0 | 0 | 273.0419 | -27.733 | -27.733
2025-09-18 11:00:00 | 2.76 | 32.4898 | 0 | 0 | 273.0419 | -29.7298 | -29.7298
2025-09-18 12:00:00 | 3.66 | 32.4898 | 0 | 0 | 273.0419 | -28.8298 | -28.8298
2025-09-18 13:00:00 | 3.54 | 30.313 | 0 | 0 | 273.0419 | -26.773 | -26.773
2025-09-18 14:00:00 | 3.6 | 26.1078 | 0 | 0 | 273.0419 | -22.5078 | -22.5078
2025-09-18 15:00:00 | 3.42 | 20.1607 | 0 | 0 | 273.0419 | -16.7407 | -16.7407
2025-09-18 16:00:00 | 2.82 | 12.877 | 0 | 0 | 273.0419 | -10.057 | -10.057
2025-09-18 17:00:00 | 2.4 | 4.7531 | 0 | 0 | 273.0419 | -2.3531 | -2.3531
2025-09-18 18:00:00 | 2.4 | 0 | 0 | 2.4 | 270.6419 | 0 | 2.4
2025-09-18 19:00:00 | 3.24 | 0 | 0 | 0 | 270.6419 | 3.24 | 3.24
2025-09-18 20:00:00 | 2.82 | 0 | 0 | 0 | 270.6419 | 2.82 | 2.82
2025-09-18 21:00:00 | 2.64 | 0 | 0 | 0 | 270.6419 | 2.64 | 2.64
2025-09-18 22:00:00 | 2.4 | 0 | 0 | 0 | 270.6419 | 2.4 | 2.4
2025-09-18 23:00:00 | 2.4 | 0 | 0 | 0 | 270.6419 | 2.4 | 2.4
2025-09-19 00:00:00 | 2.46 | 0 | 0 | 0 | 270.6419 | 2.46 | 2.46
2025-09-19 01:00:00 | 2.46 | 0 | 0 | 0 | 270.6419 | 2.46 | 2.46
2025-09-19 02:00:00 | 2.58 | 0 | 0 | 0 | 270.6419 | 2.58 | 2.58
2025-09-19 03:00:00 | 2.52 | 0 | 0 | 0 | 270.6419 | 2.52 | 2.52
2025-09-19 04:00:00 | 2.34 | 0 | 0 | 0 | 270.6419 | 2.34 | 2.34
2025-09-19 05:00:00 | 2.64 | 0 | 0 | 0 | 270.6419 | 2.64 | 2.64
2025-09-19 06:00:00 | 4.68 | 4.5345 | 0 | 0 | 270.6419 | 0.14555 | 0.14555
2025-09-19 07:00:00 | 3.96 | 12.6591 | 0 | 0 | 270.6419 | -8.6991 | -8.6991
2025-09-19 08:00:00 | 3.06 | 19.9435 | 0 | 0 | 270.6419 | -16.8835 | -16.8835
2025-09-19 09:00:00 | 3.18 | 25.8912 | 0 | 0 | 270.6419 | -22.7112 | -22.7112
2025-09-19 10:00:00 | 3.42 | 30.0969 | 0 | 0 | 270.6419 | -26.6769 | -26.6769
2025-09-19 11:00:00 | 3.36 | 32.2739 | 0 | 0 | 270.6419 | -28.9139 | -28.9139
2025-09-19 12:00:00 | 3.54 | 32.2739 | 0 | 0 | 270.6419 | -28.7339 | -28.7339
2025-09-19 13:00:00 | 2.46 | 30.0969 | 0 | 0 | 270.6419 | -27.6369 | -27.6369
2025-09-19 14:00:00 | 2.16 | 25.8912 | 0 | 0 | 270.6419 | -23.7312 | -23.7312
2025-09-19 15:00:00 | 1.92 | 19.9435 | 0 | 0 | 270.6419 | -18.0235 | -18.0235
2025-09-19 16:00:00 | 2.04 | 12.6591 | 0 | 0 | 270.6419 | -10.6191 | -10.6191
2025-09-19 17:00:00 | 1.92 | 4.5345 | 0 | 0 | 270.6419 | -2.6145 | -2.6145
2025-09-19 18:00:00 | 2.34 | 0 | 0 | 2.34 | 268.3019 | 0 | 2.34
2025-09-19 19:00:00 | 2.04 | 0 | 0 | 0 | 268.3019 | 2.04 | 2.04
2025-09-19 20:00:00 | 2.16 | 0 | 0 | 0 | 268.3019 | 2.16 | 2.16
2025-09-19 21:00:00 | 2.16 | 0 | 0 | 0 | 268.3019 | 2.16 | 2.16
2025-09-19 22:00:00 | 2.46 | 0 | 0 | 0 | 268.3019 | 2.46 | 2.46
2025-09-19 23:00:00 | 2.1 | 0 | 0 | 0 | 268.3019 | 2.1 | 2.1
2025-09-20 00:00:00 | 1.98 | 0 | 0 | 0 | 268.3019 | 1.98 | 1.98
2025-09-20 01:00:00 | 2.22 | 0 | 0 | 0 | 268.3019 | 2.22 | 2.22
2025-09-20 02:00:00 | 2.1 | 0 | 0 | 0 | 268.3019 | 2.1 | 2.1
2025-09-20 03:00:00 | 2.34 | 0 | 0 | 0 | 268.3019 | 2.34 | 2.34
2025-09-20 04:00:00 | 2.04 | 0 | 0 | 0 | 268.3019 | 2.04 | 2.04
2025-09-20 05:00:00 | 2.04 | 0 | 0 | 0 | 268.3019 | 2.04 | 2.04
2025-09-20 06:00:00 | 1.98 | 4.3155 | 0 | 0 | 268.3019 | -2.3355 | -2.3355
2025-09-20 07:00:00 | 1.92 | 12.4406 | 0 | 0 | 268.3019 | -10.5206 | -10.5206
2025-09-20 08:00:00 | 2.1 | 19.7253 | 0 | 0 | 268.3019 | -17.6253 | -17.6253
2025-09-20 09:00:00 | 1.86 | 25.6733 | 0 | 0 | 268.3019 | -23.8133 | -23.8133
2025-09-20 10:00:00 | 2.88 | 29.8792 | 0 | 0 | 268.3019 | -26.9992 | -26.9992
2025-09-20 11:00:00 | 8.52 | 32.0563 | 0 | 0 | 268.3019 | -23.5363 | -23.5363
2025-09-20 12:00:00 | 3.24 | 32.0563 | 0 | 0 | 268.3019 | -28.8163 | -28.8163
2025-09-20 13:00:00 | 16.08 | 29.8792 | 0 | 0 | 268.3019 | -13.7992 | -13.7992
2025-09-20 14:00:00 | 16.5 | 25.6733 | 0 | 0 | 268.3019 | -9.1733 | -9.1733
2025-09-20 15:00:00 | 16.62 | 19.7253 | 0 | 0 | 268.3019 | -3.1053 | -3.1053
2025-09-20 16:00:00 | 16.44 | 12.4406 | 0 | 0 | 268.3019 | 3.9994 | 3.9994
2025-09-20 17:00:00 | 16.74 | 4.3155 | 0 | 0 | 268.3019 | 12.4245 | 12.4245
2025-09-20 18:00:00 | 16.68 | 0 | 0 | 0 | 268.3019 | 16.68 | 16.68
2025-09-20 19:00:00 | 16.86 | 0 | 0 | 0 | 268.3019 | 16.86 | 16.86
2025-09-20 20:00:00 | 16.74 | 0 | 0 | 0 | 268.3019 | 16.74 | 16.74
2025-09-20 21:00:00 | 16.68 | 0 | 0 | 0 | 268.3019 | 16.68 | 16.68
2025-09-20 22:00:00 | 14.7 | 0 | 0 | 0 | 268.3019 | 14.7 | 14.7
2025-09-20 23:00:00 | 2.28 | 0 | 0 | 0 | 268.3019 | 2.28 | 2.28
2025-09-21 00:00:00 | 2.22 | 0 | 0 | 0 | 268.3019 | 2.22 | 2.22
2025-09-21 01:00:00 | 2.1 | 0 | 0 | 0 | 268.3019 | 2.1 | 2.1
2025-09-21 02:00:00 | 5.82 | 0 | 0 | 0 | 268.3019 | 5.82 | 5.82
2025-09-21 03:00:00 | 2.04 | 0 | 0 | 0 | 268.3019 | 2.04 | 2.04
2025-09-21 04:00:00 | 2.1 | 0 | 0 | 0 | 268.3019 | 2.1 | 2.1
2025-09-21 05:00:00 | 2.16 | 0 | 0 | 0 | 268.3019 | 2.16 | 2.16
2025-09-21 06:00:00 | 1.92 | 4.0962 | 0 | 0 | 268.3019 | -2.1762 | -2.1762
2025-09-21 07:00:00 | 2.16 | 12.2213 | 0 | 0 | 268.3019 | -10.0613 | -10.0613
2025-09-21 08:00:00 | 1.86 | 19.5061 | 0 | 0 | 268.3019 | -17.6461 | -17.6461
2025-09-21 09:00:00 | 1.92 | 25.4541 | 0 | 0 | 268.3019 | -23.5341 | -23.5341
2025-09-21 10:00:00 | 1.98 | 29.6599 | 0 | 0 | 268.3019 | -27.6799 | -27.6799
2025-09-21 11:00:00 | 2.22 | 31.837 | 0 | 0 | 268.3019 | -29.617 | -29.617
2025-09-21 12:00:00 | 3.66 | 31.837 | 0 | 0 | 268.3019 | -28.177 | -28.177
2025-09-21 13:00:00 | 8.16 | 29.6599 | 0 | 0 | 268.3019 | -21.4999 | -21.4999
2025-09-21 14:00:00 | 8.22 | 25.4541 | 0 | 0 | 268.3019 | -17.2341 | -17.2341
2025-09-21 15:00:00 | 8.1 | 19.5061 | 0 | 0 | 268.3019 | -11.4061 | -11.4061
2025-09-21 16:00:00 | 8.4 | 12.2213 | 0 | 0 | 268.3019 | -3.8213 | -3.8213
2025-09-21 17:00:00 | 8.1 | 4.0962 | 0 | 0 | 268.3019 | 4.0038 | 4.0038
2025-09-21 18:00:00 | 8.4 | 0 | 0 | 0 | 268.3019 | 8.4 | 8.4
2025-09-21 19:00:00 | 5.64 | 0 | 0 | 0 | 268.3019 | 5.64 | 5.64
2025-09-21 20:00:00 | 2.34 | 0 | 0 | 0 | 268.3019 | 2.34 | 2.34
2025-09-21 21:00:00 | 2.16 | 0 | 0 | 0 | 268.3019 | 2.16 | 2.16
2025-09-21 22:00:00 | 2.04 | 0 | 0 | 0 | 268.3019 | 2.04 | 2.04
2025-09-21 23:00:00 | 2.1 | 0 | 0 | 0 | 268.3019 | 2.1 | 2.1
2025-09-22 00:00:00 | 2.1 | 0 | 0 | 0 | 268.3019 | 2.1 | 2.1
2025-09-22 01:00:00 | 2.28 | 0 | 0 | 0 | 268.3019 | 2.28 | 2.28
2025-09-22 02:00:00 | 2.1 | 0 | 0 | 0 | 268.3019 | 2.1 | 2.1
2025-09-22 03:00:00 | 2.1 | 0 | 0 | 0 | 268.3019 | 2.1 | 2.1
2025-09-22 04:00:00 | 2.1 | 0 | 0 | 0 | 268.3019 | 2.1 | 2.1
2025-09-22 05:00:00 | 3.18 | 0 | 0 | 0 | 268.3019 | 3.18 | 3.18
2025-09-22 06:00:00 | 4.32 | 3.8768 | 0 | 0 | 268.3019 | 0.44316 | 0.44316
2025-09-22 07:00:00 | 4.56 | 12.0015 | 0 | 0 | 268.3019 | -7.4415 | -7.4415
2025-09-22 08:00:00 | 4.08 | 19.2859 | 0 | 0 | 268.3019 | -15.2059 | -15.2059
2025-09-22 09:00:00 | 4.26 | 25.2336 | 0 | 0 | 268.3019 | -20.9736 | -20.9736
2025-09-22 10:00:00 | 4.32 | 29.4393 | 0 | 0 | 268.3019 | -25.1193 | -25.1193
2025-09-22 11:00:00 | 4.26 | 31.6163 | 0 | 0 | 268.3019 | -27.3563 | -27.3563
2025-09-22 12:00:00 | 2.76 | 31.6163 | 0 | 0 | 268.3019 | -28.8563 | -28.8563
2025-09-22 13:00:00 | 3.06 | 29.4393 | 0 | 0 | 268.3019 | -26.3793 | -26.3793
2025-09-22 14:00:00 | 2.64 | 25.2336 | 0 | 0 | 268.3019 | -22.5936 | -22.5936
2025-09-22 15:00:00 | 1.98 | 19.2859 | 0 | 0 | 268.3019 | -17.3059 | -17.3059
2025-09-22 16:00:00 | 1.86 | 12.0015 | 0 | 0 | 268.3019 | -10.1415 | -10.1415
2025-09-22 17:00:00 | 1.98 | 3.8768 | 0 | 0 | 268.3019 | -1.8968 | -1.8968
2025-09-22 18:00:00 | 1.98 | 0 | 0 | 1.98 | 266.3219 | 0 | 1.98
2025-09-22 19:00:00 | 1.92 | 0 | 0 | 0 | 266.3219 | 1.92 | 1.92
2025-09-22 20:00:00 | 2.04 | 0 | 0 | 0 | 266.3219 | 2.04 | 2.04
2025-09-22 21:00:00 | 2.04 | 0 | 0 | 0 | 266.3219 | 2.04 | 2.04
2025-09-22 22:00:00 | 2.16 | 0 | 0 | 0 | 266.3219 | 2.16 | 2.16
2025-09-22 23:00:00 | 2.04 | 0 | 0 | 0 | 266.3219 | 2.04 | 2.04
2025-09-23 00:00:00 | 1.86 | 0 | 0 | 0 | 266.3219 | 1.86 | 1.86
2025-09-23 01:00:00 | 2.1 | 0 | 0 | 0 | 266.3219 | 2.1 | 2.1
2025-09-23 02:00:00 | 2.22 | 0 | 0 | 0 | 266.3219 | 2.22 | 2.22
2025-09-23 03:00:00 | 1.86 | 0 | 0 | 0 | 266.3219 | 1.86 | 1.86
2025-09-23 04:00:00 | 2.04 | 0 | 0 | 0 | 266.3219 | 2.04 | 2.04
2025-09-23 05:00:00 | 2.04 | 0 | 0 | 0 | 266.3219 | 2.04 | 2.04
2025-09-23 06:00:00 | 4.08 | 3.6573 | 0 | 0 | 266.3219 | 0.42265 | 0.42265
2025-09-23 07:00:00 | 4.14 | 11.7812 | 0 | 0 | 266.3219 | -7.6412 | -7.6412
2025-09-23 08:00:00 | 4.2 | 19.0649 | 0 | 0 | 266.3219 | -14.8649 | -14.8649
2025-09-23 09:00:00 | 4.08 | 25.012 | 0 | 0 | 266.3219 | -20.932 | -20.932
2025-09-23 10:00:00 | 3.9 | 29.2172 | 0 | 0 | 266.3219 | -25.3172 | -25.3172
2025-09-23 11:00:00 | 6 | 31.394 | 0 | 0 | 266.3219 | -25.394 | -25.394
2025-09-23 12:00:00 | 4.98 | 31.394 | 0 | 0 | 266.3219 | -26.414 | -26.414
2025-09-23 13:00:00 | 3.96 | 29.2172 | 0 | 0 | 266.3219 | -25.2572 | -25.2572
2025-09-23 14:00:00 | 4.02 | 25.012 | 0 | 0 | 266.3219 | -20.992 | -20.992
2025-09-23 15:00:00 | 3.24 | 19.0649 | 0 | 0 | 266.3219 | -15.8249 | -15.8249
2025-09-23 16:00:00 | 1.8 | 11.7812 | 0 | 0 | 266.3219 | -9.9812 | -9.9812
2025-09-23 17:00:00 | 1.86 | 3.6573 | 0 | 0 | 266.3219 | -1.7973 | -1.7973
2025-09-23 18:00:00 | 1.92 | 0 | 0 | 1.92 | 264.4019 | 0 | 1.92
2025-09-23 19:00:00 | 2.22 | 0 | 0 | 0 | 264.4019 | 2.22 | 2.22
2025-09-23 20:00:00 | 1.98 | 0 | 0 | 0 | 264.4019 | 1.98 | 1.98
2025-09-23 21:00:00 | 1.86 | 0 | 0 | 0 | 264.4019 | 1.86 | 1.86
2025-09-23 22:00:00 | 2.1 | 0 | 0 | 0 | 264.4019 | 2.1 | 2.1
2025-09-23 23:00:00 | 2.22 | 0 | 0 | 0 | 264.4019 | 2.22 | 2.22
2025-09-24 00:00:00 | 1.98 | 0 | 0 | 0 | 264.4019 | 1.98 | 1.98
2025-09-24 01:00:00 | 1.98 | 0 | 0 | 0 | 264.4019 | 1.98 | 1.98
2025-09-24 02:00:00 | 2.04 | 0 | 0 | 0 | 264.4019 | 2.04 | 2.04
2025-09-24 03:00:00 | 2.22 | 0 | 0 | 0 | 264.4019 | 2.22 | 2.22
2025-09-24 04:00:00 | 1.98 | 0 | 0 | 0 | 264.4019 | 1.98 | 1.98
2025-09-24 05:00:00 | 2.28 | 0 | 0 | 0 | 264.4019 | 2.28 | 2.28
2025-09-24 06:00:00 | 5.88 | 3.4378 | 0 | 0 | 264.4019 | 2.4422 | 2.4422
2025-09-24 07:00:00 | 4.02 | 11.5605 | 0 | 0 | 264.4019 | -7.5405 | -7.5405
2025-09-24 08:00:00 | 4.02 | 18.8431 | 0 | 0 | 264.4019 | -14.8231 | -14.8231
2025-09-24 09:00:00 | 4.02 | 24.7893 | 0 | 0 | 264.4019 | -20.7693 | -20.7693
2025-09-24 10:00:00 | 4.2 | 28.9939 | 0 | 0 | 264.4019 | -24.7939 | -24.7939
2025-09-24 11:00:00 | 3.96 | 31.1704 | 0 | 0 | 264.4019 | -27.2104 | -27.2104
2025-09-24 12:00:00 | 4.2 | 31.1704 | 0 | 0 | 264.4019 | -26.9704 | -26.9704
2025-09-24 13:00:00 | 3.9 | 28.9939 | 0 | 0 | 264.4019 | -25.0939 | -25.0939
2025-09-24 14:00:00 | 4.26 | 24.7893 | 0 | 0 | 264.4019 | -20.5293 | -20.5293
2025-09-24 15:00:00 | 4.32 | 18.8431 | 0 | 0 | 264.4019 | -14.5231 | -14.5231
2025-09-24 16:00:00 | 3.84 | 11.5605 | 0 | 0 | 264.4019 | -7.7205 | -7.7205
2025-09-24 17:00:00 | 2.1 | 3.4378 | 0 | 0 | 264.4019 | -1.3378 | -1.3378
2025-09-24 18:00:00 | 1.86 | 0 | 0 | 1.86 | 262.5419 | 0 | 1.86
2025-09-24 19:00:00 | 2.16 | 0 | 0 | 0 | 262.5419 | 2.16 | 2.16
2025-09-24 20:00:00 | 2.1 | 0 | 0 | 0 | 262.5419 | 2.1 | 2.1
2025-09-24 21:00:00 | 1.86 | 0 | 0 | 0 | 262.5419 | 1.86 | 1.86
2025-09-24 22:00:00 | 2.1 | 0 | 0 | 0 | 262.5419 | 2.1 | 2.1
2025-09-24 23:00:00 | 2.04 | 0 | 0 | 0 | 262.5419 | 2.04 | 2.04
2025-09-25 00:00:00 | 1.98 | 0 | 0 | 0 | 262.5419 | 1.98 | 1.98
2025-09-25 01:00:00 | 2.16 | 0 | 0 | 0 | 262.5419 | 2.16 | 2.16
2025-09-25 02:00:00 | 2.04 | 0 | 0 | 0 | 262.5419 | 2.04 | 2.04
2025-09-25 03:00:00 | 1.86 | 0 | 0 | 0 | 262.5419 | 1.86 | 1.86
2025-09-25 04:00:00 | 2.16 | 0 | 0 | 0 | 262.5419 | 2.16 | 2.16
2025-09-25 05:00:00 | 2.1 | 0 | 0 | 0 | 262.5419 | 2.1 | 2.1
2025-09-25 06:00:00 | 8.4 | 3.2184 | 0 | 0 | 262.5419 | 5.1816 | 5.1816
2025-09-25 07:00:00 | 10.08 | 11.3394 | 0 | 0 | 262.5419 | -1.2594 | -1.2594
2025-09-25 08:00:00 | 3.9 | 18.6206 | 0 | 0 | 262.5419 | -14.7206 | -14.7206
2025-09-25 09:00:00 | 2.88 | 24.5656 | 0 | 0 | 262.5419 | -21.6856 | -21.6856
2025-09-25 10:00:00 | 2.58 | 28.7694 | 0 | 0 | 262.5419 | -26.1894 | -26.1894
2025-09-25 11:00:00 | 2.7 | 30.9454 | 0 | 0 | 262.5419 | -28.2454 | -28.2454
2025-09-25 12:00:00 | 2.82 | 30.9454 | 0 | 0 | 262.5419 | -28.1254 | -28.1254
2025-09-25 13:00:00 | 2.52 | 28.7694 | 0 | 0 | 262.5419 | -26.2494 | -26.2494
2025-09-25 14:00:00 | 1.8 | 24.5656 | 0 | 0 | 262.5419 | -22.7656 | -22.7656
2025-09-25 15:00:00 | 1.98 | 18.6206 | 0 | 0 | 262.5419 | -16.6406 | -16.6406
2025-09-25 16:00:00 | 1.8 | 11.3394 | 0 | 0 | 262.5419 | -9.5394 | -9.5394
2025-09-25 17:00:00 | 1.92 | 3.2184 | 0 | 0 | 262.5419 | -1.2984 | -1.2984
2025-09-25 18:00:00 | 2.16 | 0 | 0 | 2.16 | 260.3819 | 0 | 2.16
2025-09-25 19:00:00 | 1.92 | 0 | 0 | 0 | 260.3819 | 1.92 | 1.92
2025-09-25 20:00:00 | 2.16 | 0 | 0 | 0 | 260.3819 | 2.16 | 2.16
2025-09-25 21:00:00 | 2.16 | 0 | 0 | 0 | 260.3819 | 2.16 | 2.16
2025-09-25 22:00:00 | 2.04 | 0 | 0 | 0 | 260.3819 | 2.04 | 2.04
2025-09-25 23:00:00 | 1.98 | 0 | 0 | 0 | 260.3819 | 1.98 | 1.98
2025-09-26 00:00:00 | 2.1 | 0 | 0 | 0 | 260.3819 | 2.1 | 2.1
2025-09-26 01:00:00 | 1.98 | 0 | 0 | 0 | 260.3819 | 1.98 | 1.98
2025-09-26 02:00:00 | 2.04 | 0 | 0 | 0 | 260.3819 | 2.04 | 2.04
2025-09-26 03:00:00 | 2.22 | 0 | 0 | 0 | 260.3819 | 2.22 | 2.22
2025-09-26 04:00:00 | 1.98 | 0 | 0 | 0 | 260.3819 | 1.98 | 1.98
2025-09-26 05:00:00 | 2.16 | 0 | 0 | 0 | 260.3819 | 2.16 | 2.16
2025-09-26 06:00:00 | 4.38 | 2.9991 | 0 | 0 | 260.3819 | 1.3809 | 1.3809
2025-09-26 07:00:00 | 4.38 | 11.1181 | 0 | 0 | 260.3819 | -6.7381 | -6.7381
2025-09-26 08:00:00 | 4.08 | 18.3975 | 0 | 0 | 260.3819 | -14.3175 | -14.3175
2025-09-26 09:00:00 | 4.26 | 24.341 | 0 | 0 | 260.3819 | -20.081 | -20.081
2025-09-26 10:00:00 | 3.96 | 28.5438 | 0 | 0 | 260.3819 | -24.5838 | -24.5838
2025-09-26 11:00:00 | 4.02 | 30.7193 | 0 | 0 | 260.3819 | -26.6993 | -26.6993
2025-09-26 12:00:00 | 4.38 | 30.7193 | 0 | 0 | 260.3819 | -26.3393 | -26.3393
2025-09-26 13:00:00 | 4.14 | 28.5438 | 0 | 0 | 260.3819 | -24.4038 | -24.4038
2025-09-26 14:00:00 | 4.14 | 24.341 | 0 | 0 | 260.3819 | -20.201 | -20.201
2025-09-26 15:00:00 | 2.52 | 18.3975 | 0 | 0 | 260.3819 | -15.8775 | -15.8775
2025-09-26 16:00:00 | 5.58 | 11.1181 | 0 | 0 | 260.3819 | -5.5381 | -5.5381
2025-09-26 17:00:00 | 8.4 | 2.9991 | 0 | 5.4009 | 254.9809 | -2.6645e-15 | 5.4009
2025-09-26 18:00:00 | 8.64 | 0 | 0 | 8.64 | 246.3409 | 0 | 8.64
2025-09-26 19:00:00 | 8.46 | 0 | 0 | 0 | 246.3409 | 8.46 | 8.46
2025-09-26 20:00:00 | 8.58 | 0 | 0 | 0 | 246.3409 | 8.58 | 8.58
2025-09-26 21:00:00 | 8.52 | 0 | 0 | 0 | 246.3409 | 8.52 | 8.52
2025-09-26 22:00:00 | 8.88 | 0 | 0 | 0 | 246.3409 | 8.88 | 8.88
2025-09-26 23:00:00 | 8.58 | 0 | 0 | 0 | 246.3409 | 8.58 | 8.58
2025-09-27 00:00:00 | 8.58 | 0 | 0 | 0 | 246.3409 | 8.58 | 8.58
2025-09-27 01:00:00 | 8.64 | 0 | 0 | 0 | 246.3409 | 8.64 | 8.64
2025-09-27 02:00:00 | 8.82 | 0 | 0 | 0 | 246.3409 | 8.82 | 8.82
2025-09-27 03:00:00 | 8.52 | 0 | 0 | 0 | 246.3409 | 8.52 | 8.52
2025-09-27 04:00:00 | 8.58 | 0 | 0 | 0 | 246.3409 | 8.58 | 8.58
2025-09-27 05:00:00 | 8.52 | 0 | 0 | 0 | 246.3409 | 8.52 | 8.52
2025-09-27 06:00:00 | 8.52 | 2.78 | 0 | 0 | 246.3409 | 5.74 | 5.74
2025-09-27 07:00:00 | 8.4 | 10.8966 | 0 | 0 | 246.3409 | -2.4966 | -2.4966
2025-09-27 08:00:00 | 8.28 | 18.1738 | 0 | 0 | 246.3409 | -9.8938 | -9.8938
2025-09-27 09:00:00 | 8.34 | 24.1156 | 0 | 0 | 246.3409 | -15.7756 | -15.7756
2025-09-27 10:00:00 | 8.58 | 28.3171 | 0 | 0 | 246.3409 | -19.7371 | -19.7371
2025-09-27 11:00:00 | 8.22 | 30.492 | 0 | 0 | 246.3409 | -22.272 | -22.272
2025-09-27 12:00:00 | 7.02 | 30.492 | 0 | 0 | 246.3409 | -23.472 | -23.472
2025-09-27 13:00:00 | 1.8 | 28.3171 | 0 | 0 | 246.3409 | -26.5171 | -26.5171
2025-09-27 14:00:00 | 1.68 | 24.1156 | 0 | 0 | 246.3409 | -22.4356 | -22.4356
2025-09-27 15:00:00 | 1.98 | 18.1738 | 0 | 0 | 246.3409 | -16.1938 | -16.1938
2025-09-27 16:00:00 | 1.8 | 10.8966 | 0 | 0 | 246.3409 | -9.0966 | -9.0966
2025-09-27 17:00:00 | 1.8 | 2.78 | 0 | 0 | 246.3409 | -0.97995 | -0.97995
2025-09-27 18:00:00 | 1.86 | 0 | 0 | 0 | 246.3409 | 1.86 | 1.86
2025-09-27 19:00:00 | 1.92 | 0 | 0 | 0 | 246.3409 | 1.92 | 1.92
2025-09-27 20:00:00 | 2.22 | 0 | 0 | 0 | 246.3409 | 2.22 | 2.22
2025-09-27 21:00:00 | 1.98 | 0 | 0 | 0 | 246.3409 | 1.98 | 1.98
2025-09-27 22:00:00 | 1.98 | 0 | 0 | 0 | 246.3409 | 1.98 | 1.98
2025-09-27 23:00:00 | 1.92 | 0 | 0 | 0 | 246.3409 | 1.92 | 1.92
2025-09-28 00:00:00 | 2.1 | 0 | 0 | 0 | 246.3409 | 2.1 | 2.1
2025-09-28 01:00:00 | 2.04 | 0 | 0 | 0 | 246.3409 | 2.04 | 2.04
2025-09-28 02:00:00 | 1.98 | 0 | 0 | 0 | 246.3409 | 1.98 | 1.98
2025-09-28 03:00:00 | 1.98 | 0 | 0 | 0 | 246.3409 | 1.98 | 1.98
2025-09-28 04:00:00 | 1.92 | 0 | 0 | 0 | 246.3409 | 1.92 | 1.92
2025-09-28 05:00:00 | 2.16 | 0 | 0 | 0 | 246.3409 | 2.16 | 2.16
2025-09-28 06:00:00 | 1.86 | 2.5611 | 0 | 0 | 246.3409 | -0.70113 | -0.70113
2025-09-28 07:00:00 | 1.74 | 10.675 | 0 | 0 | 246.3409 | -8.935 | -8.935
2025-09-28 08:00:00 | 1.92 | 17.9497 | 0 | 0 | 246.3409 | -16.0297 | -16.0297
2025-09-28 09:00:00 | 1.8 | 23.8894 | 0 | 0 | 246.3409 | -22.0894 | -22.0894
2025-09-28 10:00:00 | 2.04 | 28.0895 | 0 | 0 | 246.3409 | -26.0495 | -26.0495
2025-09-28 11:00:00 | 1.8 | 30.2636 | 0 | 0 | 246.3409 | -28.4636 | -28.4636
2025-09-28 12:00:00 | 1.74 | 30.2636 | 0 | 0 | 246.3409 | -28.5236 | -28.5236
2025-09-28 13:00:00 | 1.8 | 28.0895 | 0 | 0 | 246.3409 | -26.2895 | -26.2895
2025-09-28 14:00:00 | 2.04 | 23.8894 | 0 | 0 | 246.3409 | -21.8494 | -21.8494
2025-09-28 15:00:00 | 1.74 | 17.9497 | 0 | 0 | 246.3409 | -16.2097 | -16.2097
2025-09-28 16:00:00 | 1.68 | 10.675 | 0 | 0 | 246.3409 | -8.995 | -8.995
2025-09-28 17:00:00 | 1.8 | 2.5611 | 0 | 0 | 246.3409 | -0.76113 | -0.76113
2025-09-28 18:00:00 | 2.1 | 0 | 0 | 0 | 246.3409 | 2.1 | 2.1
2025-09-28 19:00:00 | 2.04 | 0 | 0 | 0 | 246.3409 | 2.04 | 2.04
2025-09-28 20:00:00 | 1.98 | 0 | 0 | 0 | 246.3409 | 1.98 | 1.98
2025-09-28 21:00:00 | 1.98 | 0 | 0 | 0 | 246.3409 | 1.98 | 1.98
2025-09-28 22:00:00 | 2.04 | 0 | 0 | 0 | 246.3409 | 2.04 | 2.04
2025-09-28 23:00:00 | 2.04 | 0 | 0 | 0 | 246.3409 | 2.04 | 2.04
2025-09-29 00:00:00 | 1.92 | 0 | 0 | 0 | 246.3409 | 1.92 | 1.92
2025-09-29 01:00:00 | 2.22 | 0 | 0 | 0 | 246.3409 | 2.22 | 2.22
2025-09-29 02:00:00 | 2.04 | 0 | 0 | 0 | 246.3409 | 2.04 | 2.04
2025-09-29 03:00:00 | 1.92 | 0 | 0 | 0 | 246.3409 | 1.92 | 1.92
2025-09-29 04:00:00 | 1.98 | 0 | 0 | 0 | 246.3409 | 1.98 | 1.98
2025-09-29 05:00:00 | 2.34 | 0 | 0 | 0 | 246.3409 | 2.34 | 2.34
2025-09-29 06:00:00 | 4.2 | 2.3427 | 0 | 0 | 246.3409 | 1.8573 | 1.8573
2025-09-29 07:00:00 | 6.72 | 10.4534 | 0 | 0 | 246.3409 | -3.7334 | -3.7334
2025-09-29 08:00:00 | 4.56 | 17.7252 | 0 | 0 | 246.3409 | -13.1652 | -13.1652
2025-09-29 09:00:00 | 4.32 | 23.6626 | 0 | 0 | 246.3409 | -19.3426 | -19.3426
2025-09-29 10:00:00 | 4.26 | 27.861 | 0 | 0 | 246.3409 | -23.601 | -23.601
2025-09-29 11:00:00 | 4.32 | 30.0343 | 0 | 0 | 246.3409 | -25.7143 | -25.7143
2025-09-29 12:00:00 | 4.08 | 30.0343 | 0 | 0 | 246.3409 | -25.9543 | -25.9543
2025-09-29 13:00:00 | 4.14 | 27.861 | 0 | 0 | 246.3409 | -23.721 | -23.721
2025-09-29 14:00:00 | 4.32 | 23.6626 | 0 | 0 | 246.3409 | -19.3426 | -19.3426
2025-09-29 15:00:00 | 3.66 | 17.7252 | 0 | 0 | 246.3409 | -14.0652 | -14.0652
2025-09-29 16:00:00 | 2.52 | 10.4534 | 0 | 0 | 246.3409 | -7.9334 | -7.9334
2025-09-29 17:00:00 | 1.8 | 2.3427 | 0 | 0 | 246.3409 | -0.54267 | -0.54267
2025-09-29 18:00:00 | 2.16 | 0 | 0 | 2.16 | 244.1809 | 0 | 2.16
2025-09-29 19:00:00 | 1.92 | 0 | 0 | 0 | 244.1809 | 1.92 | 1.92
2025-09-29 20:00:00 | 1.92 | 0 | 0 | 0 | 244.1809 | 1.92 | 1.92
2025-09-29 21:00:00 | 1.98 | 0 | 0 | 0 | 244.1809 | 1.98 | 1.98
2025-09-29 22:00:00 | 2.22 | 0 | 0 | 0 | 244.1809 | 2.22 | 2.22
2025-09-29 23:00:00 | 2.1 | 0 | 0 | 0 | 244.1809 | 2.1 | 2.1
2025-09-30 00:00:00 | 1.98 | 0 | 0 | 0 | 244.1809 | 1.98 | 1.98
2025-09-30 01:00:00 | 2.16 | 0 | 0 | 0 | 244.1809 | 2.16 | 2.16
2025-09-30 02:00:00 | 1.92 | 0 | 0 | 0 | 244.1809 | 1.92 | 1.92
2025-09-30 03:00:00 | 1.92 | 0 | 0 | 0 | 244.1809 | 1.92 | 1.92
2025-09-30 04:00:00 | 2.04 | 0 | 0 | 0 | 244.1809 | 2.04 | 2.04
2025-09-30 05:00:00 | 2.16 | 0 | 0 | 0 | 244.1809 | 2.16 | 2.16
2025-09-30 06:00:00 | 2.16 | 2.1247 | 0 | 0 | 244.1809 | 0.03535 | 0.03535
2025-09-30 07:00:00 | 2.22 | 10.2318 | 0 | 0 | 244.1809 | -8.0118 | -8.0118
2025-09-30 08:00:00 | 2.22 | 17.5004 | 0 | 0 | 244.1809 | -15.2804 | -15.2804
2025-09-30 09:00:00 | 2.4 | 23.4352 | 0 | 0 | 244.1809 | -21.0352 | -21.0352
2025-09-30 10:00:00 | 2.52 | 27.6318 | 0 | 0 | 244.1809 | -25.1118 | -25.1118
2025-09-30 11:00:00 | 3.06 | 29.8041 | 0 | 0 | 244.1809 | -26.7441 | -26.7441
2025-09-30 12:00:00 | 2.82 | 29.8041 | 0 | 0 | 244.1809 | -26.9841 | -26.9841
2025-09-30 13:00:00 | 2.76 | 27.6318 | 0 | 0 | 244.1809 | -24.8718 | -24.8718
2025-09-30 14:00:00 | 2.58 | 23.4352 | 0 | 0 | 244.1809 | -20.8552 | -20.8552
2025-09-30 15:00:00 | 2.64 | 17.5004 | 0 | 0 | 244.1809 | -14.8604 | -14.8604
2025-09-30 16:00:00 | 2.34 | 10.2318 | 0 | 0 | 244.1809 | -7.8918 | -7.8918
2025-09-30 17:00:00 | 1.8 | 2.1247 | 0 | 0 | 244.1809 | -0.32465 | -0.32465
2025-09-30 18:00:00 | 1.62 | 0 | 0 | 1.62 | 242.5609 | 0 | 1.62
2025-09-30 19:00:00 | 1.68 | 0 | 0 | 0 | 242.5609 | 1.68 | 1.68
2025-09-30 20:00:00 | 1.68 | 0 | 0 | 0 | 242.5609 | 1.68 | 1.68
2025-09-30 21:00:00 | 1.98 | 0 | 46.6604 | 0 | 283.6221 | 48.6404 | 1.98
2025-09-30 22:00:00 | 1.68 | 0 | 0 | 0 | 283.6221 | 1.68 | 1.68
2025-09-30 23:00:00 | 1.62 | 0 | 47.0204 | 0 | 325 | 48.6404 | 1.62
2025-10-01 00:00:00 | 1.68 | 0 | 0 | 0 | 325 | 1.68 | 1.68
2025-10-01 01:00:00 | 1.92 | 0 | 0 | 0 | 325 | 1.92 | 1.92
2025-10-01 02:00:00 | 1.8 | 0 | 0 | 0 | 325 | 1.8 | 1.8
2025-10-01 03:00:00 | 1.74 | 0 | 0 | 0 | 325 | 1.74 | 1.74
2025-10-01 04:00:00 | 1.68 | 0 | 0 | 0 | 325 | 1.68 | 1.68
2025-10-01 05:00:00 | 1.68 | 0 | 0 | 0 | 325 | 1.68 | 1.68
2025-10-01 06:00:00 | 1.8 | 1.3651 | 0 | 0 | 325 | 0.43488 | 0.43488
2025-10-01 07:00:00 | 2.22 | 7.1653 | 0 | 0 | 325 | -4.9453 | -4.9453
2025-10-01 08:00:00 | 2.52 | 12.3656 | 0 | 0 | 325 | -9.8456 | -9.8456
2025-10-01 09:00:00 | 2.58 | 16.6116 | 0 | 0 | 325 | -14.0316 | -14.0316
2025-10-01 10:00:00 | 2.58 | 19.6139 | 0 | 0 | 325 | -17.0339 | -17.0339
2025-10-01 11:00:00 | 2.76 | 21.1681 | 0 | 0 | 325 | -18.4081 | -18.4081
2025-10-01 12:00:00 | 2.28 | 21.1681 | 0 | 0 | 325 | -18.8881 | -18.8881
2025-10-01 13:00:00 | 2.34 | 19.6139 | 0 | 0 | 325 | -17.2739 | -17.2739
2025-10-01 14:00:00 | 2.46 | 16.6116 | 0 | 0 | 325 | -14.1516 | -14.1516
2025-10-01 15:00:00 | 2.52 | 12.3656 | 0 | 0 | 325 | -9.8456 | -9.8456
2025-10-01 16:00:00 | 1.62 | 7.1653 | 0 | 0 | 325 | -5.5453 | -5.5453
2025-10-01 17:00:00 | 1.44 | 1.3651 | 0 | 0.074884 | 324.9251 | 2.7756e-17 | 0.074884
2025-10-01 18:00:00 | 1.68 | 0 | 0 | 1.68 | 323.2451 | 0 | 1.68
2025-10-01 19:00:00 | 1.8 | 0 | 0 | 0 | 323.2451 | 1.8 | 1.8
2025-10-01 20:00:00 | 1.62 | 0 | 0 | 0 | 323.2451 | 1.62 | 1.62
2025-10-01 21:00:00 | 1.74 | 0 | 0 | 0 | 323.2451 | 1.74 | 1.74
2025-10-01 22:00:00 | 1.86 | 0 | 0 | 0 | 323.2451 | 1.86 | 1.86
2025-10-01 23:00:00 | 1.8 | 0 | 0 | 0 | 323.2451 | 1.8 | 1.8
2025-10-02 00:00:00 | 1.68 | 0 | 0 | 0 | 323.2451 | 1.68 | 1.68
2025-10-02 01:00:00 | 1.74 | 0 | 0 | 0 | 323.2451 | 1.74 | 1.74
2025-10-02 02:00:00 | 1.86 | 0 | 0 | 0 | 323.2451 | 1.86 | 1.86
2025-10-02 03:00:00 | 1.74 | 0 | 0 | 0 | 323.2451 | 1.74 | 1.74
2025-10-02 04:00:00 | 1.56 | 0 | 0 | 0 | 323.2451 | 1.56 | 1.56
2025-10-02 05:00:00 | 1.62 | 0 | 0 | 0 | 323.2451 | 1.62 | 1.62
2025-10-02 06:00:00 | 1.74 | 1.2099 | 0 | 0 | 323.2451 | 0.53015 | 0.53015
2025-10-02 07:00:00 | 1.5 | 7.0069 | 0 | 0 | 323.2451 | -5.5069 | -5.5069
2025-10-02 08:00:00 | 2.58 | 12.2044 | 0 | 0 | 323.2451 | -9.6244 | -9.6244
2025-10-02 09:00:00 | 2.58 | 16.4482 | 0 | 0 | 323.2451 | -13.8682 | -13.8682
2025-10-02 10:00:00 | 2.64 | 19.4489 | 0 | 0 | 323.2451 | -16.8089 | -16.8089
2025-10-02 11:00:00 | 2.64 | 21.0023 | 0 | 0 | 323.2451 | -18.3623 | -18.3623
2025-10-02 12:00:00 | 2.64 | 21.0023 | 0 | 0 | 323.2451 | -18.3623 | -18.3623
2025-10-02 13:00:00 | 1.98 | 19.4489 | 0 | 0 | 323.2451 | -17.4689 | -17.4689
2025-10-02 14:00:00 | 1.74 | 16.4482 | 0 | 0 | 323.2451 | -14.7082 | -14.7082
2025-10-02 15:00:00 | 1.5 | 12.2044 | 0 | 0 | 323.2451 | -10.7044 | -10.7044
2025-10-02 16:00:00 | 1.68 | 7.0069 | 0 | 0 | 323.2451 | -5.3269 | -5.3269
2025-10-02 17:00:00 | 1.56 | 1.2099 | 0 | 0.35015 | 322.895 | -1.1102e-16 | 0.35015
2025-10-02 18:00:00 | 1.8 | 0 | 0 | 1.8 | 321.095 | 0 | 1.8
2025-10-02 19:00:00 | 1.74 | 0 | 0 | 0 | 321.095 | 1.74 | 1.74
2025-10-02 20:00:00 | 1.8 | 0 | 0 | 0 | 321.095 | 1.8 | 1.8
2025-10-02 21:00:00 | 1.8 | 0 | 0 | 0 | 321.095 | 1.8 | 1.8
2025-10-02 22:00:00 | 1.8 | 0 | 0 | 0 | 321.095 | 1.8 | 1.8
2025-10-02 23:00:00 | 1.8 | 0 | 0 | 0 | 321.095 | 1.8 | 1.8
2025-10-03 00:00:00 | 1.8 | 0 | 0 | 0 | 321.095 | 1.8 | 1.8
2025-10-03 01:00:00 | 1.68 | 0 | 0 | 0 | 321.095 | 1.68 | 1.68
2025-10-03 02:00:00 | 1.92 | 0 | 0 | 0 | 321.095 | 1.92 | 1.92
2025-10-03 03:00:00 | 1.8 | 0 | 0 | 0 | 321.095 | 1.8 | 1.8
2025-10-03 04:00:00 | 1.68 | 0 | 0 | 0 | 321.095 | 1.68 | 1.68
2025-10-03 05:00:00 | 1.92 | 0 | 0 | 0 | 321.095 | 1.92 | 1.92
2025-10-03 06:00:00 | 2.7 | 1.0551 | 0 | 0 | 321.095 | 1.6449 | 1.6449
2025-10-03 07:00:00 | 3.78 | 6.8488 | 0 | 0 | 321.095 | -3.0688 | -3.0688
2025-10-03 08:00:00 | 4.56 | 12.0433 | 0 | 0 | 321.095 | -7.4833 | -7.4833
2025-10-03 09:00:00 | 4.68 | 16.2845 | 0 | 0 | 321.095 | -11.6045 | -11.6045
2025-10-03 10:00:00 | 4.5 | 19.2836 | 0 | 0 | 321.095 | -14.7836 | -14.7836
2025-10-03 11:00:00 | 4.44 | 20.836 | 0 | 0 | 321.095 | -16.396 | -16.396
2025-10-03 12:00:00 | 4.44 | 20.836 | 0 | 0 | 321.095 | -16.396 | -16.396
2025-10-03 13:00:00 | 4.44 | 19.2836 | 0 | 0 | 321.095 | -14.8436 | -14.8436
2025-10-03 14:00:00 | 4.14 | 16.2845 | 0 | 0 | 321.095 | -12.1445 | -12.1445
2025-10-03 15:00:00 | 3.3 | 12.0433 | 0 | 0 | 321.095 | -8.7433 | -8.7433
2025-10-03 16:00:00 | 2.94 | 6.8488 | 0 | 0 | 321.095 | -3.9088 | -3.9088
2025-10-03 17:00:00 | 3.12 | 1.0551 | 0 | 2.0649 | 319.03 | 2.2204e-15 | 2.0649
2025-10-03 18:00:00 | 3.12 | 0 | 0 | 3.12 | 315.91 | 1.9984e-14 | 3.12
2025-10-03 19:00:00 | 3.12 | 0 | 0 | 0 | 315.91 | 3.12 | 3.12
2025-10-03 20:00:00 | 3.3 | 0 | 0 | 0 | 315.91 | 3.3 | 3.3
2025-10-03 21:00:00 | 3.12 | 0 | 0 | 0 | 315.91 | 3.12 | 3.12
2025-10-03 22:00:00 | 3.06 | 0 | 0 | 0 | 315.91 | 3.06 | 3.06
2025-10-03 23:00:00 | 3.42 | 0 | 0 | 0 | 315.91 | 3.42 | 3.42
2025-10-04 00:00:00 | 3.06 | 0 | 0 | 0 | 315.91 | 3.06 | 3.06
2025-10-04 01:00:00 | 3.18 | 0 | 0 | 0 | 315.91 | 3.18 | 3.18
2025-10-04 02:00:00 | 3.12 | 0 | 0 | 0 | 315.91 | 3.12 | 3.12
2025-10-04 03:00:00 | 3.3 | 0 | 0 | 0 | 315.91 | 3.3 | 3.3
2025-10-04 04:00:00 | 3.18 | 0 | 0 | 0 | 315.91 | 3.18 | 3.18
2025-10-04 05:00:00 | 3.06 | 0 | 0 | 0 | 315.91 | 3.06 | 3.06
2025-10-04 06:00:00 | 2.82 | 0.90081 | 0 | 0 | 315.91 | 1.9192 | 1.9192
2025-10-04 07:00:00 | 2.94 | 6.6909 | 0 | 0 | 315.91 | -3.7509 | -3.7509
2025-10-04 08:00:00 | 3.12 | 11.8821 | 0 | 0 | 315.91 | -8.7621 | -8.7621
2025-10-04 09:00:00 | 3.06 | 16.1208 | 0 | 0 | 315.91 | -13.0608 | -13.0608
2025-10-04 10:00:00 | 2.88 | 19.1179 | 0 | 0 | 315.91 | -16.2379 | -16.2379
2025-10-04 11:00:00 | 1.8 | 20.6694 | 0 | 0 | 315.91 | -18.8694 | -18.8694
2025-10-04 12:00:00 | 1.74 | 20.6694 | 0 | 0 | 315.91 | -18.9294 | -18.9294
2025-10-04 13:00:00 | 1.56 | 19.1179 | 0 | 0 | 315.91 | -17.5579 | -17.5579
2025-10-04 14:00:00 | 1.56 | 16.1208 | 0 | 0 | 315.91 | -14.5608 | -14.5608
2025-10-04 15:00:00 | 1.44 | 11.8821 | 0 | 0 | 315.91 | -10.4421 | -10.4421
2025-10-04 16:00:00 | 1.62 | 6.6909 | 0 | 0 | 315.91 | -5.0709 | -5.0709
2025-10-04 17:00:00 | 1.8 | 0.90081 | 0 | 0 | 315.91 | 0.89919 | 0.89919
2025-10-04 18:00:00 | 1.74 | 0 | 0 | 0 | 315.91 | 1.74 | 1.74
2025-10-04 19:00:00 | 1.68 | 0 | 0 | 0 | 315.91 | 1.68 | 1.68
2025-10-04 20:00:00 | 1.68 | 0 | 0 | 0 | 315.91 | 1.68 | 1.68
2025-10-04 21:00:00 | 1.68 | 0 | 0 | 0 | 315.91 | 1.68 | 1.68
2025-10-04 22:00:00 | 1.74 | 0 | 0 | 0 | 315.91 | 1.74 | 1.74
2025-10-04 23:00:00 | 1.86 | 0 | 0 | 0 | 315.91 | 1.86 | 1.86
2025-10-05 00:00:00 | 1.68 | 0 | 0 | 0 | 315.91 | 1.68 | 1.68
2025-10-05 01:00:00 | 1.74 | 0 | 0 | 0 | 315.91 | 1.74 | 1.74
2025-10-05 02:00:00 | 1.62 | 0 | 0 | 0 | 315.91 | 1.62 | 1.62
2025-10-05 03:00:00 | 1.92 | 0 | 0 | 0 | 315.91 | 1.92 | 1.92
2025-10-05 04:00:00 | 1.74 | 0 | 0 | 0 | 315.91 | 1.74 | 1.74
2025-10-05 05:00:00 | 1.68 | 0 | 0 | 0 | 315.91 | 1.68 | 1.68
2025-10-05 06:00:00 | 1.56 | 0.74714 | 0 | 0 | 315.91 | 0.81286 | 0.81286
2025-10-05 07:00:00 | 3.3 | 6.5333 | 0 | 0 | 315.91 | -3.2333 | -3.2333
2025-10-05 08:00:00 | 2.28 | 11.7211 | 0 | 0 | 315.91 | -9.4411 | -9.4411
2025-10-05 09:00:00 | 1.56 | 15.9569 | 0 | 0 | 315.91 | -14.3969 | -14.3969
2025-10-05 10:00:00 | 1.44 | 18.952 | 0 | 0 | 315.91 | -17.512 | -17.512
2025-10-05 11:00:00 | 1.62 | 20.5024 | 0 | 0 | 315.91 | -18.8824 | -18.8824
2025-10-05 12:00:00 | 1.74 | 20.5024 | 0 | 0 | 315.91 | -18.7624 | -18.7624
2025-10-05 13:00:00 | 1.5 | 18.952 | 0 | 0 | 315.91 | -17.452 | -17.452
2025-10-05 14:00:00 | 1.5 | 15.9569 | 0 | 0 | 315.91 | -14.4569 | -14.4569
2025-10-05 15:00:00 | 1.68 | 11.7211 | 0 | 0 | 315.91 | -10.0411 | -10.0411
2025-10-05 16:00:00 | 1.74 | 6.5333 | 0 | 0 | 315.91 | -4.7933 | -4.7933
2025-10-05 17:00:00 | 1.92 | 0.74714 | 0 | 0 | 315.91 | 1.1729 | 1.1729
2025-10-05 18:00:00 | 1.74 | 0 | 0 | 0 | 315.91 | 1.74 | 1.74
2025-10-05 19:00:00 | 1.68 | 0 | 0 | 0 | 315.91 | 1.68 | 1.68
2025-10-05 20:00:00 | 1.68 | 0 | 0 | 0 | 315.91 | 1.68 | 1.68
2025-10-05 21:00:00 | 1.74 | 0 | 0 | 0 | 315.91 | 1.74 | 1.74
2025-10-05 22:00:00 | 2.04 | 0 | 0 | 0 | 315.91 | 2.04 | 2.04
2025-10-05 23:00:00 | 1.74 | 0 | 0 | 0 | 315.91 | 1.74 | 1.74
2025-10-06 00:00:00 | 1.62 | 0 | 0 | 0 | 315.91 | 1.62 | 1.62
2025-10-06 01:00:00 | 1.74 | 0 | 0 | 0 | 315.91 | 1.74 | 1.74
2025-10-06 02:00:00 | 1.62 | 0 | 0 | 0 | 315.91 | 1.62 | 1.62
2025-10-06 03:00:00 | 1.92 | 0 | 0 | 0 | 315.91 | 1.92 | 1.92
2025-10-06 04:00:00 | 1.68 | 0 | 0 | 0 | 315.91 | 1.68 | 1.68
2025-10-06 05:00:00 | 1.68 | 0 | 0 | 0 | 315.91 | 1.68 | 1.68
2025-10-06 06:00:00 | 1.56 | 0.59411 | 0 | 0 | 315.91 | 0.96589 | 0.96589
2025-10-06 07:00:00 | 1.8 | 6.3762 | 0 | 0 | 315.91 | -4.5762 | -4.5762
2025-10-06 08:00:00 | 2.76 | 11.5602 | 0 | 0 | 315.91 | -8.8002 | -8.8002
2025-10-06 09:00:00 | 2.52 | 15.793 | 0 | 0 | 315.91 | -13.273 | -13.273
2025-10-06 10:00:00 | 2.7 | 18.786 | 0 | 0 | 315.91 | -16.086 | -16.086
2025-10-06 11:00:00 | 2.4 | 20.3353 | 0 | 0 | 315.91 | -17.9353 | -17.9353
2025-10-06 12:00:00 | 2.46 | 20.3353 | 0 | 0 | 315.91 | -17.8753 | -17.8753
2025-10-06 13:00:00 | 2.94 | 18.786 | 0 | 0 | 315.91 | -15.846 | -15.846
2025-10-06 14:00:00 | 2.88 | 15.793 | 0 | 0 | 315.91 | -12.913 | -12.913
2025-10-06 15:00:00 | 1.68 | 11.5602 | 0 | 0 | 315.91 | -9.8802 | -9.8802
2025-10-06 16:00:00 | 1.8 | 6.3762 | 0 | 0 | 315.91 | -4.5762 | -4.5762
2025-10-06 17:00:00 | 1.62 | 0.59411 | 0 | 1.0259 | 314.8842 | -2.4425e-15 | 1.0259
2025-10-06 18:00:00 | 1.98 | 0 | 0 | 1.98 | 312.9042 | 0 | 1.98
2025-10-06 19:00:00 | 1.74 | 0 | 0 | 0 | 312.9042 | 1.74 | 1.74
2025-10-06 20:00:00 | 1.74 | 0 | 0 | 0 | 312.9042 | 1.74 | 1.74
2025-10-06 21:00:00 | 1.8 | 0 | 0 | 0 | 312.9042 | 1.8 | 1.8
2025-10-06 22:00:00 | 2.04 | 0 | 0 | 0 | 312.9042 | 2.04 | 2.04
2025-10-06 23:00:00 | 1.74 | 0 | 0 | 0 | 312.9042 | 1.74 | 1.74
2025-10-07 00:00:00 | 1.74 | 0 | 0 | 0 | 312.9042 | 1.74 | 1.74
2025-10-07 01:00:00 | 1.74 | 0 | 0 | 0 | 312.9042 | 1.74 | 1.74
2025-10-07 02:00:00 | 2.04 | 0 | 0 | 0 | 312.9042 | 2.04 | 2.04
2025-10-07 03:00:00 | 1.74 | 0 | 0 | 0 | 312.9042 | 1.74 | 1.74
2025-10-07 04:00:00 | 1.74 | 0 | 0 | 0 | 312.9042 | 1.74 | 1.74
2025-10-07 05:00:00 | 1.74 | 0 | 0 | 0 | 312.9042 | 1.74 | 1.74
2025-10-07 06:00:00 | 2.34 | 0.44177 | 0 | 0 | 312.9042 | 1.8982 | 1.8982
2025-10-07 07:00:00 | 1.86 | 6.2195 | 0 | 0 | 312.9042 | -4.3595 | -4.3595
2025-10-07 08:00:00 | 1.5 | 11.3996 | 0 | 0 | 312.9042 | -9.8996 | -9.8996
2025-10-07 09:00:00 | 1.56 | 15.6291 | 0 | 0 | 312.9042 | -14.0691 | -14.0691
2025-10-07 10:00:00 | 1.74 | 18.6199 | 0 | 0 | 312.9042 | -16.8799 | -16.8799
2025-10-07 11:00:00 | 2.22 | 20.168 | 0 | 0 | 312.9042 | -17.948 | -17.948
2025-10-07 12:00:00 | 2.58 | 20.168 | 0 | 0 | 312.9042 | -17.588 | -17.588
2025-10-07 13:00:00 | 2.46 | 18.6199 | 0 | 0 | 312.9042 | -16.1599 | -16.1599
2025-10-07 14:00:00 | 2.46 | 15.6291 | 0 | 0 | 312.9042 | -13.1691 | -13.1691
2025-10-07 15:00:00 | 2.34 | 11.3996 | 0 | 0 | 312.9042 | -9.0596 | -9.0596
2025-10-07 16:00:00 | 2.4 | 6.2195 | 0 | 0 | 312.9042 | -3.8195 | -3.8195
2025-10-07 17:00:00 | 2.58 | 0.44177 | 0 | 2.1382 | 310.7659 | -4.4409e-15 | 2.1382
2025-10-07 18:00:00 | 2.52 | 0 | 0 | 2.52 | 308.2459 | -9.77e-15 | 2.52
2025-10-07 19:00:00 | 2.58 | 0 | 0 | 0 | 308.2459 | 2.58 | 2.58
2025-10-07 20:00:00 | 2.94 | 0 | 0 | 0 | 308.2459 | 2.94 | 2.94
2025-10-07 21:00:00 | 2.76 | 0 | 0 | 0 | 308.2459 | 2.76 | 2.76
2025-10-07 22:00:00 | 2.7 | 0 | 0 | 0 | 308.2459 | 2.7 | 2.7
2025-10-07 23:00:00 | 2.7 | 0 | 0 | 0 | 308.2459 | 2.7 | 2.7
2025-10-08 00:00:00 | 2.94 | 0 | 0 | 0 | 308.2459 | 2.94 | 2.94
2025-10-08 01:00:00 | 2.76 | 0 | 0 | 0 | 308.2459 | 2.76 | 2.76
2025-10-08 02:00:00 | 2.7 | 0 | 0 | 0 | 308.2459 | 2.7 | 2.7
2025-10-08 03:00:00 | 2.76 | 0 | 0 | 0 | 308.2459 | 2.76 | 2.76
2025-10-08 04:00:00 | 2.82 | 0 | 0 | 0 | 308.2459 | 2.82 | 2.82
2025-10-08 05:00:00 | 2.76 | 0 | 0 | 0 | 308.2459 | 2.76 | 2.76
2025-10-08 06:00:00 | 2.52 | 0.29018 | 0 | 0 | 308.2459 | 2.2298 | 2.2298
2025-10-08 07:00:00 | 2.22 | 6.0632 | 0 | 0 | 308.2459 | -3.8432 | -3.8432
2025-10-08 08:00:00 | 1.74 | 11.2392 | 0 | 0 | 308.2459 | -9.4992 | -9.4992
2025-10-08 09:00:00 | 1.56 | 15.4654 | 0 | 0 | 308.2459 | -13.9054 | -13.9054
2025-10-08 10:00:00 | 1.44 | 18.4538 | 0 | 0 | 308.2459 | -17.0138 | -17.0138
2025-10-08 11:00:00 | 1.5 | 20.0006 | 0 | 0 | 308.2459 | -18.5006 | -18.5006
2025-10-08 12:00:00 | 1.5 | 20.0006 | 0 | 0 | 308.2459 | -18.5006 | -18.5006
2025-10-08 13:00:00 | 1.68 | 18.4538 | 0 | 0 | 308.2459 | -16.7738 | -16.7738
2025-10-08 14:00:00 | 1.56 | 15.4654 | 0 | 0 | 308.2459 | -13.9054 | -13.9054
2025-10-08 15:00:00 | 1.38 | 11.2392 | 0 | 0 | 308.2459 | -9.8592 | -9.8592
2025-10-08 16:00:00 | 1.56 | 6.0632 | 0 | 0 | 308.2459 | -4.5032 | -4.5032
2025-10-08 17:00:00 | 1.74 | 0.29018 | 0 | 1.4498 | 306.7961 | -4.885e-15 | 1.4498
2025-10-08 18:00:00 | 1.68 | 0 | 0 | 1.68 | 305.1161 | 0 | 1.68
2025-10-08 19:00:00 | 1.62 | 0 | 0 | 0 | 305.1161 | 1.62 | 1.62
2025-10-08 20:00:00 | 1.8 | 0 | 0 | 0 | 305.1161 | 1.8 | 1.8
2025-10-08 21:00:00 | 1.74 | 0 | 0 | 0 | 305.1161 | 1.74 | 1.74
2025-10-08 22:00:00 | 2.22 | 0 | 0 | 0 | 305.1161 | 2.22 | 2.22
2025-10-08 23:00:00 | 2.28 | 0 | 0 | 0 | 305.1161 | 2.28 | 2.28
2025-10-09 00:00:00 | 2.16 | 0 | 0 | 0 | 305.1161 | 2.16 | 2.16
2025-10-09 01:00:00 | 2.22 | 0 | 0 | 0 | 305.1161 | 2.22 | 2.22
2025-10-09 02:00:00 | 2.4 | 0 | 0 | 0 | 305.1161 | 2.4 | 2.4
2025-10-09 03:00:00 | 2.16 | 0 | 0 | 0 | 305.1161 | 2.16 | 2.16
2025-10-09 04:00:00 | 2.16 | 0 | 0 | 0 | 305.1161 | 2.16 | 2.16
2025-10-09 05:00:00 | 2.22 | 0 | 0 | 0 | 305.1161 | 2.22 | 2.22
2025-10-09 06:00:00 | 2.28 | 0.13938 | 0 | 0 | 305.1161 | 2.1406 | 2.1406
2025-10-09 07:00:00 | 2.1 | 5.9076 | 0 | 0 | 305.1161 | -3.8076 | -3.8076
2025-10-09 08:00:00 | 2.4 | 11.0792 | 0 | 0 | 305.1161 | -8.6792 | -8.6792
2025-10-09 09:00:00 | 2.4 | 15.3018 | 0 | 0 | 305.1161 | -12.9018 | -12.9018
2025-10-09 10:00:00 | 2.64 | 18.2877 | 0 | 0 | 305.1161 | -15.6477 | -15.6477
2025-10-09 11:00:00 | 2.04 | 19.8333 | 0 | 0 | 305.1161 | -17.7933 | -17.7933
2025-10-09 12:00:00 | 1.86 | 19.8333 | 0 | 0 | 305.1161 | -17.9733 | -17.9733
2025-10-09 13:00:00 | 1.8 | 18.2877 | 0 | 0 | 305.1161 | -16.4877 | -16.4877
2025-10-09 14:00:00 | 2.1 | 15.3018 | 0 | 0 | 305.1161 | -13.2018 | -13.2018
2025-10-09 15:00:00 | 1.74 | 11.0792 | 0 | 0 | 305.1161 | -9.3392 | -9.3392
2025-10-09 16:00:00 | 1.92 | 5.9076 | 0 | 0 | 305.1161 | -3.9876 | -3.9876
2025-10-09 17:00:00 | 1.8 | 0.13938 | 0 | 1.6606 | 303.4555 | -4.2188e-15 | 1.6606
2025-10-09 18:00:00 | 1.92 | 0 | 0 | 1.92 | 301.5355 | 9.992e-15 | 1.92
2025-10-09 19:00:00 | 2.22 | 0 | 0 | 0 | 301.5355 | 2.22 | 2.22
2025-10-09 20:00:00 | 2.34 | 0 | 0 | 0 | 301.5355 | 2.34 | 2.34
2025-10-09 21:00:00 | 2.52 | 0 | 0 | 0 | 301.5355 | 2.52 | 2.52
2025-10-09 22:00:00 | 2.52 | 0 | 0 | 0 | 301.5355 | 2.52 | 2.52
2025-10-09 23:00:00 | 2.82 | 0 | 0 | 0 | 301.5355 | 2.82 | 2.82
2025-10-10 00:00:00 | 2.46 | 0 | 0 | 0 | 301.5355 | 2.46 | 2.46
2025-10-10 01:00:00 | 2.52 | 0 | 0 | 0 | 301.5355 | 2.52 | 2.52
2025-10-10 02:00:00 | 2.46 | 0 | 0 | 0 | 301.5355 | 2.46 | 2.46
2025-10-10 03:00:00 | 2.88 | 0 | 0 | 0 | 301.5355 | 2.88 | 2.88
2025-10-10 04:00:00 | 2.4 | 0 | 0 | 0 | 301.5355 | 2.4 | 2.4
2025-10-10 05:00:00 | 2.52 | 0 | 0 | 0 | 301.5355 | 2.52 | 2.52
2025-10-10 06:00:00 | 2.28 | 0 | 0 | 0 | 301.5355 | 2.28 | 2.28
2025-10-10 07:00:00 | 2.28 | 5.7525 | 0 | 0 | 301.5355 | -3.4725 | -3.4725
2025-10-10 08:00:00 | 2.58 | 10.9196 | 0 | 0 | 301.5355 | -8.3396 | -8.3396
2025-10-10 09:00:00 | 2.04 | 15.1385 | 0 | 0 | 301.5355 | -13.0985 | -13.0985
2025-10-10 10:00:00 | 1.8 | 18.1217 | 0 | 0 | 301.5355 | -16.3217 | -16.3217
2025-10-10 11:00:00 | 2.52 | 19.6659 | 0 | 0 | 301.5355 | -17.1459 | -17.1459
2025-10-10 12:00:00 | 3 | 19.6659 | 0 | 0 | 301.5355 | -16.6659 | -16.6659
2025-10-10 13:00:00 | 2.58 | 18.1217 | 0 | 0 | 301.5355 | -15.5417 | -15.5417
2025-10-10 14:00:00 | 2.64 | 15.1385 | 0 | 0 | 301.5355 | -12.4985 | -12.4985
2025-10-10 15:00:00 | 2.52 | 10.9196 | 0 | 0 | 301.5355 | -8.3996 | -8.3996
2025-10-10 16:00:00 | 2.88 | 5.7525 | 0 | 0 | 301.5355 | -2.8725 | -2.8725
2025-10-10 17:00:00 | 1.86 | 0 | 0 | 1.86 | 299.6755 | 0 | 1.86
2025-10-10 18:00:00 | 1.68 | 0 | 0 | 1.68 | 297.9955 | 1.9984e-14 | 1.68
2025-10-10 19:00:00 | 1.62 | 0 | 0 | 0 | 297.9955 | 1.62 | 1.62
2025-10-10 20:00:00 | 1.92 | 0 | 0 | 0 | 297.9955 | 1.92 | 1.92
2025-10-10 21:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-10 22:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-10 23:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-11 00:00:00 | 1.92 | 0 | 0 | 0 | 297.9955 | 1.92 | 1.92
2025-10-11 01:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-11 02:00:00 | 1.62 | 0 | 0 | 0 | 297.9955 | 1.62 | 1.62
2025-10-11 03:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-11 04:00:00 | 1.62 | 0 | 0 | 0 | 297.9955 | 1.62 | 1.62
2025-10-11 05:00:00 | 1.86 | 0 | 0 | 0 | 297.9955 | 1.86 | 1.86
2025-10-11 06:00:00 | 1.62 | 0 | 0 | 0 | 297.9955 | 1.62 | 1.62
2025-10-11 07:00:00 | 1.5 | 5.5982 | 0 | 0 | 297.9955 | -4.0982 | -4.0982
2025-10-11 08:00:00 | 5.7 | 10.7605 | 0 | 0 | 297.9955 | -5.0605 | -5.0605
2025-10-11 09:00:00 | 8.28 | 14.9755 | 0 | 0 | 297.9955 | -6.6955 | -6.6955
2025-10-11 10:00:00 | 8.1 | 17.9559 | 0 | 0 | 297.9955 | -9.8559 | -9.8559
2025-10-11 11:00:00 | 7.98 | 19.4987 | 0 | 0 | 297.9955 | -11.5187 | -11.5187
2025-10-11 12:00:00 | 8.04 | 19.4987 | 0 | 0 | 297.9955 | -11.4587 | -11.4587
2025-10-11 13:00:00 | 2.22 | 17.9559 | 0 | 0 | 297.9955 | -15.7359 | -15.7359
2025-10-11 14:00:00 | 1.62 | 14.9755 | 0 | 0 | 297.9955 | -13.3555 | -13.3555
2025-10-11 15:00:00 | 1.5 | 10.7605 | 0 | 0 | 297.9955 | -9.2605 | -9.2605
2025-10-11 16:00:00 | 1.44 | 5.5982 | 0 | 0 | 297.9955 | -4.1582 | -4.1582
2025-10-11 17:00:00 | 1.62 | 0 | 0 | 0 | 297.9955 | 1.62 | 1.62
2025-10-11 18:00:00 | 1.86 | 0 | 0 | 0 | 297.9955 | 1.86 | 1.86
2025-10-11 19:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-11 20:00:00 | 1.62 | 0 | 0 | 0 | 297.9955 | 1.62 | 1.62
2025-10-11 21:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-11 22:00:00 | 1.92 | 0 | 0 | 0 | 297.9955 | 1.92 | 1.92
2025-10-11 23:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-12 00:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-12 01:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-12 02:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-12 03:00:00 | 1.92 | 0 | 0 | 0 | 297.9955 | 1.92 | 1.92
2025-10-12 04:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-12 05:00:00 | 1.56 | 0 | 0 | 0 | 297.9955 | 1.56 | 1.56
2025-10-12 06:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-12 07:00:00 | 1.74 | 5.4445 | 0 | 0 | 297.9955 | -3.7045 | -3.7045
2025-10-12 08:00:00 | 1.5 | 10.6019 | 0 | 0 | 297.9955 | -9.1019 | -9.1019
2025-10-12 09:00:00 | 2.88 | 14.8128 | 0 | 0 | 297.9955 | -11.9328 | -11.9328
2025-10-12 10:00:00 | 15.96 | 17.7904 | 0 | 0 | 297.9955 | -1.8304 | -1.8304
2025-10-12 11:00:00 | 9.72 | 19.3318 | 0 | 0 | 297.9955 | -9.6118 | -9.6118
2025-10-12 12:00:00 | 1.5 | 19.3318 | 0 | 0 | 297.9955 | -17.8318 | -17.8318
2025-10-12 13:00:00 | 4.68 | 17.7904 | 0 | 0 | 297.9955 | -13.1104 | -13.1104
2025-10-12 14:00:00 | 16.02 | 14.8128 | 0 | 0 | 297.9955 | 1.2072 | 1.2072
2025-10-12 15:00:00 | 16.32 | 10.6019 | 0 | 0 | 297.9955 | 5.7181 | 5.7181
2025-10-12 16:00:00 | 15.96 | 5.4445 | 0 | 0 | 297.9955 | 10.5155 | 10.5155
2025-10-12 17:00:00 | 16.02 | 0 | 0 | 0 | 297.9955 | 16.02 | 16.02
2025-10-12 18:00:00 | 3.12 | 0 | 0 | 0 | 297.9955 | 3.12 | 3.12
2025-10-12 19:00:00 | 1.86 | 0 | 0 | 0 | 297.9955 | 1.86 | 1.86
2025-10-12 20:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-12 21:00:00 | 1.62 | 0 | 0 | 0 | 297.9955 | 1.62 | 1.62
2025-10-12 22:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-12 23:00:00 | 1.92 | 0 | 0 | 0 | 297.9955 | 1.92 | 1.92
2025-10-13 00:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-13 01:00:00 | 1.62 | 0 | 0 | 0 | 297.9955 | 1.62 | 1.62
2025-10-13 02:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-13 03:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-13 04:00:00 | 2.04 | 0 | 0 | 0 | 297.9955 | 2.04 | 2.04
2025-10-13 05:00:00 | 1.62 | 0 | 0 | 0 | 297.9955 | 1.62 | 1.62
2025-10-13 06:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-13 07:00:00 | 1.5 | 5.2917 | 0 | 0 | 297.9955 | -3.7917 | -3.7917
2025-10-13 08:00:00 | 1.74 | 10.4439 | 0 | 0 | 297.9955 | -8.7039 | -8.7039
2025-10-13 09:00:00 | 1.44 | 14.6507 | 0 | 0 | 297.9955 | -13.2107 | -13.2107
2025-10-13 10:00:00 | 1.5 | 17.6253 | 0 | 0 | 297.9955 | -16.1253 | -16.1253
2025-10-13 11:00:00 | 1.5 | 19.1651 | 0 | 0 | 297.9955 | -17.6651 | -17.6651
2025-10-13 12:00:00 | 1.74 | 19.1651 | 0 | 0 | 297.9955 | -17.4251 | -17.4251
2025-10-13 13:00:00 | 1.5 | 17.6253 | 0 | 0 | 297.9955 | -16.1253 | -16.1253
2025-10-13 14:00:00 | 1.5 | 14.6507 | 0 | 0 | 297.9955 | -13.1507 | -13.1507
2025-10-13 15:00:00 | 1.5 | 10.4439 | 0 | 0 | 297.9955 | -8.9439 | -8.9439
2025-10-13 16:00:00 | 1.44 | 5.2917 | 0 | 0 | 297.9955 | -3.8517 | -3.8517
2025-10-13 17:00:00 | 1.92 | 0 | 0 | 0 | 297.9955 | 1.92 | 1.92
2025-10-13 18:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-13 19:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-13 20:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-13 21:00:00 | 1.92 | 0 | 0 | 0 | 297.9955 | 1.92 | 1.92
2025-10-13 22:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-13 23:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-14 00:00:00 | 1.68 | 0 | 0 | 0 | 297.9955 | 1.68 | 1.68
2025-10-14 01:00:00 | 1.92 | 0 | 0 | 0 | 297.9955 | 1.92 | 1.92
2025-10-14 02:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-14 03:00:00 | 1.62 | 0 | 0 | 0 | 297.9955 | 1.62 | 1.62
2025-10-14 04:00:00 | 1.74 | 0 | 0 | 0 | 297.9955 | 1.74 | 1.74
2025-10-14 05:00:00 | 1.86 | 0 | 0 | 0 | 297.9955 | 1.86 | 1.86
2025-10-14 06:00:00 | 1.56 | 0 | 0 | 0 | 297.9955 | 1.56 | 1.56
2025-10-14 07:00:00 | 1.5 | 5.1397 | 0 | 0 | 297.9955 | -3.6397 | -3.6397
2025-10-14 08:00:00 | 1.56 | 10.2866 | 0 | 0 | 297.9955 | -8.7266 | -8.7266
2025-10-14 09:00:00 | 1.8 | 14.489 | 0 | 0 | 297.9955 | -12.689 | -12.689
2025-10-14 10:00:00 | 1.56 | 17.4605 | 0 | 0 | 297.9955 | -15.9005 | -15.9005
2025-10-14 11:00:00 | 1.5 | 18.9987 | 0 | 0 | 297.9955 | -17.4987 | -17.4987
2025-10-14 12:00:00 | 1.5 | 18.9987 | 0 | 0 | 297.9955 | -17.4987 | -17.4987
2025-10-14 13:00:00 | 1.8 | 17.4605 | 0 | 0 | 297.9955 | -15.6605 | -15.6605
2025-10-14 14:00:00 | 1.44 | 14.489 | 0 | 0 | 297.9955 | -13.049 | -13.049
2025-10-14 15:00:00 | 1.56 | 10.2866 | 0 | 0 | 297.9955 | -8.7266 | -8.7266
2025-10-14 16:00:00 | 1.56 | 5.1397 | 0 | 0 | 297.9955 | -3.5797 | -3.5797
2025-10-14 17:00:00 | 1.5 | 0 | 0 | 1.5 | 296.4955 | 0 | 1.5
2025-10-14 18:00:00 | 1.98 | 0 | 0 | 1.98 | 294.5155 | 9.992e-15 | 1.98
2025-10-14 19:00:00 | 1.68 | 0 | 0 | 0 | 294.5155 | 1.68 | 1.68
2025-10-14 20:00:00 | 1.74 | 0 | 0 | 0 | 294.5155 | 1.74 | 1.74
2025-10-14 21:00:00 | 1.68 | 0 | 0 | 0 | 294.5155 | 1.68 | 1.68
2025-10-14 22:00:00 | 1.92 | 0 | 0 | 0 | 294.5155 | 1.92 | 1.92
2025-10-14 23:00:00 | 1.68 | 0 | 0 | 0 | 294.5155 | 1.68 | 1.68
2025-10-15 00:00:00 | 1.74 | 0 | 0 | 0 | 294.5155 | 1.74 | 1.74
2025-10-15 01:00:00 | 1.68 | 0 | 0 | 0 | 294.5155 | 1.68 | 1.68
2025-10-15 02:00:00 | 1.62 | 0 | 0 | 0 | 294.5155 | 1.62 | 1.62
2025-10-15 03:00:00 | 1.98 | 0 | 0 | 0 | 294.5155 | 1.98 | 1.98
2025-10-15 04:00:00 | 1.68 | 0 | 0 | 0 | 294.5155 | 1.68 | 1.68
2025-10-15 05:00:00 | 1.74 | 0 | 0 | 0 | 294.5155 | 1.74 | 1.74
2025-10-15 06:00:00 | 1.62 | 0 | 0 | 0 | 294.5155 | 1.62 | 1.62
2025-10-15 07:00:00 | 1.74 | 4.9886 | 0 | 0 | 294.5155 | -3.2486 | -3.2486
2025-10-15 08:00:00 | 1.62 | 10.13 | 0 | 0 | 294.5155 | -8.51 | -8.51
2025-10-15 09:00:00 | 1.68 | 14.3279 | 0 | 0 | 294.5155 | -12.6479 | -12.6479
2025-10-15 10:00:00 | 1.8 | 17.2963 | 0 | 0 | 294.5155 | -15.4963 | -15.4963
2025-10-15 11:00:00 | 1.86 | 18.8328 | 0 | 0 | 294.5155 | -16.9728 | -16.9728
2025-10-15 12:00:00 | 1.5 | 18.8328 | 0 | 0 | 294.5155 | -17.3328 | -17.3328
2025-10-15 13:00:00 | 1.62 | 17.2963 | 0 | 0 | 294.5155 | -15.6763 | -15.6763
2025-10-15 14:00:00 | 2.76 | 14.3279 | 0 | 0 | 294.5155 | -11.5679 | -11.5679
2025-10-15 15:00:00 | 1.62 | 10.13 | 0 | 0 | 294.5155 | -8.51 | -8.51
2025-10-15 16:00:00 | 1.74 | 4.9886 | 0 | 0 | 294.5155 | -3.2486 | -3.2486
2025-10-15 17:00:00 | 1.74 | 0 | 0 | 1.74 | 292.7755 | 0 | 1.74
2025-10-15 18:00:00 | 1.68 | 0 | 0 | 1.68 | 291.0955 | -5.9952e-14 | 1.68
2025-10-15 19:00:00 | 1.74 | 0 | 0 | 0 | 291.0955 | 1.74 | 1.74
2025-10-15 20:00:00 | 1.92 | 0 | 0 | 0 | 291.0955 | 1.92 | 1.92
2025-10-15 21:00:00 | 1.74 | 0 | 0 | 0 | 291.0955 | 1.74 | 1.74
2025-10-15 22:00:00 | 1.92 | 0 | 0 | 0 | 291.0955 | 1.92 | 1.92
2025-10-15 23:00:00 | 2.46 | 0 | 0 | 0 | 291.0955 | 2.46 | 2.46
2025-10-16 00:00:00 | 2.28 | 0 | 0 | 0 | 291.0955 | 2.28 | 2.28
2025-10-16 01:00:00 | 2.22 | 0 | 0 | 0 | 291.0955 | 2.22 | 2.22
2025-10-16 02:00:00 | 2.16 | 0 | 0 | 0 | 291.0955 | 2.16 | 2.16
2025-10-16 03:00:00 | 2.28 | 0 | 0 | 0 | 291.0955 | 2.28 | 2.28
2025-10-16 04:00:00 | 2.4 | 0 | 0 | 0 | 291.0955 | 2.4 | 2.4
2025-10-16 05:00:00 | 2.28 | 0 | 0 | 0 | 291.0955 | 2.28 | 2.28
2025-10-16 06:00:00 | 2.1 | 0 | 0 | 0 | 291.0955 | 2.1 | 2.1
2025-10-16 07:00:00 | 1.98 | 4.8384 | 0 | 0 | 291.0955 | -2.8584 | -2.8584
2025-10-16 08:00:00 | 2.34 | 9.9741 | 0 | 0 | 291.0955 | -7.6341 | -7.6341
2025-10-16 09:00:00 | 2.04 | 14.1674 | 0 | 0 | 291.0955 | -12.1274 | -12.1274
2025-10-16 10:00:00 | 1.68 | 17.1325 | 0 | 0 | 291.0955 | -15.4525 | -15.4525
2025-10-16 11:00:00 | 1.5 | 18.6674 | 0 | 0 | 291.0955 | -17.1674 | -17.1674
2025-10-16 12:00:00 | 1.86 | 18.6674 | 0 | 0 | 291.0955 | -16.8074 | -16.8074
2025-10-16 13:00:00 | 1.5 | 17.1325 | 0 | 0 | 291.0955 | -15.6325 | -15.6325
2025-10-16 14:00:00 | 1.62 | 14.1674 | 0 | 0 | 291.0955 | -12.5474 | -12.5474
2025-10-16 15:00:00 | 1.5 | 9.9741 | 0 | 0 | 291.0955 | -8.4741 | -8.4741
2025-10-16 16:00:00 | 1.86 | 4.8384 | 0 | 0 | 291.0955 | -2.9784 | -2.9784
2025-10-16 17:00:00 | 1.56 | 0 | 0 | 1.56 | 289.5355 | 0 | 1.56
2025-10-16 18:00:00 | 1.74 | 0 | 0 | 1.74 | 287.7955 | -9.992e-15 | 1.74
2025-10-16 19:00:00 | 1.68 | 0 | 0 | 0 | 287.7955 | 1.68 | 1.68
2025-10-16 20:00:00 | 1.98 | 0 | 0 | 0 | 287.7955 | 1.98 | 1.98
2025-10-16 21:00:00 | 1.68 | 0 | 0 | 0 | 287.7955 | 1.68 | 1.68
2025-10-16 22:00:00 | 1.74 | 0 | 0 | 0 | 287.7955 | 1.74 | 1.74
2025-10-16 23:00:00 | 1.68 | 0 | 0 | 0 | 287.7955 | 1.68 | 1.68
2025-10-17 00:00:00 | 2.04 | 0 | 0 | 0 | 287.7955 | 2.04 | 2.04
2025-10-17 01:00:00 | 2.28 | 0 | 0 | 0 | 287.7955 | 2.28 | 2.28
2025-10-17 02:00:00 | 2.22 | 0 | 0 | 0 | 287.7955 | 2.22 | 2.22
2025-10-17 03:00:00 | 2.22 | 0 | 0 | 0 | 287.7955 | 2.22 | 2.22
2025-10-17 04:00:00 | 2.46 | 0 | 0 | 0 | 287.7955 | 2.46 | 2.46
2025-10-17 05:00:00 | 2.22 | 0 | 0 | 0 | 287.7955 | 2.22 | 2.22
2025-10-17 06:00:00 | 2.16 | 0 | 0 | 0 | 287.7955 | 2.16 | 2.16
2025-10-17 07:00:00 | 2.28 | 4.6893 | 0 | 0 | 287.7955 | -2.4093 | -2.4093
2025-10-17 08:00:00 | 2.16 | 9.8192 | 0 | 0 | 287.7955 | -7.6592 | -7.6592
2025-10-17 09:00:00 | 1.98 | 14.0077 | 0 | 0 | 287.7955 | -12.0277 | -12.0277
2025-10-17 10:00:00 | 1.5 | 16.9694 | 0 | 0 | 287.7955 | -15.4694 | -15.4694
2025-10-17 11:00:00 | 1.86 | 18.5025 | 0 | 0 | 287.7955 | -16.6425 | -16.6425
2025-10-17 12:00:00 | 1.56 | 18.5025 | 0 | 0 | 287.7955 | -16.9425 | -16.9425
2025-10-17 13:00:00 | 1.56 | 16.9694 | 0 | 0 | 287.7955 | -15.4094 | -15.4094
2025-10-17 14:00:00 | 13.5 | 14.0077 | 0 | 0 | 287.7955 | -0.5077 | -0.5077
2025-10-17 15:00:00 | 16.38 | 9.8192 | 0 | 6.5608 | 281.2347 | -2.6645e-15 | 6.5608
2025-10-17 16:00:00 | 16.08 | 4.6893 | 0 | 11.3907 | 269.844 | 4.4409e-14 | 11.3907
2025-10-17 17:00:00 | 9.6 | 0 | 0 | 9.6 | 260.244 | 8.8818e-15 | 9.6
2025-10-17 18:00:00 | 1.8 | 0 | 0 | 1.8 | 258.444 | 1.9984e-14 | 1.8
2025-10-17 19:00:00 | 1.86 | 0 | 0 | 0 | 258.444 | 1.86 | 1.86
2025-10-17 20:00:00 | 1.8 | 0 | 0 | 0 | 258.444 | 1.8 | 1.8
2025-10-17 21:00:00 | 1.68 | 0 | 0 | 0 | 258.444 | 1.68 | 1.68
2025-10-17 22:00:00 | 1.74 | 0 | 0 | 0 | 258.444 | 1.74 | 1.74
2025-10-17 23:00:00 | 3.24 | 0 | 0 | 0 | 258.444 | 3.24 | 3.24
2025-10-18 00:00:00 | 8.28 | 0 | 0 | 0 | 258.444 | 8.28 | 8.28
2025-10-18 01:00:00 | 8.22 | 0 | 0 | 0 | 258.444 | 8.22 | 8.22
2025-10-18 02:00:00 | 8.34 | 0 | 0 | 0 | 258.444 | 8.34 | 8.34
2025-10-18 03:00:00 | 8.46 | 0 | 0 | 0 | 258.444 | 8.46 | 8.46
2025-10-18 04:00:00 | 8.28 | 0 | 0 | 0 | 258.444 | 8.28 | 8.28
2025-10-18 05:00:00 | 8.22 | 0 | 0 | 0 | 258.444 | 8.22 | 8.22
2025-10-18 06:00:00 | 8.28 | 0 | 0 | 0 | 258.444 | 8.28 | 8.28
2025-10-18 07:00:00 | 8.34 | 4.5413 | 0 | 0 | 258.444 | 3.7987 | 3.7987
2025-10-18 08:00:00 | 8.16 | 9.6651 | 0 | 0 | 258.444 | -1.5051 | -1.5051
2025-10-18 09:00:00 | 2.46 | 13.8488 | 0 | 0 | 258.444 | -11.3888 | -11.3888
2025-10-18 10:00:00 | 1.62 | 16.807 | 0 | 0 | 258.444 | -15.187 | -15.187
2025-10-18 11:00:00 | 1.74 | 18.3383 | 0 | 0 | 258.444 | -16.5983 | -16.5983
2025-10-18 12:00:00 | 1.62 | 18.3383 | 0 | 0 | 258.444 | -16.7183 | -16.7183
2025-10-18 13:00:00 | 1.5 | 16.807 | 0 | 0 | 258.444 | -15.307 | -15.307
2025-10-18 14:00:00 | 1.56 | 13.8488 | 0 | 0 | 258.444 | -12.2888 | -12.2888
2025-10-18 15:00:00 | 1.74 | 9.6651 | 0 | 0 | 258.444 | -7.9251 | -7.9251
2025-10-18 16:00:00 | 1.5 | 4.5413 | 0 | 0 | 258.444 | -3.0413 | -3.0413
2025-10-18 17:00:00 | 1.62 | 0 | 0 | 0 | 258.444 | 1.62 | 1.62
2025-10-18 18:00:00 | 1.92 | 0 | 0 | 0 | 258.444 | 1.92 | 1.92
2025-10-18 19:00:00 | 1.62 | 0 | 0 | 0 | 258.444 | 1.62 | 1.62
2025-10-18 20:00:00 | 1.8 | 0 | 0 | 0 | 258.444 | 1.8 | 1.8
2025-10-18 21:00:00 | 1.68 | 0 | 0 | 0 | 258.444 | 1.68 | 1.68
2025-10-18 22:00:00 | 1.86 | 0 | 0 | 0 | 258.444 | 1.86 | 1.86
2025-10-18 23:00:00 | 1.8 | 0 | 0 | 0 | 258.444 | 1.8 | 1.8
2025-10-19 00:00:00 | 1.74 | 0 | 0 | 0 | 258.444 | 1.74 | 1.74
2025-10-19 01:00:00 | 1.86 | 0 | 0 | 0 | 258.444 | 1.86 | 1.86
2025-10-19 02:00:00 | 1.68 | 0 | 0 | 0 | 258.444 | 1.68 | 1.68
2025-10-19 03:00:00 | 1.74 | 0 | 0 | 0 | 258.444 | 1.74 | 1.74
2025-10-19 04:00:00 | 1.8 | 0 | 0 | 0 | 258.444 | 1.8 | 1.8
2025-10-19 05:00:00 | 1.74 | 0 | 0 | 0 | 258.444 | 1.74 | 1.74
2025-10-19 06:00:00 | 1.62 | 0 | 0 | 0 | 258.444 | 1.62 | 1.62
2025-10-19 07:00:00 | 1.74 | 4.3943 | 0 | 0 | 258.444 | -2.6543 | -2.6543
2025-10-19 08:00:00 | 1.44 | 9.5121 | 0 | 0 | 258.444 | -8.0721 | -8.0721
2025-10-19 09:00:00 | 8.58 | 13.6907 | 0 | 0 | 258.444 | -5.1107 | -5.1107
2025-10-19 10:00:00 | 1.68 | 16.6454 | 0 | 0 | 258.444 | -14.9654 | -14.9654
2025-10-19 11:00:00 | 1.5 | 18.1749 | 0 | 0 | 258.444 | -16.6749 | -16.6749
2025-10-19 12:00:00 | 1.56 | 18.1749 | 0 | 0 | 258.444 | -16.6149 | -16.6149
2025-10-19 13:00:00 | 1.74 | 16.6454 | 0 | 0 | 258.444 | -14.9054 | -14.9054
2025-10-19 14:00:00 | 1.56 | 13.6907 | 0 | 0 | 258.444 | -12.1307 | -12.1307
2025-10-19 15:00:00 | 1.56 | 9.5121 | 0 | 0 | 258.444 | -7.9521 | -7.9521
2025-10-19 16:00:00 | 1.68 | 4.3943 | 0 | 0 | 258.444 | -2.7143 | -2.7143
2025-10-19 17:00:00 | 1.62 | 0 | 0 | 0 | 258.444 | 1.62 | 1.62
2025-10-19 18:00:00 | 1.8 | 0 | 0 | 0 | 258.444 | 1.8 | 1.8
2025-10-19 19:00:00 | 1.86 | 0 | 0 | 0 | 258.444 | 1.86 | 1.86
2025-10-19 20:00:00 | 1.74 | 0 | 0 | 0 | 258.444 | 1.74 | 1.74
2025-10-19 21:00:00 | 1.68 | 0 | 0 | 0 | 258.444 | 1.68 | 1.68
2025-10-19 22:00:00 | 5.82 | 0 | 0 | 0 | 258.444 | 5.82 | 5.82
2025-10-19 23:00:00 | 8.22 | 0 | 0 | 0 | 258.444 | 8.22 | 8.22
2025-10-20 00:00:00 | 8.28 | 0 | 0 | 0 | 258.444 | 8.28 | 8.28
2025-10-20 01:00:00 | 8.4 | 0 | 0 | 0 | 258.444 | 8.4 | 8.4
2025-10-20 02:00:00 | 8.22 | 0 | 0 | 0 | 258.444 | 8.22 | 8.22
2025-10-20 03:00:00 | 8.16 | 0 | 0 | 0 | 258.444 | 8.16 | 8.16
2025-10-20 04:00:00 | 8.46 | 0 | 0 | 0 | 258.444 | 8.46 | 8.46
2025-10-20 05:00:00 | 8.22 | 0 | 0 | 0 | 258.444 | 8.22 | 8.22
2025-10-20 06:00:00 | 8.22 | 0 | 0 | 0 | 258.444 | 8.22 | 8.22
2025-10-20 07:00:00 | 8.22 | 4.2486 | 0 | 3.9714 | 254.4725 | 8.8818e-16 | 3.9714
2025-10-20 08:00:00 | 8.1 | 9.36 | 0 | 0 | 254.4725 | -1.26 | -1.26
2025-10-20 09:00:00 | 8.04 | 13.5335 | 0 | 0 | 254.4725 | -5.4935 | -5.4935
2025-10-20 10:00:00 | 4.26 | 16.4846 | 0 | 0 | 254.4725 | -12.2246 | -12.2246
2025-10-20 11:00:00 | 1.5 | 18.0122 | 0 | 0 | 254.4725 | -16.5122 | -16.5122
2025-10-20 12:00:00 | 1.62 | 18.0122 | 0 | 0 | 254.4725 | -16.3922 | -16.3922
2025-10-20 13:00:00 | 1.62 | 16.4846 | 0 | 0 | 254.4725 | -14.8646 | -14.8646
2025-10-20 14:00:00 | 1.5 | 13.5335 | 0 | 0 | 254.4725 | -12.0335 | -12.0335
2025-10-20 15:00:00 | 1.5 | 9.36 | 0 | 0 | 254.4725 | -7.86 | -7.86
2025-10-20 16:00:00 | 1.74 | 4.2486 | 0 | 0 | 254.4725 | -2.5086 | -2.5086
2025-10-20 17:00:00 | 1.62 | 0 | 0 | 1.62 | 252.8525 | 0 | 1.62
2025-10-20 18:00:00 | 1.74 | 0 | 0 | 1.74 | 251.1125 | -9.992e-15 | 1.74
2025-10-20 19:00:00 | 1.68 | 0 | 0 | 0 | 251.1125 | 1.68 | 1.68
2025-10-20 20:00:00 | 1.86 | 0 | 0 | 0 | 251.1125 | 1.86 | 1.86
2025-10-20 21:00:00 | 1.86 | 0 | 0 | 0 | 251.1125 | 1.86 | 1.86
2025-10-20 22:00:00 | 2.28 | 0 | 0 | 0 | 251.1125 | 2.28 | 2.28
2025-10-20 23:00:00 | 2.28 | 0 | 0 | 0 | 251.1125 | 2.28 | 2.28
2025-10-21 00:00:00 | 2.34 | 0 | 0 | 0 | 251.1125 | 2.34 | 2.34
2025-10-21 01:00:00 | 2.1 | 0 | 0 | 0 | 251.1125 | 2.1 | 2.1
2025-10-21 02:00:00 | 2.46 | 0 | 0 | 0 | 251.1125 | 2.46 | 2.46
2025-10-21 03:00:00 | 2.16 | 0 | 0 | 0 | 251.1125 | 2.16 | 2.16
2025-10-21 04:00:00 | 2.28 | 0 | 0 | 0 | 251.1125 | 2.28 | 2.28
2025-10-21 05:00:00 | 2.46 | 0 | 0 | 0 | 251.1125 | 2.46 | 2.46
2025-10-21 06:00:00 | 2.16 | 0 | 0 | 0 | 251.1125 | 2.16 | 2.16
2025-10-21 07:00:00 | 2.7 | 4.104 | 0 | 0 | 251.1125 | -1.404 | -1.404
2025-10-21 08:00:00 | 4.2 | 9.2091 | 0 | 0 | 251.1125 | -5.0091 | -5.0091
2025-10-21 09:00:00 | 3.3 | 13.3773 | 0 | 0 | 251.1125 | -10.0773 | -10.0773
2025-10-21 10:00:00 | 3 | 16.3247 | 0 | 0 | 251.1125 | -13.3247 | -13.3247
2025-10-21 11:00:00 | 2.88 | 17.8504 | 0 | 0 | 251.1125 | -14.9704 | -14.9704
2025-10-21 12:00:00 | 2.76 | 17.8504 | 0 | 0 | 251.1125 | -15.0904 | -15.0904
2025-10-21 13:00:00 | 3.06 | 16.3247 | 0 | 0 | 251.1125 | -13.2647 | -13.2647
2025-10-21 14:00:00 | 2.82 | 13.3773 | 0 | 0 | 251.1125 | -10.5573 | -10.5573
2025-10-21 15:00:00 | 2.82 | 9.2091 | 0 | 0 | 251.1125 | -6.3891 | -6.3891
2025-10-21 16:00:00 | 3 | 4.104 | 0 | 0 | 251.1125 | -1.104 | -1.104
2025-10-21 17:00:00 | 2.94 | 0 | 0 | 2.94 | 248.1725 | 0 | 2.94
2025-10-21 18:00:00 | 3 | 0 | 0 | 3 | 245.1725 | 0 | 3
2025-10-21 19:00:00 | 3.18 | 0 | 0 | 0 | 245.1725 | 3.18 | 3.18
2025-10-21 20:00:00 | 3 | 0 | 0 | 0 | 245.1725 | 3 | 3
2025-10-21 21:00:00 | 3 | 0 | 0 | 0 | 245.1725 | 3 | 3
2025-10-21 22:00:00 | 3.18 | 0 | 0 | 0 | 245.1725 | 3.18 | 3.18
2025-10-21 23:00:00 | 3 | 0 | 0 | 0 | 245.1725 | 3 | 3
2025-10-22 00:00:00 | 2.82 | 0 | 0 | 0 | 245.1725 | 2.82 | 2.82
2025-10-22 01:00:00 | 3.06 | 0 | 0 | 0 | 245.1725 | 3.06 | 3.06
2025-10-22 02:00:00 | 3.06 | 0 | 0 | 0 | 245.1725 | 3.06 | 3.06
2025-10-22 03:00:00 | 3.06 | 0 | 0 | 0 | 245.1725 | 3.06 | 3.06
2025-10-22 04:00:00 | 3.24 | 0 | 0 | 0 | 245.1725 | 3.24 | 3.24
2025-10-22 05:00:00 | 11.28 | 0 | 0 | 0 | 245.1725 | 11.28 | 11.28
2025-10-22 06:00:00 | 10.26 | 0 | 0 | 0 | 245.1725 | 10.26 | 10.26
2025-10-22 07:00:00 | 3.3 | 3.9608 | 0 | 0 | 245.1725 | -0.66077 | -0.66077
2025-10-22 08:00:00 | 3.6 | 9.0593 | 0 | 0 | 245.1725 | -5.4593 | -5.4593
2025-10-22 09:00:00 | 3.3 | 13.2222 | 0 | 0 | 245.1725 | -9.9222 | -9.9222
2025-10-22 10:00:00 | 3.36 | 16.1658 | 0 | 0 | 245.1725 | -12.8058 | -12.8058
2025-10-22 11:00:00 | 3.72 | 17.6895 | 0 | 0 | 245.1725 | -13.9695 | -13.9695
2025-10-22 12:00:00 | 3.42 | 17.6895 | 0 | 0 | 245.1725 | -14.2695 | -14.2695
2025-10-22 13:00:00 | 3.42 | 16.1658 | 0 | 0 | 245.1725 | -12.7458 | -12.7458
2025-10-22 14:00:00 | 3.54 | 13.2222 | 0 | 0 | 245.1725 | -9.6822 | -9.6822
2025-10-22 15:00:00 | 3.42 | 9.0593 | 0 | 0 | 245.1725 | -5.6393 | -5.6393
2025-10-22 16:00:00 | 3.3 | 3.9608 | 0 | 0 | 245.1725 | -0.66077 | -0.66077
2025-10-22 17:00:00 | 3.48 | 0 | 0 | 3.48 | 241.6925 | 0 | 3.48
2025-10-22 18:00:00 | 3.72 | 0 | 0 | 3.72 | 237.9725 | 3.0198e-14 | 3.72
2025-10-22 19:00:00 | 3.6 | 0 | 0 | 0 | 237.9725 | 3.6 | 3.6
2025-10-22 20:00:00 | 3.48 | 0 | 0 | 0 | 237.9725 | 3.48 | 3.48
2025-10-22 21:00:00 | 3.78 | 0 | 0 | 0 | 237.9725 | 3.78 | 3.78
2025-10-22 22:00:00 | 10.8 | 0 | 0 | 0 | 237.9725 | 10.8 | 10.8
2025-10-22 23:00:00 | 18.18 | 0 | 0 | 0 | 237.9725 | 18.18 | 18.18
2025-10-23 00:00:00 | 18.24 | 0 | 0 | 0 | 237.9725 | 18.24 | 18.24
2025-10-23 01:00:00 | 18.12 | 0 | 0 | 0 | 237.9725 | 18.12 | 18.12
2025-10-23 02:00:00 | 18.06 | 0 | 0 | 0 | 237.9725 | 18.06 | 18.06
2025-10-23 03:00:00 | 18.36 | 0 | 0 | 0 | 237.9725 | 18.36 | 18.36
2025-10-23 04:00:00 | 18.12 | 0 | 0 | 0 | 237.9725 | 18.12 | 18.12
2025-10-23 05:00:00 | 17.88 | 0 | 0 | 0 | 237.9725 | 17.88 | 17.88
2025-10-23 06:00:00 | 17.88 | 0 | 0 | 0 | 237.9725 | 17.88 | 17.88
2025-10-23 07:00:00 | 16.8 | 3.8189 | 0 | 12.9811 | 224.9914 | -3.0198e-14 | 12.9811
2025-10-23 08:00:00 | 16.32 | 8.9107 | 0 | 7.4093 | 217.5821 | 1.5099e-14 | 7.4093
2025-10-23 09:00:00 | 6.36 | 13.0682 | 0 | 0 | 217.5821 | -6.7082 | -6.7082
2025-10-23 10:00:00 | 2.46 | 16.008 | 0 | 0 | 217.5821 | -13.548 | -13.548
2025-10-23 11:00:00 | 2.28 | 17.5297 | 0 | 0 | 217.5821 | -15.2497 | -15.2497
2025-10-23 12:00:00 | 1.92 | 17.5297 | 0 | 0 | 217.5821 | -15.6097 | -15.6097
2025-10-23 13:00:00 | 1.86 | 16.008 | 0 | 0 | 217.5821 | -14.148 | -14.148
2025-10-23 14:00:00 | 1.56 | 13.0682 | 0 | 0 | 217.5821 | -11.5082 | -11.5082
2025-10-23 15:00:00 | 1.56 | 8.9107 | 0 | 0 | 217.5821 | -7.3507 | -7.3507
2025-10-23 16:00:00 | 1.86 | 3.8189 | 0 | 0 | 217.5821 | -1.9589 | -1.9589
2025-10-23 17:00:00 | 1.68 | 0 | 0 | 1.68 | 215.9021 | 0 | 1.68
2025-10-23 18:00:00 | 1.8 | 0 | 0 | 1.8 | 214.1021 | 1.9984e-14 | 1.8
2025-10-23 19:00:00 | 1.92 | 0 | 0 | 0 | 214.1021 | 1.92 | 1.92
2025-10-23 20:00:00 | 1.86 | 0 | 0 | 0 | 214.1021 | 1.86 | 1.86
2025-10-23 21:00:00 | 2.28 | 0 | 0 | 0 | 214.1021 | 2.28 | 2.28
2025-10-23 22:00:00 | 2.28 | 0 | 0 | 0 | 214.1021 | 2.28 | 2.28
2025-10-23 23:00:00 | 2.52 | 0 | 0 | 0 | 214.1021 | 2.52 | 2.52
2025-10-24 00:00:00 | 2.28 | 0 | 0 | 0 | 214.1021 | 2.28 | 2.28
2025-10-24 01:00:00 | 2.34 | 0 | 0 | 0 | 214.1021 | 2.34 | 2.34
2025-10-24 02:00:00 | 2.46 | 0 | 0 | 0 | 214.1021 | 2.46 | 2.46
2025-10-24 03:00:00 | 2.34 | 0 | 0 | 0 | 214.1021 | 2.34 | 2.34
2025-10-24 04:00:00 | 2.28 | 0 | 0 | 0 | 214.1021 | 2.28 | 2.28
2025-10-24 05:00:00 | 2.52 | 0 | 0 | 0 | 214.1021 | 2.52 | 2.52
2025-10-24 06:00:00 | 9.96 | 0 | 0 | 0 | 214.1021 | 9.96 | 9.96
2025-10-24 07:00:00 | 17.16 | 3.6783 | 0 | 13.4817 | 200.6204 | 3.5527e-14 | 13.4817
2025-10-24 08:00:00 | 17.1 | 8.7634 | 0 | 8.3366 | 192.2838 | 3.5527e-15 | 8.3366
2025-10-24 09:00:00 | 16.8 | 12.9154 | 0 | 3.8846 | 188.3992 | -3.1086e-15 | 3.8846
2025-10-24 10:00:00 | 17.22 | 15.8512 | 0 | 1.3688 | 187.0304 | -6.6613e-16 | 1.3688
2025-10-24 11:00:00 | 17.64 | 17.371 | 0 | 0.26903 | 186.7614 | -2.7756e-16 | 0.26903
2025-10-24 12:00:00 | 16.8 | 17.371 | 0 | 0 | 186.7614 | -0.57097 | -0.57097
2025-10-24 13:00:00 | 16.68 | 15.8512 | 0 | 0.82876 | 185.9326 | 5.107e-15 | 0.82876
2025-10-24 14:00:00 | 5.46 | 12.9154 | 0 | 0 | 185.9326 | -7.4554 | -7.4554
2025-10-24 15:00:00 | 2.28 | 8.7634 | 0 | 0 | 185.9326 | -6.4834 | -6.4834
2025-10-24 16:00:00 | 2.1 | 3.6783 | 0 | 0 | 185.9326 | -1.5783 | -1.5783
2025-10-24 17:00:00 | 2.22 | 0 | 0 | 2.22 | 183.7126 | 0 | 2.22
2025-10-24 18:00:00 | 2.4 | 0 | 0 | 2.4 | 181.3126 | -1.0214e-14 | 2.4
2025-10-24 19:00:00 | 2.28 | 0 | 0 | 0 | 181.3126 | 2.28 | 2.28
2025-10-24 20:00:00 | 2.22 | 0 | 0 | 0 | 181.3126 | 2.22 | 2.22
2025-10-24 21:00:00 | 2.22 | 0 | 0 | 0 | 181.3126 | 2.22 | 2.22
2025-10-24 22:00:00 | 2.52 | 0 | 0 | 0 | 181.3126 | 2.52 | 2.52
2025-10-24 23:00:00 | 2.16 | 0 | 0 | 0 | 181.3126 | 2.16 | 2.16
2025-10-25 00:00:00 | 2.22 | 0 | 0 | 0 | 181.3126 | 2.22 | 2.22
2025-10-25 01:00:00 | 2.46 | 0 | 0 | 0 | 181.3126 | 2.46 | 2.46
2025-10-25 02:00:00 | 2.34 | 0 | 0 | 0 | 181.3126 | 2.34 | 2.34
2025-10-25 03:00:00 | 2.16 | 0 | 0 | 0 | 181.3126 | 2.16 | 2.16
2025-10-25 04:00:00 | 2.34 | 0 | 0 | 0 | 181.3126 | 2.34 | 2.34
2025-10-25 05:00:00 | 2.46 | 0 | 0 | 0 | 181.3126 | 2.46 | 2.46
2025-10-25 06:00:00 | 2.22 | 0 | 0 | 0 | 181.3126 | 2.22 | 2.22
2025-10-25 07:00:00 | 2.16 | 3.5392 | 0 | 0 | 181.3126 | -1.3792 | -1.3792
2025-10-25 08:00:00 | 2.28 | 8.6175 | 0 | 0 | 181.3126 | -6.3375 | -6.3375
2025-10-25 09:00:00 | 2.16 | 12.7638 | 0 | 0 | 181.3126 | -10.6038 | -10.6038
2025-10-25 10:00:00 | 2.1 | 15.6957 | 0 | 0 | 181.3126 | -13.5957 | -13.5957
2025-10-25 11:00:00 | 2.4 | 17.2134 | 0 | 0 | 181.3126 | -14.8134 | -14.8134
2025-10-25 12:00:00 | 1.68 | 17.2134 | 0 | 0 | 181.3126 | -15.5334 | -15.5334
2025-10-25 13:00:00 | 1.56 | 15.6957 | 0 | 0 | 181.3126 | -14.1357 | -14.1357
2025-10-25 14:00:00 | 1.56 | 12.7638 | 0 | 0 | 181.3126 | -11.2038 | -11.2038
2025-10-25 15:00:00 | 1.8 | 8.6175 | 0 | 0 | 181.3126 | -6.8175 | -6.8175
2025-10-25 16:00:00 | 1.56 | 3.5392 | 0 | 0 | 181.3126 | -1.9792 | -1.9792
2025-10-25 17:00:00 | 1.62 | 0 | 0 | 0 | 181.3126 | 1.62 | 1.62
2025-10-25 18:00:00 | 1.98 | 0 | 0 | 0 | 181.3126 | 1.98 | 1.98
2025-10-25 19:00:00 | 1.86 | 0 | 0 | 0 | 181.3126 | 1.86 | 1.86
2025-10-25 20:00:00 | 2.28 | 0 | 0 | 0 | 181.3126 | 2.28 | 2.28
2025-10-25 21:00:00 | 2.22 | 0 | 0 | 0 | 181.3126 | 2.22 | 2.22
2025-10-25 22:00:00 | 2.46 | 0 | 0 | 0 | 181.3126 | 2.46 | 2.46
2025-10-25 23:00:00 | 2.28 | 0 | 0 | 0 | 181.3126 | 2.28 | 2.28
2025-10-26 00:00:00 | 2.22 | 0 | 0 | 0 | 181.3126 | 2.22 | 2.22
2025-10-26 01:00:00 | 2.46 | 0 | 0 | 0 | 181.3126 | 2.46 | 2.46
2025-10-26 02:00:00 | 2.28 | 0 | 0 | 0 | 181.3126 | 2.28 | 2.28
2025-10-26 03:00:00 | 2.28 | 0 | 0 | 0 | 181.3126 | 2.28 | 2.28
2025-10-26 04:00:00 | 2.4 | 0 | 0 | 0 | 181.3126 | 2.4 | 2.4
2025-10-26 05:00:00 | 2.34 | 0 | 0 | 0 | 181.3126 | 2.34 | 2.34
2025-10-26 06:00:00 | 2.28 | 0 | 0 | 0 | 181.3126 | 2.28 | 2.28
2025-10-26 07:00:00 | 2.04 | 3.4016 | 0 | 0 | 181.3126 | -1.3616 | -1.3616
2025-10-26 08:00:00 | 2.34 | 8.4729 | 0 | 0 | 181.3126 | -6.1329 | -6.1329
2025-10-26 09:00:00 | 2.16 | 12.6136 | 0 | 0 | 181.3126 | -10.4536 | -10.4536
2025-10-26 10:00:00 | 9.6 | 15.5415 | 0 | 0 | 181.3126 | -5.9415 | -5.9415
2025-10-26 11:00:00 | 11.94 | 17.057 | 0 | 0 | 181.3126 | -5.117 | -5.117
2025-10-26 12:00:00 | 11.58 | 17.057 | 0 | 0 | 181.3126 | -5.477 | -5.477
2025-10-26 13:00:00 | 11.7 | 15.5415 | 0 | 0 | 181.3126 | -3.8415 | -3.8415
2025-10-26 14:00:00 | 11.88 | 12.6136 | 0 | 0 | 181.3126 | -0.73356 | -0.73356
2025-10-26 15:00:00 | 11.7 | 8.4729 | 0 | 0 | 181.3126 | 3.2271 | 3.2271
2025-10-26 16:00:00 | 9.9 | 3.4016 | 0 | 0 | 181.3126 | 6.4984 | 6.4984
2025-10-26 17:00:00 | 2.1 | 0 | 0 | 0 | 181.3126 | 2.1 | 2.1
2025-10-26 18:00:00 | 2.4 | 0 | 0 | 0 | 181.3126 | 2.4 | 2.4
2025-10-26 19:00:00 | 2.28 | 0 | 0 | 0 | 181.3126 | 2.28 | 2.28
2025-10-26 20:00:00 | 2.28 | 0 | 0 | 0 | 181.3126 | 2.28 | 2.28
2025-10-26 21:00:00 | 2.16 | 0 | 0 | 0 | 181.3126 | 2.16 | 2.16
2025-10-26 22:00:00 | 2.58 | 0 | 0 | 0 | 181.3126 | 2.58 | 2.58
2025-10-26 23:00:00 | 2.22 | 0 | 0 | 0 | 181.3126 | 2.22 | 2.22
2025-10-27 00:00:00 | 2.34 | 0 | 0 | 0 | 181.3126 | 2.34 | 2.34
2025-10-27 01:00:00 | 2.46 | 0 | 0 | 0 | 181.3126 | 2.46 | 2.46
2025-10-27 02:00:00 | 2.34 | 0 | 0 | 0 | 181.3126 | 2.34 | 2.34
2025-10-27 03:00:00 | 2.22 | 0 | 0 | 0 | 181.3126 | 2.22 | 2.22
2025-10-27 04:00:00 | 2.28 | 0 | 0 | 0 | 181.3126 | 2.28 | 2.28
2025-10-27 05:00:00 | 2.58 | 0 | 0 | 0 | 181.3126 | 2.58 | 2.58
2025-10-27 06:00:00 | 2.16 | 0 | 0 | 0 | 181.3126 | 2.16 | 2.16
2025-10-27 07:00:00 | 2.1 | 3.2655 | 0 | 0 | 181.3126 | -1.1655 | -1.1655
2025-10-27 08:00:00 | 2.34 | 8.3298 | 0 | 0 | 181.3126 | -5.9898 | -5.9898
2025-10-27 09:00:00 | 2.1 | 12.4647 | 0 | 0 | 181.3126 | -10.3647 | -10.3647
2025-10-27 10:00:00 | 6.42 | 15.3885 | 0 | 0 | 181.3126 | -8.9685 | -8.9685
2025-10-27 11:00:00 | 3.18 | 16.902 | 0 | 0 | 181.3126 | -13.722 | -13.722
2025-10-27 12:00:00 | 2.4 | 16.902 | 0 | 0 | 181.3126 | -14.502 | -14.502
2025-10-27 13:00:00 | 4.56 | 15.3885 | 0 | 0 | 181.3126 | -10.8285 | -10.8285
2025-10-27 14:00:00 | 8.7 | 12.4647 | 0 | 0 | 181.3126 | -3.7647 | -3.7647
2025-10-27 15:00:00 | 9.06 | 8.3298 | 0 | 0.73022 | 180.5824 | -3.3307e-16 | 0.73022
2025-10-27 16:00:00 | 7.86 | 3.2655 | 0 | 4.5945 | 175.988 | 0 | 4.5945
2025-10-27 17:00:00 | 2.58 | 0 | 0 | 2.58 | 173.408 | 0 | 2.58
2025-10-27 18:00:00 | 2.52 | 0 | 0 | 2.52 | 170.888 | 0 | 2.52
2025-10-27 19:00:00 | 2.82 | 0 | 0 | 0 | 170.888 | 2.82 | 2.82
2025-10-27 20:00:00 | 2.52 | 0 | 0 | 0 | 170.888 | 2.52 | 2.52
2025-10-27 21:00:00 | 2.58 | 0 | 0 | 0 | 170.888 | 2.58 | 2.58
2025-10-27 22:00:00 | 2.76 | 0 | 0 | 0 | 170.888 | 2.76 | 2.76
2025-10-27 23:00:00 | 2.58 | 0 | 0 | 0 | 170.888 | 2.58 | 2.58
2025-10-28 00:00:00 | 2.52 | 0 | 0 | 0 | 170.888 | 2.52 | 2.52
2025-10-28 01:00:00 | 2.58 | 0 | 0 | 0 | 170.888 | 2.58 | 2.58
2025-10-28 02:00:00 | 2.82 | 0 | 0 | 0 | 170.888 | 2.82 | 2.82
2025-10-28 03:00:00 | 2.52 | 0 | 0 | 0 | 170.888 | 2.52 | 2.52
2025-10-28 04:00:00 | 2.58 | 0 | 0 | 0 | 170.888 | 2.58 | 2.58
2025-10-28 05:00:00 | 2.76 | 0 | 0 | 0 | 170.888 | 2.76 | 2.76
2025-10-28 06:00:00 | 2.52 | 0 | 0 | 0 | 170.888 | 2.52 | 2.52
2025-10-28 07:00:00 | 2.34 | 3.1311 | 0 | 0 | 170.888 | -0.79107 | -0.79107
2025-10-28 08:00:00 | 2.34 | 8.1882 | 0 | 0 | 170.888 | -5.8482 | -5.8482
2025-10-28 09:00:00 | 2.58 | 12.3173 | 0 | 0 | 170.888 | -9.7373 | -9.7373
2025-10-28 10:00:00 | 2.4 | 15.237 | 0 | 0 | 170.888 | -12.837 | -12.837
2025-10-28 11:00:00 | 2.46 | 16.7484 | 0 | 0 | 170.888 | -14.2884 | -14.2884
2025-10-28 12:00:00 | 2.58 | 16.7484 | 0 | 0 | 170.888 | -14.1684 | -14.1684
2025-10-28 13:00:00 | 2.4 | 15.237 | 0 | 0 | 170.888 | -12.837 | -12.837
2025-10-28 14:00:00 | 2.4 | 12.3173 | 0 | 0 | 170.888 | -9.9173 | -9.9173
2025-10-28 15:00:00 | 2.52 | 8.1882 | 0 | 0 | 170.888 | -5.6682 | -5.6682
2025-10-28 16:00:00 | 2.4 | 3.1311 | 0 | 0 | 170.888 | -0.73107 | -0.73107
2025-10-28 17:00:00 | 2.52 | 0 | 0 | 2.52 | 168.368 | 0 | 2.52
2025-10-28 18:00:00 | 2.52 | 0 | 0 | 2.52 | 165.848 | 0 | 2.52
2025-10-28 19:00:00 | 2.76 | 0 | 0 | 0 | 165.848 | 2.76 | 2.76
2025-10-28 20:00:00 | 2.52 | 0 | 0 | 0 | 165.848 | 2.52 | 2.52
2025-10-28 21:00:00 | 2.58 | 0 | 0 | 0 | 165.848 | 2.58 | 2.58
2025-10-28 22:00:00 | 2.7 | 0 | 0 | 0 | 165.848 | 2.7 | 2.7
2025-10-28 23:00:00 | 2.64 | 0 | 0 | 0 | 165.848 | 2.64 | 2.64
2025-10-29 00:00:00 | 2.58 | 0 | 0 | 0 | 165.848 | 2.58 | 2.58
2025-10-29 01:00:00 | 2.76 | 0 | 0 | 0 | 165.848 | 2.76 | 2.76
2025-10-29 02:00:00 | 2.58 | 0 | 0 | 0 | 165.848 | 2.58 | 2.58
2025-10-29 03:00:00 | 2.58 | 0 | 0 | 0 | 165.848 | 2.58 | 2.58
2025-10-29 04:00:00 | 2.82 | 0 | 0 | 0 | 165.848 | 2.82 | 2.82
2025-10-29 05:00:00 | 2.52 | 0 | 0 | 0 | 165.848 | 2.52 | 2.52
2025-10-29 06:00:00 | 2.58 | 0 | 0 | 0 | 165.848 | 2.58 | 2.58
2025-10-29 07:00:00 | 2.4 | 2.9982 | 0 | 0 | 165.848 | -0.59822 | -0.59822
2025-10-29 08:00:00 | 2.58 | 8.0481 | 0 | 0 | 165.848 | -5.4681 | -5.4681
2025-10-29 09:00:00 | 2.64 | 12.1714 | 0 | 0 | 165.848 | -9.5314 | -9.5314
2025-10-29 10:00:00 | 2.52 | 15.087 | 0 | 0 | 165.848 | -12.567 | -12.567
2025-10-29 11:00:00 | 2.76 | 16.5962 | 0 | 0 | 165.848 | -13.8362 | -13.8362
2025-10-29 12:00:00 | 2.58 | 16.5962 | 0 | 0 | 165.848 | -14.0162 | -14.0162
2025-10-29 13:00:00 | 2.64 | 15.087 | 0 | 0 | 165.848 | -12.447 | -12.447
2025-10-29 14:00:00 | 2.1 | 12.1714 | 0 | 0 | 165.848 | -10.0714 | -10.0714
2025-10-29 15:00:00 | 15 | 8.0481 | 0 | 6.9519 | 158.8961 | -8.8818e-16 | 6.9519
2025-10-29 16:00:00 | 16.26 | 2.9982 | 0 | 13.2618 | 145.6343 | -3.1974e-14 | 13.2618
2025-10-29 17:00:00 | 16.08 | 0 | 0 | 16.08 | 129.5543 | 0 | 16.08
2025-10-29 18:00:00 | 16.5 | 0 | 0 | 16.5 | 113.0543 | 0 | 16.5
2025-10-29 19:00:00 | 16.2 | 0 | 0 | 0 | 113.0543 | 16.2 | 16.2
2025-10-29 20:00:00 | 16.86 | 0 | 0 | 0 | 113.0543 | 16.86 | 16.86
2025-10-29 21:00:00 | 17.04 | 0 | 0 | 0 | 113.0543 | 17.04 | 17.04
2025-10-29 22:00:00 | 16.8 | 0 | 0 | 0 | 113.0543 | 16.8 | 16.8
2025-10-29 23:00:00 | 16.8 | 0 | 0 | 0 | 113.0543 | 16.8 | 16.8
2025-10-30 00:00:00 | 16.8 | 0 | 0 | 0 | 113.0543 | 16.8 | 16.8
2025-10-30 01:00:00 | 16.98 | 0 | 0 | 0 | 113.0543 | 16.98 | 16.98
2025-10-30 02:00:00 | 6.3 | 0 | 0 | 0 | 113.0543 | 6.3 | 6.3
2025-10-30 03:00:00 | 2.28 | 0 | 0 | 0 | 113.0543 | 2.28 | 2.28
2025-10-30 04:00:00 | 2.46 | 0 | 0 | 0 | 113.0543 | 2.46 | 2.46
2025-10-30 05:00:00 | 2.94 | 0 | 0 | 0 | 113.0543 | 2.94 | 2.94
2025-10-30 06:00:00 | 2.28 | 0 | 0 | 0 | 113.0543 | 2.28 | 2.28
2025-10-30 07:00:00 | 2.28 | 2.867 | 0 | 0 | 113.0543 | -0.58705 | -0.58705
2025-10-30 08:00:00 | 2.16 | 7.9097 | 0 | 0 | 113.0543 | -5.7497 | -5.7497
2025-10-30 09:00:00 | 2.04 | 12.0271 | 0 | 0 | 113.0543 | -9.9871 | -9.9871
2025-10-30 10:00:00 | 2.1 | 14.9384 | 0 | 0 | 113.0543 | -12.8384 | -12.8384
2025-10-30 11:00:00 | 2.34 | 16.4455 | 0 | 0 | 113.0543 | -14.1055 | -14.1055
2025-10-30 12:00:00 | 6.36 | 16.4455 | 0 | 0 | 113.0543 | -10.0855 | -10.0855
2025-10-30 13:00:00 | 10.5 | 14.9384 | 0 | 0 | 113.0543 | -4.4384 | -4.4384
2025-10-30 14:00:00 | 10.32 | 12.0271 | 0 | 0 | 113.0543 | -1.7071 | -1.7071
2025-10-30 15:00:00 | 10.62 | 7.9097 | 0 | 2.7103 | 110.3441 | -8.8818e-16 | 2.7103
2025-10-30 16:00:00 | 10.26 | 2.867 | 0 | 7.393 | 102.9511 | 8.8818e-16 | 7.393
2025-10-30 17:00:00 | 5.4 | 0 | 0 | 5.4 | 97.5511 | -9.77e-15 | 5.4
2025-10-30 18:00:00 | 4.44 | 0 | 0 | 4.44 | 93.1111 | 0 | 4.44
2025-10-30 19:00:00 | 4.08 | 0 | 0 | 0 | 93.1111 | 4.08 | 4.08
2025-10-30 20:00:00 | 4.2 | 0 | 0 | 0 | 93.1111 | 4.2 | 4.2
2025-10-30 21:00:00 | 4.38 | 0 | 0 | 0 | 93.1111 | 4.38 | 4.38
2025-10-30 22:00:00 | 4.2 | 0 | 0 | 0 | 93.1111 | 4.2 | 4.2
2025-10-30 23:00:00 | 4.08 | 0 | 0 | 0 | 93.1111 | 4.08 | 4.08
2025-10-31 00:00:00 | 4.38 | 0 | 0 | 0 | 93.1111 | 4.38 | 4.38
2025-10-31 01:00:00 | 4.14 | 0 | 0 | 0 | 93.1111 | 4.14 | 4.14
2025-10-31 02:00:00 | 4.14 | 0 | 0 | 0 | 93.1111 | 4.14 | 4.14
2025-10-31 03:00:00 | 4.2 | 0 | 0 | 0 | 93.1111 | 4.2 | 4.2
2025-10-31 04:00:00 | 4.32 | 0 | 0 | 0 | 93.1111 | 4.32 | 4.32
2025-10-31 05:00:00 | 4.14 | 0 | 0 | 0 | 93.1111 | 4.14 | 4.14
2025-10-31 06:00:00 | 15.72 | 0 | 0 | 0 | 93.1111 | 15.72 | 15.72
2025-10-31 07:00:00 | 18.06 | 2.7376 | 0 | 15.3224 | 77.7887 | 2.6645e-14 | 15.3224
2025-10-31 08:00:00 | 6 | 7.773 | 0 | 0 | 77.7887 | -1.773 | -1.773
2025-10-31 09:00:00 | 3.48 | 11.8844 | 0 | 0 | 77.7887 | -8.4044 | -8.4044
2025-10-31 10:00:00 | 3.48 | 14.7915 | 0 | 0 | 77.7887 | -11.3115 | -11.3115
2025-10-31 11:00:00 | 3.3 | 16.2964 | 12.9964 | 0 | 89.2256 | 1.7764e-15 | -12.9964
2025-10-31 12:00:00 | 3.66 | 16.2964 | 12.6364 | 0 | 100.3456 | 1.7764e-15 | -12.6364
2025-10-31 13:00:00 | 4.26 | 14.7915 | 10.5315 | 0 | 109.6134 | -8.8818e-15 | -10.5315
2025-10-31 14:00:00 | 5.76 | 11.8844 | 6.1244 | 0 | 115.0028 | 8.8818e-16 | -6.1244
2025-10-31 15:00:00 | 13.2 | 7.773 | 0 | 5.427 | 109.5758 | 8.8818e-16 | 5.427
2025-10-31 16:00:00 | 13.14 | 2.7376 | 0 | 10.4024 | 99.1734 | 2.8422e-14 | 10.4024
2025-10-31 17:00:00 | 13.26 | 0 | 0 | 13.26 | 85.9134 | 0 | 13.26
2025-10-31 18:00:00 | 12.3 | 0 | 0 | 12.3 | 73.6134 | 0 | 12.3
2025-10-31 19:00:00 | 5.28 | 0 | 0 | 0 | 73.6134 | 5.28 | 5.28
2025-10-31 20:00:00 | 4.44 | 0 | 60.6666 | 0 | 127 | 65.1066 | 4.44
2025-10-31 21:00:00 | 5.22 | 0 | 75 | 0 | 193 | 80.22 | 5.22
2025-10-31 22:00:00 | 3.54 | 0 | 75 | 0 | 259 | 78.54 | 3.54
2025-10-31 23:00:00 | 3.78 | 0 | 75 | 0 | 325 | 78.78 | 3.78
2025-11-01 00:00:00 | 4.68 | 0 | 0 | 0 | 325 | 4.68 | 4.68
2025-11-01 01:00:00 | 4.2 | 0 | 0 | 0 | 325 | 4.2 | 4.2
2025-11-01 02:00:00 | 3.54 | 0 | 0 | 0 | 325 | 3.54 | 3.54
2025-11-01 03:00:00 | 3.66 | 0 | 0 | 0 | 325 | 3.66 | 3.66
2025-11-01 04:00:00 | 4.56 | 0 | 0 | 0 | 325 | 4.56 | 4.56
2025-11-01 05:00:00 | 4.32 | 0 | 0 | 0 | 325 | 4.32 | 4.32
2025-11-01 06:00:00 | 3.6 | 0 | 0 | 0 | 325 | 3.6 | 3.6
2025-11-01 07:00:00 | 10.8 | 1.612 | 0 | 0 | 325 | 9.188 | 9.188
2025-11-01 08:00:00 | 61.74 | 4.7176 | 0 | 0 | 325 | 57.0224 | 57.0224
2025-11-01 09:00:00 | 67.38 | 7.2533 | 0 | 0 | 325 | 60.1267 | 60.1267
2025-11-01 10:00:00 | 71.82 | 9.0463 | 0 | 0 | 325 | 62.7737 | 62.7737
2025-11-01 11:00:00 | 54.18 | 9.9744 | 0 | 0 | 325 | 44.2056 | 44.2056
2025-11-01 12:00:00 | 54 | 9.9744 | 0 | 0 | 325 | 44.0256 | 44.0256
2025-11-01 13:00:00 | 54.12 | 9.0463 | 0 | 0 | 325 | 45.0737 | 45.0737
2025-11-01 14:00:00 | 55.02 | 7.2533 | 0 | 0 | 325 | 47.7667 | 47.7667
2025-11-01 15:00:00 | 93.24 | 4.7176 | 0 | 0 | 325 | 88.5224 | 88.5224
2025-11-01 16:00:00 | 91.5 | 1.612 | 0 | 0 | 325 | 89.888 | 89.888
2025-11-01 17:00:00 | 88.86 | 0 | 0 | 0 | 325 | 88.86 | 88.86
2025-11-01 18:00:00 | 87.48 | 0 | 0 | 0 | 325 | 87.48 | 87.48
2025-11-01 19:00:00 | 84.66 | 0 | 0 | 0 | 325 | 84.66 | 84.66
2025-11-01 20:00:00 | 94.98 | 0 | 0 | 0 | 325 | 94.98 | 94.98
2025-11-01 21:00:00 | 88.38 | 0 | 0 | 0 | 325 | 88.38 | 88.38
2025-11-01 22:00:00 | 78 | 0 | 0 | 0 | 325 | 78 | 78
2025-11-01 23:00:00 | 50.88 | 0 | 0 | 0 | 325 | 50.88 | 50.88
2025-11-02 00:00:00 | 50.28 | 0 | 0 | 0 | 325 | 50.28 | 50.28
2025-11-02 01:00:00 | 49.08 | 0 | 0 | 0 | 325 | 49.08 | 49.08
2025-11-02 02:00:00 | 42.96 | 0 | 0 | 0 | 325 | 42.96 | 42.96
2025-11-02 03:00:00 | 40.92 | 0 | 0 | 0 | 325 | 40.92 | 40.92
2025-11-02 04:00:00 | 39.6 | 0 | 0 | 0 | 325 | 39.6 | 39.6
2025-11-02 05:00:00 | 39.78 | 0 | 0 | 0 | 325 | 39.78 | 39.78
2025-11-02 06:00:00 | 38.22 | 0 | 0 | 0 | 325 | 38.22 | 38.22
2025-11-02 07:00:00 | 39.54 | 1.5343 | 0 | 0 | 325 | 38.0057 | 38.0057
2025-11-02 08:00:00 | 42.66 | 4.6353 | 0 | 0 | 325 | 38.0247 | 38.0247
2025-11-02 09:00:00 | 49.74 | 7.1673 | 0 | 0 | 325 | 42.5727 | 42.5727
2025-11-02 10:00:00 | 53.82 | 8.9576 | 0 | 0 | 325 | 44.8624 | 44.8624
2025-11-02 11:00:00 | 51.9 | 9.8844 | 0 | 0 | 325 | 42.0156 | 42.0156
2025-11-02 12:00:00 | 69.54 | 9.8844 | 0 | 0 | 325 | 59.6556 | 59.6556
2025-11-02 13:00:00 | 68.52 | 8.9576 | 0 | 0 | 325 | 59.5624 | 59.5624
2025-11-02 14:00:00 | 70.14 | 7.1673 | 0 | 0 | 325 | 62.9727 | 62.9727
2025-11-02 15:00:00 | 69.66 | 4.6353 | 0 | 0 | 325 | 65.0247 | 65.0247
2025-11-02 16:00:00 | 58.2 | 1.5343 | 0 | 0 | 325 | 56.6657 | 56.6657
2025-11-02 17:00:00 | 57.48 | 0 | 0 | 0 | 325 | 57.48 | 57.48
2025-11-02 18:00:00 | 55.98 | 0 | 0 | 0 | 325 | 55.98 | 55.98
2025-11-02 19:00:00 | 57.66 | 0 | 0 | 0 | 325 | 57.66 | 57.66
2025-11-02 20:00:00 | 88.2 | 0 | 0 | 0 | 325 | 88.2 | 88.2
2025-11-02 21:00:00 | 114.9 | 0 | 0 | 0 | 325 | 114.9 | 114.9
2025-11-02 22:00:00 | 111.36 | 0 | 0 | 0 | 325 | 111.36 | 111.36
2025-11-02 23:00:00 | 106.14 | 0 | 0 | 0 | 325 | 106.14 | 106.14
2025-11-03 00:00:00 | 104.82 | 0 | 0 | 0 | 325 | 104.82 | 104.82
2025-11-03 01:00:00 | 100.74 | 0 | 0 | 0 | 325 | 100.74 | 100.74
2025-11-03 02:00:00 | 82.44 | 0 | 0 | 0 | 325 | 82.44 | 82.44
2025-11-03 03:00:00 | 80.46 | 0 | 70.4545 | 0 | 387 | 150.9145 | 80.46
2025-11-03 04:00:00 | 53.88 | 0 | 75 | 0 | 453 | 128.88 | 53.88
2025-11-03 05:00:00 | 50.7 | 0 | 75 | 0 | 519 | 125.7 | 50.7
2025-11-03 06:00:00 | 52.86 | 0 | 75 | 0 | 585 | 127.86 | 52.86
2025-11-03 07:00:00 | 65.58 | 1.4577 | 0 | 64.1223 | 520.8777 | -2.8422e-14 | 64.1223
2025-11-03 08:00:00 | 68.64 | 4.5542 | 0 | 64.0858 | 456.7919 | 5.6843e-14 | 64.0858
2025-11-03 09:00:00 | 52.26 | 7.0824 | 0 | 45.1776 | 411.6143 | -7.1054e-15 | 45.1776
2025-11-03 10:00:00 | 67.38 | 8.8701 | 0 | 58.5099 | 353.1044 | 4.9738e-14 | 58.5099
2025-11-03 11:00:00 | 70.32 | 9.7955 | 0 | 60.5245 | 292.5799 | -7.1054e-15 | 60.5245
2025-11-03 12:00:00 | 54.6 | 9.7955 | 0 | 44.8045 | 247.7754 | -7.1054e-15 | 44.8045
2025-11-03 13:00:00 | 57.54 | 8.8701 | 0 | 32.7754 | 215 | 15.8945 | 48.6699
2025-11-03 14:00:00 | 68.64 | 7.0824 | 0 | 0 | 215 | 61.5576 | 61.5576
2025-11-03 15:00:00 | 85.44 | 4.5542 | 0 | 0 | 215 | 80.8858 | 80.8858
2025-11-03 16:00:00 | 98.1 | 1.4577 | 0 | 0 | 215 | 96.6423 | 96.6423
2025-11-03 17:00:00 | 112.32 | 0 | 0 | 75 | 140 | 37.32 | 112.32
2025-11-03 18:00:00 | 112.44 | 0 | 0 | 75 | 65 | 37.44 | 112.44
2025-11-03 19:00:00 | 112.02 | 0 | 56.88 | 0 | 115.0544 | 168.9 | 112.02
2025-11-03 20:00:00 | 111.66 | 0 | 9.0291 | 0 | 123 | 120.6891 | 111.66
2025-11-03 21:00:00 | 111.84 | 0 | 0 | 0 | 123 | 111.84 | 111.84
2025-11-03 22:00:00 | 103.5 | 0 | 0 | 0 | 123 | 103.5 | 103.5
2025-11-03 23:00:00 | 100.08 | 0 | 0 | 0 | 123 | 100.08 | 100.08
2025-11-04 00:00:00 | 85.92 | 0 | 75 | 0 | 189 | 160.92 | 85.92
2025-11-04 01:00:00 | 86.4 | 0 | 75 | 0 | 255 | 161.4 | 86.4
2025-11-04 02:00:00 | 89.22 | 0 | 75 | 0 | 321 | 164.22 | 89.22
2025-11-04 03:00:00 | 60.54 | 0 | 75 | 0 | 387 | 135.54 | 60.54
2025-11-04 04:00:00 | 51.18 | 0 | 75 | 0 | 453 | 126.18 | 51.18
2025-11-04 05:00:00 | 50.88 | 0 | 75 | 0 | 519 | 125.88 | 50.88
2025-11-04 06:00:00 | 49.62 | 0 | 75 | 0 | 585 | 124.62 | 49.62
2025-11-04 07:00:00 | 39.84 | 1.3823 | 0 | 38.4577 | 546.5423 | -2.8422e-14 | 38.4577
2025-11-04 08:00:00 | 42.6 | 4.4742 | 0 | 38.1258 | 508.4165 | -2.1316e-14 | 38.1258
2025-11-04 09:00:00 | 47.4 | 6.9987 | 0 | 40.4013 | 468.0152 | 0 | 40.4013
2025-11-04 10:00:00 | 64.5 | 8.7838 | 0 | 55.7162 | 412.2989 | 2.1316e-14 | 55.7162
2025-11-04 11:00:00 | 93.24 | 9.7078 | 0 | 75 | 337.2989 | 8.5322 | 83.5322
2025-11-04 12:00:00 | 97.2 | 9.7078 | 0 | 75 | 262.2989 | 12.4922 | 87.4922
2025-11-04 13:00:00 | 89.16 | 8.7838 | 0 | 47.2989 | 215 | 33.0773 | 80.3762
2025-11-04 14:00:00 | 81.3 | 6.9987 | 0 | 0 | 215 | 74.3013 | 74.3013
2025-11-04 15:00:00 | 74.16 | 4.4742 | 0 | 0 | 215 | 69.6858 | 69.6858
2025-11-04 16:00:00 | 80.88 | 1.3823 | 0 | 0 | 215 | 79.4977 | 79.4977
2025-11-04 17:00:00 | 93.36 | 0 | 0 | 75 | 140 | 18.36 | 93.36
2025-11-04 18:00:00 | 102.48 | 0 | 0 | 75 | 65 | 27.48 | 102.48
2025-11-04 19:00:00 | 86.34 | 0 | 65.9091 | 0 | 123 | 152.2491 | 86.34
2025-11-04 20:00:00 | 84.42 | 0 | 0 | 0 | 123 | 84.42 | 84.42
2025-11-04 21:00:00 | 84.72 | 0 | 0 | 0 | 123 | 84.72 | 84.72
2025-11-04 22:00:00 | 84.84 | 0 | 0 | 0 | 123 | 84.84 | 84.84
2025-11-04 23:00:00 | 79.44 | 0 | 0 | 0 | 123 | 79.44 | 79.44
2025-11-05 00:00:00 | 47.64 | 0 | 75 | 0 | 189 | 122.64 | 47.64
2025-11-05 01:00:00 | 47.82 | 0 | 75 | 0 | 255 | 122.82 | 47.82
2025-11-05 02:00:00 | 53.16 | 0 | 75 | 0 | 321 | 128.16 | 53.16
2025-11-05 03:00:00 | 51.06 | 0 | 75 | 0 | 387 | 126.06 | 51.06
2025-11-05 04:00:00 | 50.4 | 0 | 75 | 0 | 453 | 125.4 | 50.4
2025-11-05 05:00:00 | 52.86 | 0 | 75 | 0 | 519 | 127.86 | 52.86
2025-11-05 06:00:00 | 51.3 | 0 | 75 | 0 | 585 | 126.3 | 51.3
2025-11-05 07:00:00 | 50.82 | 1.3081 | 0 | 49.5119 | 535.4881 | -3.5527e-14 | 49.5119
2025-11-05 08:00:00 | 54.12 | 4.3954 | 0 | 49.7246 | 485.7635 | -2.8422e-14 | 49.7246
2025-11-05 09:00:00 | 65.76 | 6.9162 | 0 | 58.8438 | 426.9197 | 0 | 58.8438
2025-11-05 10:00:00 | 65.4 | 8.6986 | 0 | 56.7014 | 370.2183 | -2.8422e-14 | 56.7014
2025-11-05 11:00:00 | 63.42 | 9.6213 | 0 | 53.7987 | 316.4195 | -7.1054e-15 | 53.7987
2025-11-05 12:00:00 | 61.68 | 9.6213 | 0 | 52.0587 | 264.3608 | -1.4211e-14 | 52.0587
2025-11-05 13:00:00 | 60 | 8.6986 | 0 | 51.3014 | 213.0594 | -3.5527e-14 | 51.3014
2025-11-05 14:00:00 | 55.44 | 6.9162 | 0 | 27.2194 | 185.84 | 21.3044 | 48.5238
2025-11-05 15:00:00 | 55.5 | 4.3954 | 0 | 0 | 185.84 | 51.1046 | 51.1046
2025-11-05 16:00:00 | 57.42 | 1.3081 | 0 | 0 | 185.84 | 56.1119 | 56.1119
2025-11-05 17:00:00 | 55.44 | 0 | 0 | 55.44 | 130.4 | 0 | 55.44
2025-11-05 18:00:00 | 65.4 | 0 | 0 | 65.4 | 65 | 0 | 65.4
2025-11-05 19:00:00 | 93.9 | 0 | 75 | 0 | 131 | 168.9 | 93.9
2025-11-05 20:00:00 | 96.84 | 0 | 65.9091 | 0 | 189 | 162.7491 | 96.84
2025-11-05 21:00:00 | 92.4 | 0 | 0 | 0 | 189 | 92.4 | 92.4
2025-11-05 22:00:00 | 61.86 | 0 | 0 | 0 | 189 | 61.86 | 61.86
2025-11-05 23:00:00 | 58.14 | 0 | 0 | 0 | 189 | 58.14 | 58.14
2025-11-06 00:00:00 | 51.6 | 0 | 0 | 0 | 189 | 51.6 | 51.6
2025-11-06 01:00:00 | 49.26 | 0 | 75 | 0 | 255 | 124.26 | 49.26
2025-11-06 02:00:00 | 48.18 | 0 | 75 | 0 | 321 | 123.18 | 48.18
2025-11-06 03:00:00 | 47.94 | 0 | 75 | 0 | 387 | 122.94 | 47.94
2025-11-06 04:00:00 | 48.06 | 0 | 75 | 0 | 453 | 123.06 | 48.06
2025-11-06 05:00:00 | 46.74 | 0 | 75 | 0 | 519 | 121.74 | 46.74
2025-11-06 06:00:00 | 45.66 | 0 | 75 | 0 | 585 | 120.66 | 45.66
2025-11-06 07:00:00 | 45.6 | 1.2351 | 0 | 44.3649 | 540.6351 | 1.4211e-14 | 44.3649
2025-11-06 08:00:00 | 44.46 | 4.3178 | 0 | 40.1422 | 500.493 | -2.8422e-14 | 40.1422
2025-11-06 09:00:00 | 46.62 | 6.8349 | 0 | 39.7851 | 460.7079 | -4.2633e-14 | 39.7851
2025-11-06 10:00:00 | 46.98 | 8.6147 | 0 | 38.3653 | 422.3425 | -1.4211e-14 | 38.3653
2025-11-06 11:00:00 | 47.46 | 9.536 | 0 | 37.924 | 384.4185 | 2.8422e-14 | 37.924
2025-11-06 12:00:00 | 46.5 | 9.536 | 0 | 36.964 | 347.4545 | 2.1316e-14 | 36.964
2025-11-06 13:00:00 | 48.42 | 8.6147 | 0 | 39.8053 | 307.6491 | 0 | 39.8053
2025-11-06 14:00:00 | 46.56 | 6.8349 | 0 | 39.7251 | 267.924 | -4.2633e-14 | 39.7251
2025-11-06 15:00:00 | 50.76 | 4.3178 | 0 | 46.4422 | 221.4819 | -2.8422e-14 | 46.4422
2025-11-06 16:00:00 | 51.72 | 1.2351 | 0 | 33.7819 | 187.7 | 16.703 | 50.4849
2025-11-06 17:00:00 | 59.58 | 0 | 0 | 59.58 | 128.12 | 0 | 59.58
2025-11-06 18:00:00 | 63.12 | 0 | 0 | 63.12 | 65 | 0 | 63.12
2025-11-06 19:00:00 | 65.94 | 0 | 65.9091 | 0 | 123 | 131.8491 | 65.94
2025-11-06 20:00:00 | 67.56 | 0 | 0 | 0 | 123 | 67.56 | 67.56
2025-11-06 21:00:00 | 63.06 | 0 | 0 | 0 | 123 | 63.06 | 63.06
2025-11-06 22:00:00 | 54.6 | 0 | 0 | 0 | 123 | 54.6 | 54.6
2025-11-06 23:00:00 | 52.26 | 0 | 0 | 0 | 123 | 52.26 | 52.26
2025-11-07 00:00:00 | 44.16 | 0 | 75 | 0 | 189 | 119.16 | 44.16
2025-11-07 01:00:00 | 43.02 | 0 | 75 | 0 | 255 | 118.02 | 43.02
2025-11-07 02:00:00 | 43.38 | 0 | 75 | 0 | 321 | 118.38 | 43.38
2025-11-07 03:00:00 | 42.42 | 0 | 75 | 0 | 387 | 117.42 | 42.42
2025-11-07 04:00:00 | 43.56 | 0 | 75 | 0 | 453 | 118.56 | 43.56
2025-11-07 05:00:00 | 44.22 | 0 | 75 | 0 | 519 | 119.22 | 44.22
2025-11-07 06:00:00 | 43.92 | 0 | 75 | 0 | 585 | 118.92 | 43.92
2025-11-07 07:00:00 | 46.26 | 1.1634 | 0 | 45.0966 | 539.9034 | -2.1316e-14 | 45.0966
2025-11-07 08:00:00 | 48.12 | 4.2416 | 0 | 43.8784 | 496.025 | 4.9738e-14 | 43.8784
2025-11-07 09:00:00 | 49.14 | 6.7549 | 0 | 42.3851 | 453.6398 | 4.9738e-14 | 42.3851
2025-11-07 10:00:00 | 48.42 | 8.532 | 0 | 39.888 | 413.7518 | -3.5527e-14 | 39.888
2025-11-07 11:00:00 | 48.66 | 9.4519 | 0 | 39.2081 | 374.5438 | 2.1316e-14 | 39.2081
2025-11-07 12:00:00 | 50.34 | 9.4519 | 0 | 40.8881 | 333.6557 | 2.8422e-14 | 40.8881
2025-11-07 13:00:00 | 47.52 | 8.532 | 0 | 38.988 | 294.6678 | -2.8422e-14 | 38.988
2025-11-07 14:00:00 | 55.44 | 6.7549 | 0 | 48.6851 | 245.9826 | 4.9738e-14 | 48.6851
2025-11-07 15:00:00 | 84.06 | 4.2416 | 0 | 30.9826 | 215 | 48.8358 | 79.8184
2025-11-07 16:00:00 | 92.34 | 1.1634 | 0 | 0 | 215 | 91.1766 | 91.1766
2025-11-07 17:00:00 | 90.54 | 0 | 0 | 75 | 140 | 15.54 | 90.54
2025-11-07 18:00:00 | 84.78 | 0 | 0 | 75 | 65 | 9.78 | 84.78
2025-11-07 19:00:00 | 80.7 | 0 | 0 | 0 | 65 | 80.7 | 80.7
2025-11-07 20:00:00 | 78.6 | 0 | 0 | 0 | 65 | 78.6 | 78.6
2025-11-07 21:00:00 | 53.7 | 0 | 0 | 0 | 65 | 53.7 | 53.7
2025-11-07 22:00:00 | 53.64 | 0 | 0 | 0 | 65 | 53.64 | 53.64
2025-11-07 23:00:00 | 53.46 | 0 | 0 | 0 | 65 | 53.46 | 53.46
2025-11-08 00:00:00 | 51.78 | 0 | 0 | 0 | 65 | 51.78 | 51.78
2025-11-08 01:00:00 | 51.6 | 0 | 0 | 0 | 65 | 51.6 | 51.6
2025-11-08 02:00:00 | 51.84 | 0 | 0 | 0 | 65 | 51.84 | 51.84
2025-11-08 03:00:00 | 50.46 | 0 | 0 | 0 | 65 | 50.46 | 50.46
2025-11-08 04:00:00 | 50.4 | 0 | 0 | 0 | 65 | 50.4 | 50.4
2025-11-08 05:00:00 | 51.54 | 0 | 0 | 0 | 65 | 51.54 | 51.54
2025-11-08 06:00:00 | 51.36 | 0 | 0 | 0 | 65 | 51.36 | 51.36
2025-11-08 07:00:00 | 48.24 | 1.093 | 0 | 0 | 65 | 47.147 | 47.147
2025-11-08 08:00:00 | 46.08 | 4.1666 | 0 | 0 | 65 | 41.9134 | 41.9134
2025-11-08 09:00:00 | 47.34 | 6.6761 | 0 | 0 | 65 | 40.6639 | 40.6639
2025-11-08 10:00:00 | 48.3 | 8.4507 | 0 | 0 | 65 | 39.8493 | 39.8493
2025-11-08 11:00:00 | 47.52 | 9.3692 | 0 | 0 | 65 | 38.1508 | 38.1508
2025-11-08 12:00:00 | 47.58 | 9.3692 | 0 | 0 | 65 | 38.2108 | 38.2108
2025-11-08 13:00:00 | 51.12 | 8.4507 | 0 | 0 | 65 | 42.6693 | 42.6693
2025-11-08 14:00:00 | 55.92 | 6.6761 | 0 | 0 | 65 | 49.2439 | 49.2439
2025-11-08 15:00:00 | 92.64 | 4.1666 | 0 | 0 | 65 | 88.4734 | 88.4734
2025-11-08 16:00:00 | 104.88 | 1.093 | 0 | 0 | 65 | 103.787 | 103.787
2025-11-08 17:00:00 | 92.34 | 0 | 0 | 0 | 65 | 92.34 | 92.34
2025-11-08 18:00:00 | 71.88 | 0 | 0 | 0 | 65 | 71.88 | 71.88
2025-11-08 19:00:00 | 70.32 | 0 | 0 | 0 | 65 | 70.32 | 70.32
2025-11-08 20:00:00 | 65.76 | 0 | 0 | 0 | 65 | 65.76 | 65.76
2025-11-08 21:00:00 | 60.96 | 0 | 0 | 0 | 65 | 60.96 | 60.96
2025-11-08 22:00:00 | 53.7 | 0 | 0 | 0 | 65 | 53.7 | 53.7
2025-11-08 23:00:00 | 46.44 | 0 | 0 | 0 | 65 | 46.44 | 46.44
2025-11-09 00:00:00 | 53.7 | 0 | 0 | 0 | 65 | 53.7 | 53.7
2025-11-09 01:00:00 | 59.04 | 0 | 0 | 0 | 65 | 59.04 | 59.04
2025-11-09 02:00:00 | 57.9 | 0 | 0 | 0 | 65 | 57.9 | 57.9
2025-11-09 03:00:00 | 57.96 | 0 | 0 | 0 | 65 | 57.96 | 57.96
2025-11-09 04:00:00 | 57.3 | 0 | 0 | 0 | 65 | 57.3 | 57.3
2025-11-09 05:00:00 | 56.04 | 0 | 0 | 0 | 65 | 56.04 | 56.04
2025-11-09 06:00:00 | 57.78 | 0 | 0 | 0 | 65 | 57.78 | 57.78
2025-11-09 07:00:00 | 54.36 | 1.0238 | 0 | 0 | 65 | 53.3362 | 53.3362
2025-11-09 08:00:00 | 50.28 | 4.0929 | 0 | 0 | 65 | 46.1871 | 46.1871
2025-11-09 09:00:00 | 62.94 | 6.5987 | 0 | 0 | 65 | 56.3413 | 56.3413
2025-11-09 10:00:00 | 68.52 | 8.3707 | 0 | 0 | 65 | 60.1493 | 60.1493
2025-11-09 11:00:00 | 60.6 | 9.2879 | 0 | 0 | 65 | 51.3121 | 51.3121
2025-11-09 12:00:00 | 54.12 | 9.2879 | 0 | 0 | 65 | 44.8321 | 44.8321
2025-11-09 13:00:00 | 47.94 | 8.3707 | 0 | 0 | 65 | 39.5693 | 39.5693
2025-11-09 14:00:00 | 44.64 | 6.5987 | 0 | 0 | 65 | 38.0413 | 38.0413
2025-11-09 15:00:00 | 43.38 | 4.0929 | 0 | 0 | 65 | 39.2871 | 39.2871
2025-11-09 16:00:00 | 42.42 | 1.0238 | 75 | 0 | 131 | 116.3962 | 41.3962
2025-11-09 17:00:00 | 42.78 | 0 | 75 | 0 | 197 | 117.78 | 42.78
2025-11-09 18:00:00 | 40.56 | 0 | 45.9108 | 0 | 237.4015 | 86.4708 | 40.56
2025-11-09 19:00:00 | 36.54 | 0 | 0 | 0 | 237.4015 | 36.54 | 36.54
2025-11-09 20:00:00 | 39.78 | 0 | 0 | 0 | 237.4015 | 39.78 | 39.78
2025-11-09 21:00:00 | 35.52 | 0 | 0 | 0 | 237.4015 | 35.52 | 35.52
2025-11-09 22:00:00 | 35.46 | 0 | 0 | 0 | 237.4015 | 35.46 | 35.46
2025-11-09 23:00:00 | 36.36 | 0 | 0 | 0 | 237.4015 | 36.36 | 36.36
2025-11-10 00:00:00 | 37.56 | 0 | 0 | 0 | 237.4015 | 37.56 | 37.56
2025-11-10 01:00:00 | 35.7 | 0 | 0 | 0 | 237.4015 | 35.7 | 35.7
2025-11-10 02:00:00 | 35.52 | 0 | 75 | 0 | 303.4015 | 110.52 | 35.52
2025-11-10 03:00:00 | 36.18 | 0 | 75 | 0 | 369.4015 | 111.18 | 36.18
2025-11-10 04:00:00 | 35.64 | 0 | 75 | 0 | 435.4015 | 110.64 | 35.64
2025-11-10 05:00:00 | 36.06 | 0 | 75 | 0 | 501.4015 | 111.06 | 36.06
2025-11-10 06:00:00 | 35.94 | 0 | 75 | 0 | 567.4015 | 110.94 | 35.94
2025-11-10 07:00:00 | 35.64 | 0.95603 | 0 | 34.684 | 532.7175 | 1.4211e-14 | 34.684
2025-11-10 08:00:00 | 35.34 | 4.0206 | 0 | 31.3194 | 501.3981 | 7.1054e-15 | 31.3194
2025-11-10 09:00:00 | 37.62 | 6.5227 | 0 | 31.0973 | 470.3008 | 1.0658e-14 | 31.0973
2025-11-10 10:00:00 | 35.22 | 8.292 | 0 | 26.928 | 443.3729 | -3.1974e-14 | 26.928
2025-11-10 11:00:00 | 41.82 | 9.2079 | 0 | 32.6121 | 410.7608 | 2.8422e-14 | 32.6121
2025-11-10 12:00:00 | 45 | 9.2079 | 0 | 35.7921 | 374.9686 | 2.8422e-14 | 35.7921
2025-11-10 13:00:00 | 57.06 | 8.292 | 0 | 48.768 | 326.2007 | -2.8422e-14 | 48.768
2025-11-10 14:00:00 | 60 | 6.5227 | 0 | 53.4773 | 272.7234 | 1.4211e-14 | 53.4773
2025-11-10 15:00:00 | 55.08 | 4.0206 | 0 | 51.0594 | 221.664 | 7.1054e-15 | 51.0594
2025-11-10 16:00:00 | 59.34 | 0.95603 | 0 | 58.384 | 163.28 | 2.1316e-14 | 58.384
2025-11-10 17:00:00 | 58.86 | 0 | 0 | 58.86 | 104.42 | 0 | 58.86
2025-11-10 18:00:00 | 39.42 | 0 | 0 | 39.42 | 65 | 0 | 39.42
2025-11-10 19:00:00 | 42.66 | 0 | 0 | 0 | 65 | 42.66 | 42.66
2025-11-10 20:00:00 | 47.4 | 0 | 0 | 0 | 65 | 47.4 | 47.4
2025-11-10 21:00:00 | 51.18 | 0 | 0 | 0 | 65 | 51.18 | 51.18
2025-11-10 22:00:00 | 42.78 | 0 | 0 | 0 | 65 | 42.78 | 42.78
2025-11-10 23:00:00 | 39.66 | 0 | 0 | 0 | 65 | 39.66 | 39.66
2025-11-11 00:00:00 | 35.82 | 0 | 0 | 0 | 65 | 35.82 | 35.82
2025-11-11 01:00:00 | 36.9 | 0 | 0 | 0 | 65 | 36.9 | 36.9
2025-11-11 02:00:00 | 35.88 | 0 | 0 | 0 | 65 | 35.88 | 35.88
2025-11-11 03:00:00 | 35.76 | 0 | 0 | 0 | 65 | 35.76 | 35.76
2025-11-11 04:00:00 | 35.46 | 0 | 0 | 0 | 65 | 35.46 | 35.46
2025-11-11 05:00:00 | 36.18 | 0 | 0 | 0 | 65 | 36.18 | 36.18
2025-11-11 06:00:00 | 35.64 | 0 | 0 | 0 | 65 | 35.64 | 35.64
2025-11-11 07:00:00 | 35.28 | 0.88957 | 0 | 0 | 65 | 34.3904 | 34.3904
2025-11-11 08:00:00 | 36.18 | 3.9496 | 0 | 0 | 65 | 32.2304 | 32.2304
2025-11-11 09:00:00 | 36.12 | 6.4481 | 0 | 0 | 65 | 29.6719 | 29.6719
2025-11-11 10:00:00 | 36.42 | 8.2148 | 0 | 0 | 65 | 28.2052 | 28.2052
2025-11-11 11:00:00 | 43.5 | 9.1293 | 0 | 0 | 65 | 34.3707 | 34.3707
2025-11-11 12:00:00 | 44.16 | 9.1293 | 0 | 0 | 65 | 35.0307 | 35.0307
2025-11-11 13:00:00 | 44.88 | 8.2148 | 0 | 0 | 65 | 36.6652 | 36.6652
2025-11-11 14:00:00 | 45.48 | 6.4481 | 0 | 0 | 65 | 39.0319 | 39.0319
2025-11-11 15:00:00 | 44.76 | 3.9496 | 75 | 0 | 131 | 115.8104 | 40.8104
2025-11-11 16:00:00 | 46.44 | 0.88957 | 75 | 0 | 197 | 120.5504 | 45.5504
2025-11-11 17:00:00 | 55.2 | 0 | 65.9091 | 0 | 255 | 121.1091 | 55.2
2025-11-11 18:00:00 | 61.38 | 0 | 0 | 0 | 255 | 61.38 | 61.38
2025-11-11 19:00:00 | 59.76 | 0 | 0 | 0 | 255 | 59.76 | 59.76
2025-11-11 20:00:00 | 72.6 | 0 | 0 | 0 | 255 | 72.6 | 72.6
2025-11-11 21:00:00 | 74.52 | 0 | 0 | 0 | 255 | 74.52 | 74.52
2025-11-11 22:00:00 | 71.58 | 0 | 0 | 0 | 255 | 71.58 | 71.58
2025-11-11 23:00:00 | 60.18 | 0 | 0 | 0 | 255 | 60.18 | 60.18
2025-11-12 00:00:00 | 59.22 | 0 | 0 | 0 | 255 | 59.22 | 59.22
2025-11-12 01:00:00 | 57.18 | 0 | 0 | 0 | 255 | 57.18 | 57.18
2025-11-12 02:00:00 | 55.26 | 0 | 75 | 0 | 321 | 130.26 | 55.26
2025-11-12 03:00:00 | 56.16 | 0 | 75 | 0 | 387 | 131.16 | 56.16
2025-11-12 04:00:00 | 53.58 | 0 | 75 | 0 | 453 | 128.58 | 53.58
2025-11-12 05:00:00 | 51.06 | 0 | 75 | 0 | 519 | 126.06 | 51.06
2025-11-12 06:00:00 | 40.32 | 0 | 75 | 0 | 585 | 115.32 | 40.32
2025-11-12 07:00:00 | 40.74 | 0.82448 | 0 | 39.9155 | 545.0845 | 0 | 39.9155
2025-11-12 08:00:00 | 45.84 | 3.8801 | 0 | 41.9599 | 503.1245 | -7.1054e-15 | 41.9599
2025-11-12 09:00:00 | 41.16 | 6.3749 | 0 | 34.7851 | 468.3395 | 1.4211e-14 | 34.7851
2025-11-12 10:00:00 | 43.38 | 8.1391 | 0 | 35.2409 | 433.0985 | -3.5527e-14 | 35.2409
2025-11-12 11:00:00 | 45 | 9.0523 | 0 | 35.9477 | 397.1508 | -4.2633e-14 | 35.9477
2025-11-12 12:00:00 | 47.28 | 9.0523 | 0 | 38.2277 | 358.923 | -4.2633e-14 | 38.2277
2025-11-12 13:00:00 | 48 | 8.1391 | 0 | 39.8609 | 319.0621 | -3.5527e-14 | 39.8609
2025-11-12 14:00:00 | 48.66 | 6.3749 | 0 | 42.2851 | 276.777 | 1.4211e-14 | 42.2851
2025-11-12 15:00:00 | 53.88 | 3.8801 | 0 | 49.9999 | 226.7771 | -7.1054e-15 | 49.9999
2025-11-12 16:00:00 | 55.02 | 0.82448 | 0 | 50.9571 | 175.82 | 3.2384 | 54.1955
2025-11-12 17:00:00 | 57.72 | 0 | 0 | 57.72 | 118.1 | 0 | 57.72
2025-11-12 18:00:00 | 53.1 | 0 | 0 | 53.1 | 65 | 0 | 53.1
2025-11-12 19:00:00 | 54.54 | 0 | 75 | 0 | 131 | 129.54 | 54.54
2025-11-12 20:00:00 | 61.14 | 0 | 65.9091 | 0 | 189 | 127.0491 | 61.14
2025-11-12 21:00:00 | 58.38 | 0 | 0 | 0 | 189 | 58.38 | 58.38
2025-11-12 22:00:00 | 53.4 | 0 | 0 | 0 | 189 | 53.4 | 53.4
2025-11-12 23:00:00 | 52.08 | 0 | 0 | 0 | 189 | 52.08 | 52.08
2025-11-13 00:00:00 | 52.32 | 0 | 0 | 0 | 189 | 52.32 | 52.32
2025-11-13 01:00:00 | 48 | 0 | 75 | 0 | 255 | 123 | 48
2025-11-13 02:00:00 | 46.8 | 0 | 75 | 0 | 321 | 121.8 | 46.8
2025-11-13 03:00:00 | 45.6 | 0 | 75 | 0 | 387 | 120.6 | 45.6
2025-11-13 04:00:00 | 44.88 | 0 | 75 | 0 | 453 | 119.88 | 44.88
2025-11-13 05:00:00 | 43.62 | 0 | 75 | 0 | 519 | 118.62 | 43.62
2025-11-13 06:00:00 | 45.3 | 0 | 75 | 0 | 585 | 120.3 | 45.3
2025-11-13 07:00:00 | 42.48 | 0.76077 | 0 | 41.7192 | 543.2808 | 1.4211e-14 | 41.7192
2025-11-13 08:00:00 | 43.74 | 3.8119 | 0 | 39.9281 | 503.3527 | 7.1054e-15 | 39.9281
2025-11-13 09:00:00 | 45.3 | 6.3032 | 0 | 38.9968 | 464.3559 | -7.1054e-15 | 38.9968
2025-11-13 10:00:00 | 46.56 | 8.0648 | 0 | 38.4952 | 425.8607 | -4.2633e-14 | 38.4952
2025-11-13 11:00:00 | 51.72 | 8.9767 | 0 | 42.7433 | 383.1174 | -1.4211e-14 | 42.7433
2025-11-13 12:00:00 | 52.02 | 8.9767 | 0 | 43.0433 | 340.074 | -2.1316e-14 | 43.0433
2025-11-13 13:00:00 | 52.14 | 8.0648 | 0 | 44.0752 | 295.9988 | -4.2633e-14 | 44.0752
2025-11-13 14:00:00 | 52.32 | 6.3032 | 0 | 46.0168 | 249.982 | -7.1054e-15 | 46.0168
2025-11-13 15:00:00 | 50.52 | 3.8119 | 0 | 46.7081 | 203.274 | 7.1054e-15 | 46.7081
2025-11-13 16:00:00 | 61.26 | 0.76077 | 0 | 13.414 | 189.86 | 47.0853 | 60.4992
2025-11-13 17:00:00 | 62.22 | 0 | 0 | 62.22 | 127.64 | 0 | 62.22
2025-11-13 18:00:00 | 62.64 | 0 | 0 | 62.64 | 65 | 0 | 62.64
2025-11-13 19:00:00 | 64.08 | 0 | 75 | 0 | 131 | 139.08 | 64.08
2025-11-13 20:00:00 | 63.36 | 0 | 65.9091 | 0 | 189 | 129.2691 | 63.36
2025-11-13 21:00:00 | 61.08 | 0 | 0 | 0 | 189 | 61.08 | 61.08
2025-11-13 22:00:00 | 56.28 | 0 | 0 | 0 | 189 | 56.28 | 56.28
2025-11-13 23:00:00 | 46.8 | 0 | 0 | 0 | 189 | 46.8 | 46.8
2025-11-14 00:00:00 | 47.28 | 0 | 0 | 0 | 189 | 47.28 | 47.28
2025-11-14 01:00:00 | 47.16 | 0 | 75 | 0 | 255 | 122.16 | 47.16
2025-11-14 02:00:00 | 43.86 | 0 | 75 | 0 | 321 | 118.86 | 43.86
2025-11-14 03:00:00 | 45.6 | 0 | 75 | 0 | 387 | 120.6 | 45.6
2025-11-14 04:00:00 | 45.12 | 0 | 75 | 0 | 453 | 120.12 | 45.12
2025-11-14 05:00:00 | 45.48 | 0 | 75 | 0 | 519 | 120.48 | 45.48
2025-11-14 06:00:00 | 46.08 | 0 | 75 | 0 | 585 | 121.08 | 46.08
2025-11-14 07:00:00 | 42.84 | 0.69849 | 0 | 42.1415 | 542.8585 | -1.4211e-14 | 42.1415
2025-11-14 08:00:00 | 42.96 | 3.7453 | 0 | 39.2147 | 503.6438 | 3.5527e-14 | 39.2147
2025-11-14 09:00:00 | 41.7 | 6.233 | 0 | 35.467 | 468.1767 | 1.4211e-14 | 35.467
2025-11-14 10:00:00 | 46.32 | 7.992 | 0 | 38.328 | 429.8488 | 7.1054e-15 | 38.328
2025-11-14 11:00:00 | 52.74 | 8.9026 | 0 | 43.8374 | 386.0114 | -2.1316e-14 | 43.8374
2025-11-14 12:00:00 | 59.4 | 8.9026 | 0 | 50.4974 | 335.514 | -2.8422e-14 | 50.4974
2025-11-14 13:00:00 | 62.7 | 7.992 | 0 | 54.708 | 280.806 | 7.1054e-15 | 54.708
2025-11-14 14:00:00 | 62.52 | 6.233 | 0 | 56.287 | 224.519 | 1.4211e-14 | 56.287
2025-11-14 15:00:00 | 60.78 | 3.7453 | 0 | 39.159 | 185.36 | 17.8757 | 57.0347
2025-11-14 16:00:00 | 64.56 | 0.69849 | 0 | 0 | 185.36 | 63.8615 | 63.8615
2025-11-14 17:00:00 | 62.04 | 0 | 0 | 62.04 | 123.32 | 0 | 62.04
2025-11-14 18:00:00 | 58.32 | 0 | 0 | 58.32 | 65 | 0 | 58.32
2025-11-14 19:00:00 | 55.44 | 0 | 0 | 0 | 65 | 55.44 | 55.44
2025-11-14 20:00:00 | 55.02 | 0 | 0 | 0 | 65 | 55.02 | 55.02
2025-11-14 21:00:00 | 53.4 | 0 | 0 | 0 | 65 | 53.4 | 53.4
2025-11-14 22:00:00 | 51.24 | 0 | 0 | 0 | 65 | 51.24 | 51.24
2025-11-14 23:00:00 | 55.32 | 0 | 0 | 0 | 65 | 55.32 | 55.32
2025-11-15 00:00:00 | 52.68 | 0 | 0 | 0 | 65 | 52.68 | 52.68
2025-11-15 01:00:00 | 52.26 | 0 | 0 | 0 | 65 | 52.26 | 52.26
2025-11-15 02:00:00 | 49.86 | 0 | 0 | 0 | 65 | 49.86 | 49.86
2025-11-15 03:00:00 | 49.74 | 0 | 0 | 0 | 65 | 49.74 | 49.74
2025-11-15 04:00:00 | 50.16 | 0 | 0 | 0 | 65 | 50.16 | 50.16
2025-11-15 05:00:00 | 50.34 | 0 | 0 | 0 | 65 | 50.34 | 50.34
2025-11-15 06:00:00 | 48.3 | 0 | 0 | 0 | 65 | 48.3 | 48.3
2025-11-15 07:00:00 | 52.62 | 0.63763 | 0 | 0 | 65 | 51.9824 | 51.9824
2025-11-15 08:00:00 | 60.42 | 3.6801 | 0 | 0 | 65 | 56.7399 | 56.7399
2025-11-15 09:00:00 | 60.42 | 6.1643 | 0 | 0 | 65 | 54.2557 | 54.2557
2025-11-15 10:00:00 | 58.26 | 7.9208 | 0 | 0 | 65 | 50.3392 | 50.3392
2025-11-15 11:00:00 | 57.72 | 8.8301 | 0 | 0 | 65 | 48.8899 | 48.8899
2025-11-15 12:00:00 | 55.74 | 8.8301 | 0 | 0 | 65 | 46.9099 | 46.9099
2025-11-15 13:00:00 | 63.06 | 7.9208 | 0 | 0 | 65 | 55.1392 | 55.1392
2025-11-15 14:00:00 | 71.04 | 6.1643 | 0 | 0 | 65 | 64.8757 | 64.8757
2025-11-15 15:00:00 | 76.8 | 3.6801 | 0 | 0 | 65 | 73.1199 | 73.1199
2025-11-15 16:00:00 | 75.9 | 0.63763 | 0 | 0 | 65 | 75.2624 | 75.2624
2025-11-15 17:00:00 | 72.54 | 0 | 0 | 0 | 65 | 72.54 | 72.54
2025-11-15 18:00:00 | 71.76 | 0 | 0 | 0 | 65 | 71.76 | 71.76
2025-11-15 19:00:00 | 72.3 | 0 | 0 | 0 | 65 | 72.3 | 72.3
2025-11-15 20:00:00 | 70.86 | 0 | 0 | 0 | 65 | 70.86 | 70.86
2025-11-15 21:00:00 | 68.46 | 0 | 0 | 0 | 65 | 68.46 | 68.46
2025-11-15 22:00:00 | 62.4 | 0 | 0 | 0 | 65 | 62.4 | 62.4
2025-11-15 23:00:00 | 54.36 | 0 | 0 | 0 | 65 | 54.36 | 54.36
2025-11-16 00:00:00 | 53.88 | 0 | 0 | 0 | 65 | 53.88 | 53.88
2025-11-16 01:00:00 | 53.04 | 0 | 0 | 0 | 65 | 53.04 | 53.04
2025-11-16 02:00:00 | 54.12 | 0 | 0 | 0 | 65 | 54.12 | 54.12
2025-11-16 03:00:00 | 53.7 | 0 | 0 | 0 | 65 | 53.7 | 53.7
2025-11-16 04:00:00 | 53.1 | 0 | 0 | 0 | 65 | 53.1 | 53.1
2025-11-16 05:00:00 | 53.34 | 0 | 0 | 0 | 65 | 53.34 | 53.34
2025-11-16 06:00:00 | 53.28 | 0 | 0 | 0 | 65 | 53.28 | 53.28
2025-11-16 07:00:00 | 52.68 | 0.57823 | 0 | 0 | 65 | 52.1018 | 52.1018
2025-11-16 08:00:00 | 51 | 3.6164 | 0 | 0 | 65 | 47.3836 | 47.3836
2025-11-16 09:00:00 | 68.58 | 6.0971 | 0 | 0 | 65 | 62.4829 | 62.4829
2025-11-16 10:00:00 | 73.2 | 7.8512 | 0 | 0 | 65 | 65.3488 | 65.3488
2025-11-16 11:00:00 | 73.14 | 8.7592 | 0 | 0 | 65 | 64.3808 | 64.3808
2025-11-16 12:00:00 | 71.34 | 8.7592 | 0 | 0 | 65 | 62.5808 | 62.5808
2025-11-16 13:00:00 | 68.88 | 7.8512 | 0 | 0 | 65 | 61.0288 | 61.0288
2025-11-16 14:00:00 | 69.24 | 6.0971 | 0 | 0 | 65 | 63.1429 | 63.1429
2025-11-16 15:00:00 | 65.7 | 3.6164 | 75 | 0 | 131 | 137.0836 | 62.0836
2025-11-16 16:00:00 | 61.38 | 0.57823 | 51.4789 | 0 | 176.3014 | 112.2806 | 60.8018
2025-11-16 17:00:00 | 58.62 | 0 | 0 | 0 | 176.3014 | 58.62 | 58.62
2025-11-16 18:00:00 | 55.86 | 0 | 0 | 0 | 176.3014 | 55.86 | 55.86
2025-11-16 19:00:00 | 55.8 | 0 | 0 | 0 | 176.3014 | 55.8 | 55.8
2025-11-16 20:00:00 | 56.4 | 0 | 0 | 0 | 176.3014 | 56.4 | 56.4
2025-11-16 21:00:00 | 55.14 | 0 | 0 | 0 | 176.3014 | 55.14 | 55.14
2025-11-16 22:00:00 | 53.88 | 0 | 0 | 0 | 176.3014 | 53.88 | 53.88
2025-11-16 23:00:00 | 52.26 | 0 | 0 | 0 | 176.3014 | 52.26 | 52.26
2025-11-17 00:00:00 | 43.62 | 0 | 0 | 0 | 176.3014 | 43.62 | 43.62
2025-11-17 01:00:00 | 37.86 | 0 | 75 | 0 | 242.3014 | 112.86 | 37.86
2025-11-17 02:00:00 | 36.66 | 0 | 75 | 0 | 308.3014 | 111.66 | 36.66
2025-11-17 03:00:00 | 40.32 | 0 | 75 | 0 | 374.3014 | 115.32 | 40.32
2025-11-17 04:00:00 | 37.5 | 0 | 75 | 0 | 440.3014 | 112.5 | 37.5
2025-11-17 05:00:00 | 40.56 | 0 | 75 | 0 | 506.3014 | 115.56 | 40.56
2025-11-17 06:00:00 | 37.02 | 0 | 75 | 0 | 572.3014 | 112.02 | 37.02
2025-11-17 07:00:00 | 41.22 | 0.5203 | 0 | 40.6997 | 531.6017 | -3.5527e-14 | 40.6997
2025-11-17 08:00:00 | 38.76 | 3.5543 | 0 | 35.2057 | 496.396 | -7.1054e-15 | 35.2057
2025-11-17 09:00:00 | 43.68 | 6.0315 | 0 | 37.6485 | 458.7475 | -4.2633e-14 | 37.6485
2025-11-17 10:00:00 | 43.56 | 7.7832 | 0 | 35.7768 | 422.9707 | -7.1054e-15 | 35.7768
2025-11-17 11:00:00 | 48.12 | 8.6899 | 0 | 39.4301 | 383.5407 | -2.8422e-14 | 39.4301
2025-11-17 12:00:00 | 50.1 | 8.6899 | 0 | 41.4101 | 342.1306 | -2.1316e-14 | 41.4101
2025-11-17 13:00:00 | 48.96 | 7.7832 | 0 | 41.1768 | 300.9539 | -1.4211e-14 | 41.1768
2025-11-17 14:00:00 | 48.9 | 6.0315 | 0 | 42.8685 | 258.0854 | -4.2633e-14 | 42.8685
2025-11-17 15:00:00 | 48.12 | 3.5543 | 0 | 44.5657 | 213.5197 | -7.1054e-15 | 44.5657
2025-11-17 16:00:00 | 47.04 | 0.5203 | 0 | 46.5197 | 167 | -3.5527e-14 | 46.5197
2025-11-17 17:00:00 | 50.58 | 0 | 0 | 50.58 | 116.42 | 0 | 50.58
2025-11-17 18:00:00 | 51.42 | 0 | 0 | 51.42 | 65 | 0 | 51.42
2025-11-17 19:00:00 | 34.56 | 0 | 75 | 0 | 131 | 109.56 | 34.56
2025-11-17 20:00:00 | 36.48 | 0 | 73.5355 | 0 | 195.7113 | 110.0155 | 36.48
2025-11-17 21:00:00 | 34.62 | 0 | 0 | 0 | 195.7113 | 34.62 | 34.62
2025-11-17 22:00:00 | 28.2 | 0 | 0 | 0 | 195.7113 | 28.2 | 28.2
2025-11-17 23:00:00 | 23.88 | 0 | 0 | 0 | 195.7113 | 23.88 | 23.88
2025-11-18 00:00:00 | 22.08 | 0 | 0 | 0 | 195.7113 | 22.08 | 22.08
2025-11-18 01:00:00 | 21.72 | 0 | 0 | 0 | 195.7113 | 21.72 | 21.72
2025-11-18 02:00:00 | 19.56 | 0 | 0 | 0 | 195.7113 | 19.56 | 19.56
2025-11-18 03:00:00 | 20.04 | 0 | 75 | 0 | 261.7113 | 95.04 | 20.04
2025-11-18 04:00:00 | 18.9 | 0 | 75 | 0 | 327.7113 | 93.9 | 18.9
2025-11-18 05:00:00 | 18.78 | 0 | 75 | 0 | 393.7113 | 93.78 | 18.78
2025-11-18 06:00:00 | 20.28 | 0 | 75 | 0 | 459.7113 | 95.28 | 20.28
2025-11-18 07:00:00 | 18.72 | 0.46387 | 0 | 18.2561 | 441.4551 | 3.5527e-15 | 18.2561
2025-11-18 08:00:00 | 18.9 | 3.4937 | 0 | 15.4063 | 426.0489 | -2.3093e-14 | 15.4063
2025-11-18 09:00:00 | 19.5 | 5.9676 | 0 | 13.5324 | 412.5164 | -3.3751e-14 | 13.5324
2025-11-18 10:00:00 | 27.84 | 7.7169 | 0 | 20.1231 | 392.3933 | -1.4211e-14 | 20.1231
2025-11-18 11:00:00 | 34.74 | 8.6224 | 0 | 26.1176 | 366.2756 | -2.1316e-14 | 26.1176
2025-11-18 12:00:00 | 34.8 | 8.6224 | 0 | 26.1776 | 340.098 | -2.4869e-14 | 26.1776
2025-11-18 13:00:00 | 35.4 | 7.7169 | 0 | 27.6831 | 312.4148 | -1.0658e-14 | 27.6831
2025-11-18 14:00:00 | 45.54 | 5.9676 | 0 | 39.5724 | 272.8424 | -3.5527e-14 | 39.5724
2025-11-18 15:00:00 | 57.78 | 3.4937 | 0 | 54.2863 | 218.5561 | -2.1316e-14 | 54.2863
2025-11-18 16:00:00 | 56.4 | 0.46387 | 0 | 55.9361 | 162.62 | 0 | 55.9361
2025-11-18 17:00:00 | 49.02 | 0 | 0 | 49.02 | 113.6 | 0 | 49.02
2025-11-18 18:00:00 | 48.6 | 0 | 0 | 48.6 | 65 | 0 | 48.6
2025-11-18 19:00:00 | 50.28 | 0 | 75 | 0 | 131 | 125.28 | 50.28
2025-11-18 20:00:00 | 57.66 | 0 | 51.3238 | 0 | 176.165 | 108.9838 | 57.66
2025-11-18 21:00:00 | 58.14 | 0 | 0 | 0 | 176.165 | 58.14 | 58.14
2025-11-18 22:00:00 | 43.32 | 0 | 0 | 0 | 176.165 | 43.32 | 43.32
2025-11-18 23:00:00 | 28.74 | 0 | 0 | 0 | 176.165 | 28.74 | 28.74
2025-11-19 00:00:00 | 27.72 | 0 | 0 | 0 | 176.165 | 27.72 | 27.72
2025-11-19 01:00:00 | 28.08 | 0 | 0 | 0 | 176.165 | 28.08 | 28.08
2025-11-19 02:00:00 | 31.8 | 0 | 75 | 0 | 242.165 | 106.8 | 31.8
2025-11-19 03:00:00 | 37.26 | 0 | 75 | 0 | 308.165 | 112.26 | 37.26
2025-11-19 04:00:00 | 35.58 | 0 | 75 | 0 | 374.165 | 110.58 | 35.58
2025-11-19 05:00:00 | 36.42 | 0 | 75 | 0 | 440.165 | 111.42 | 36.42
2025-11-19 06:00:00 | 18.96 | 0 | 75 | 0 | 506.165 | 93.96 | 18.96
2025-11-19 07:00:00 | 20.58 | 0.40894 | 0 | 20.1711 | 485.9939 | -1.7764e-14 | 20.1711
2025-11-19 08:00:00 | 28.68 | 3.4347 | 0 | 25.2453 | 460.7486 | -7.1054e-15 | 25.2453
2025-11-19 09:00:00 | 43.62 | 5.9052 | 0 | 37.7148 | 423.0339 | -7.1054e-15 | 37.7148
2025-11-19 10:00:00 | 42.6 | 7.6522 | 0 | 34.9478 | 388.086 | 3.5527e-14 | 34.9478
2025-11-19 11:00:00 | 41.34 | 8.5564 | 0 | 32.7836 | 355.3025 | 7.1054e-15 | 32.7836
2025-11-19 12:00:00 | 37.32 | 8.5564 | 0 | 28.7636 | 326.5389 | 3.5527e-15 | 28.7636
2025-11-19 13:00:00 | 38.58 | 7.6522 | 0 | 30.9278 | 295.6111 | 2.8422e-14 | 30.9278
2025-11-19 14:00:00 | 40.8 | 5.9052 | 0 | 34.8948 | 260.7163 | -7.1054e-15 | 34.8948
2025-11-19 15:00:00 | 50.94 | 3.4347 | 0 | 47.5053 | 213.2111 | -1.4211e-14 | 47.5053
2025-11-19 16:00:00 | 55.86 | 0.40894 | 0 | 55.4511 | 157.76 | -1.4211e-14 | 55.4511
2025-11-19 17:00:00 | 47.76 | 0 | 0 | 47.76 | 110 | 0 | 47.76
2025-11-19 18:00:00 | 45 | 0 | 0 | 45 | 65 | 0 | 45
2025-11-19 19:00:00 | 42.6 | 0 | 75 | 0 | 131 | 117.6 | 42.6
2025-11-19 20:00:00 | 48.9 | 0 | 39.3889 | 0 | 165.6622 | 88.2889 | 48.9
2025-11-19 21:00:00 | 49.2 | 0 | 0 | 0 | 165.6622 | 49.2 | 49.2
2025-11-19 22:00:00 | 38.94 | 0 | 0 | 0 | 165.6622 | 38.94 | 38.94
2025-11-19 23:00:00 | 22.26 | 0 | 0 | 0 | 165.6622 | 22.26 | 22.26
2025-11-20 00:00:00 | 20.28 | 0 | 0 | 0 | 165.6622 | 20.28 | 20.28
2025-11-20 01:00:00 | 19.2 | 0 | 0 | 0 | 165.6622 | 19.2 | 19.2
2025-11-20 02:00:00 | 34.44 | 0 | 75 | 0 | 231.6622 | 109.44 | 34.44
2025-11-20 03:00:00 | 34.98 | 0 | 75 | 0 | 297.6622 | 109.98 | 34.98
2025-11-20 04:00:00 | 35.52 | 0 | 75 | 0 | 363.6622 | 110.52 | 35.52
2025-11-20 05:00:00 | 35.22 | 0 | 75 | 0 | 429.6622 | 110.22 | 35.22
2025-11-20 06:00:00 | 29.7 | 0 | 75 | 0 | 495.6622 | 104.7 | 29.7
2025-11-20 07:00:00 | 19.38 | 0.35554 | 0 | 19.0245 | 476.6378 | 2.4869e-14 | 19.0245
2025-11-20 08:00:00 | 19.44 | 3.3773 | 0 | 16.0627 | 460.5751 | -3.5527e-15 | 16.0627
2025-11-20 09:00:00 | 19.32 | 5.8446 | 0 | 13.4754 | 447.0997 | -2.6645e-14 | 13.4754
2025-11-20 10:00:00 | 33.66 | 7.5892 | 0 | 26.0708 | 421.0288 | -3.1974e-14 | 26.0708
2025-11-20 11:00:00 | 38.52 | 8.4923 | 0 | 30.0277 | 391.0011 | 0 | 30.0277
2025-11-20 12:00:00 | 39.3 | 8.4923 | 0 | 30.8077 | 360.1934 | -7.1054e-15 | 30.8077
2025-11-20 13:00:00 | 46.5 | 7.5892 | 0 | 38.9108 | 321.2826 | -2.8422e-14 | 38.9108
2025-11-20 14:00:00 | 49.08 | 5.8446 | 0 | 43.2354 | 278.0471 | -2.8422e-14 | 43.2354
2025-11-20 15:00:00 | 48.06 | 3.3773 | 0 | 44.6827 | 233.3645 | 0 | 44.6827
2025-11-20 16:00:00 | 59.34 | 0.35554 | 0 | 58.9845 | 174.38 | 2.1316e-14 | 58.9845
2025-11-20 17:00:00 | 57.78 | 0 | 0 | 57.78 | 116.6 | 0 | 57.78
2025-11-20 18:00:00 | 51.6 | 0 | 0 | 51.6 | 65 | 0 | 51.6
2025-11-20 19:00:00 | 47.58 | 0 | 75 | 0 | 131 | 122.58 | 47.58
2025-11-20 20:00:00 | 47.46 | 0 | 75 | 0 | 197 | 122.46 | 47.46
2025-11-20 21:00:00 | 47.58 | 0 | 60.2305 | 0 | 250.0028 | 107.8105 | 47.58
2025-11-20 22:00:00 | 49.44 | 0 | 0 | 0 | 250.0028 | 49.44 | 49.44
2025-11-20 23:00:00 | 42.48 | 0 | 0 | 0 | 250.0028 | 42.48 | 42.48
2025-11-21 00:00:00 | 40.02 | 0 | 0 | 0 | 250.0028 | 40.02 | 40.02
2025-11-21 01:00:00 | 40.02 | 0 | 0 | 0 | 250.0028 | 40.02 | 40.02
2025-11-21 02:00:00 | 38.52 | 0 | 75 | 0 | 316.0028 | 113.52 | 38.52
2025-11-21 03:00:00 | 39.12 | 0 | 75 | 0 | 382.0028 | 114.12 | 39.12
2025-11-21 04:00:00 | 39.48 | 0 | 75 | 0 | 448.0028 | 114.48 | 39.48
2025-11-21 05:00:00 | 20.46 | 0 | 75 | 0 | 514.0028 | 95.46 | 20.46
2025-11-21 06:00:00 | 22.98 | 0 | 75 | 0 | 580.0028 | 97.98 | 22.98
2025-11-21 07:00:00 | 35.46 | 0.30369 | 0 | 35.1563 | 544.8465 | 2.8422e-14 | 35.1563
2025-11-21 08:00:00 | 36.48 | 3.3215 | 0 | 33.1585 | 511.688 | -2.8422e-14 | 33.1585
2025-11-21 09:00:00 | 36.06 | 5.7856 | 0 | 30.2744 | 481.4136 | -2.4869e-14 | 30.2744
2025-11-21 10:00:00 | 44.58 | 7.5279 | 0 | 37.0521 | 444.3616 | 3.5527e-14 | 37.0521
2025-11-21 11:00:00 | 56.34 | 8.4298 | 0 | 47.9102 | 396.4514 | -4.2633e-14 | 47.9102
2025-11-21 12:00:00 | 52.14 | 8.4298 | 0 | 43.7102 | 352.7413 | -4.2633e-14 | 43.7102
2025-11-21 13:00:00 | 55.38 | 7.5279 | 0 | 47.8521 | 304.8892 | 4.2633e-14 | 47.8521
2025-11-21 14:00:00 | 54.9 | 5.7856 | 0 | 49.1144 | 255.7748 | -2.8422e-14 | 49.1144
2025-11-21 15:00:00 | 47.16 | 3.3215 | 0 | 43.8385 | 211.9363 | -3.5527e-14 | 43.8385
2025-11-21 16:00:00 | 50.4 | 0.30369 | 0 | 50.0963 | 161.84 | 2.8422e-14 | 50.0963
2025-11-21 17:00:00 | 52.8 | 0 | 0 | 52.8 | 109.04 | 0 | 52.8
2025-11-21 18:00:00 | 44.04 | 0 | 0 | 44.04 | 65 | 0 | 44.04
2025-11-21 19:00:00 | 39.72 | 0 | 0 | 0 | 65 | 39.72 | 39.72
2025-11-21 20:00:00 | 37.98 | 0 | 0 | 0 | 65 | 37.98 | 37.98
2025-11-21 21:00:00 | 35.94 | 0 | 0 | 0 | 65 | 35.94 | 35.94
2025-11-21 22:00:00 | 36.72 | 0 | 0 | 0 | 65 | 36.72 | 36.72
2025-11-21 23:00:00 | 36.18 | 0 | 0 | 0 | 65 | 36.18 | 36.18
2025-11-22 00:00:00 | 40.32 | 0 | 0 | 0 | 65 | 40.32 | 40.32
2025-11-22 01:00:00 | 50.4 | 0 | 0 | 0 | 65 | 50.4 | 50.4
2025-11-22 02:00:00 | 50.34 | 0 | 0 | 0 | 65 | 50.34 | 50.34
2025-11-22 03:00:00 | 51.06 | 0 | 0 | 0 | 65 | 51.06 | 51.06
2025-11-22 04:00:00 | 50.04 | 0 | 0 | 0 | 65 | 50.04 | 50.04
2025-11-22 05:00:00 | 34.14 | 0 | 0 | 0 | 65 | 34.14 | 34.14
2025-11-22 06:00:00 | 33.72 | 0 | 0 | 0 | 65 | 33.72 | 33.72
2025-11-22 07:00:00 | 33.72 | 0.25339 | 0 | 0 | 65 | 33.4666 | 33.4666
2025-11-22 08:00:00 | 33.78 | 3.2674 | 0 | 0 | 65 | 30.5126 | 30.5126
2025-11-22 09:00:00 | 35.16 | 5.7283 | 0 | 0 | 65 | 29.4317 | 29.4317
2025-11-22 10:00:00 | 35.28 | 7.4685 | 0 | 0 | 65 | 27.8115 | 27.8115
2025-11-22 11:00:00 | 36.36 | 8.3692 | 0 | 0 | 65 | 27.9908 | 27.9908
2025-11-22 12:00:00 | 44.46 | 8.3692 | 0 | 0 | 65 | 36.0908 | 36.0908
2025-11-22 13:00:00 | 51.54 | 7.4685 | 0 | 0 | 65 | 44.0715 | 44.0715
2025-11-22 14:00:00 | 48.24 | 5.7283 | 0 | 0 | 65 | 42.5117 | 42.5117
2025-11-22 15:00:00 | 53.58 | 3.2674 | 0 | 0 | 65 | 50.3126 | 50.3126
2025-11-22 16:00:00 | 50.34 | 0.25339 | 0 | 0 | 65 | 50.0866 | 50.0866
2025-11-22 17:00:00 | 43.2 | 0 | 0 | 0 | 65 | 43.2 | 43.2
2025-11-22 18:00:00 | 43.38 | 0 | 0 | 0 | 65 | 43.38 | 43.38
2025-11-22 19:00:00 | 40.98 | 0 | 0 | 0 | 65 | 40.98 | 40.98
2025-11-22 20:00:00 | 38.94 | 0 | 0 | 0 | 65 | 38.94 | 38.94
2025-11-22 21:00:00 | 40.32 | 0 | 0 | 0 | 65 | 40.32 | 40.32
2025-11-22 22:00:00 | 24.84 | 0 | 0 | 0 | 65 | 24.84 | 24.84
2025-11-22 23:00:00 | 19.2 | 0 | 0 | 0 | 65 | 19.2 | 19.2
2025-11-23 00:00:00 | 23.46 | 0 | 0 | 0 | 65 | 23.46 | 23.46
2025-11-23 01:00:00 | 36.3 | 0 | 0 | 0 | 65 | 36.3 | 36.3
2025-11-23 02:00:00 | 35.22 | 0 | 0 | 0 | 65 | 35.22 | 35.22
2025-11-23 03:00:00 | 36 | 0 | 0 | 0 | 65 | 36 | 36
2025-11-23 04:00:00 | 35.22 | 0 | 0 | 0 | 65 | 35.22 | 35.22
2025-11-23 05:00:00 | 35.88 | 0 | 0 | 0 | 65 | 35.88 | 35.88
2025-11-23 06:00:00 | 35.22 | 0 | 0 | 0 | 65 | 35.22 | 35.22
2025-11-23 07:00:00 | 35.4 | 0.20467 | 0 | 0 | 65 | 35.1953 | 35.1953
2025-11-23 08:00:00 | 44.76 | 3.2149 | 0 | 0 | 65 | 41.5451 | 41.5451
2025-11-23 09:00:00 | 48.96 | 5.6728 | 0 | 0 | 65 | 43.2872 | 43.2872
2025-11-23 10:00:00 | 53.04 | 7.4107 | 0 | 0 | 65 | 45.6293 | 45.6293
2025-11-23 11:00:00 | 45.42 | 8.3104 | 0 | 0 | 65 | 37.1096 | 37.1096
2025-11-23 12:00:00 | 42.6 | 8.3104 | 0 | 0 | 65 | 34.2896 | 34.2896
2025-11-23 13:00:00 | 44.1 | 7.4107 | 0 | 0 | 65 | 36.6893 | 36.6893
2025-11-23 14:00:00 | 57.3 | 5.6728 | 0 | 0 | 65 | 51.6272 | 51.6272
2025-11-23 15:00:00 | 54.66 | 3.2149 | 0 | 0 | 65 | 51.4451 | 51.4451
2025-11-23 16:00:00 | 51.84 | 0.20467 | 65.6388 | 0 | 122.7622 | 117.2741 | 51.6353
2025-11-23 17:00:00 | 37.02 | 0 | 0 | 0 | 122.7622 | 37.02 | 37.02
2025-11-23 18:00:00 | 35.76 | 0 | 0 | 0 | 122.7622 | 35.76 | 35.76
2025-11-23 19:00:00 | 36 | 0 | 0 | 0 | 122.7622 | 36 | 36
2025-11-23 20:00:00 | 36.3 | 0 | 0 | 0 | 122.7622 | 36.3 | 36.3
2025-11-23 21:00:00 | 35.52 | 0 | 0 | 0 | 122.7622 | 35.52 | 35.52
2025-11-23 22:00:00 | 35.88 | 0 | 0 | 0 | 122.7622 | 35.88 | 35.88
2025-11-23 23:00:00 | 36.3 | 0 | 0 | 0 | 122.7622 | 36.3 | 36.3
2025-11-24 00:00:00 | 35.64 | 0 | 0 | 0 | 122.7622 | 35.64 | 35.64
2025-11-24 01:00:00 | 35.76 | 0 | 0 | 0 | 122.7622 | 35.76 | 35.76
2025-11-24 02:00:00 | 36.54 | 0 | 75 | 0 | 188.7622 | 111.54 | 36.54
2025-11-24 03:00:00 | 36.06 | 0 | 75 | 0 | 254.7622 | 111.06 | 36.06
2025-11-24 04:00:00 | 36.24 | 0 | 75 | 0 | 320.7622 | 111.24 | 36.24
2025-11-24 05:00:00 | 35.58 | 0 | 75 | 0 | 386.7622 | 110.58 | 35.58
2025-11-24 06:00:00 | 25.44 | 0 | 75 | 0 | 452.7622 | 100.44 | 25.44
2025-11-24 07:00:00 | 19.98 | 0.15755 | 0 | 19.8225 | 432.9397 | -4.2633e-14 | 19.8225
2025-11-24 08:00:00 | 19.56 | 3.1641 | 0 | 16.3959 | 416.5438 | 3.908e-14 | 16.3959
2025-11-24 09:00:00 | 24.18 | 5.619 | 0 | 18.561 | 397.9828 | 1.7764e-14 | 18.561
2025-11-24 10:00:00 | 37.26 | 7.3549 | 0 | 29.9051 | 368.0777 | -2.1316e-14 | 29.9051
2025-11-24 11:00:00 | 35.16 | 8.2534 | 0 | 26.9066 | 341.1711 | -3.5527e-14 | 26.9066
2025-11-24 12:00:00 | 35.88 | 8.2534 | 0 | 27.6266 | 313.5445 | -2.8422e-14 | 27.6266
2025-11-24 13:00:00 | 37.74 | 7.3549 | 0 | 30.3851 | 283.1593 | -1.7764e-14 | 30.3851
2025-11-24 14:00:00 | 41.22 | 5.619 | 0 | 35.601 | 247.5583 | 1.4211e-14 | 35.601
2025-11-24 15:00:00 | 41.82 | 3.1641 | 0 | 38.6559 | 208.9025 | 4.2633e-14 | 38.6559
2025-11-24 16:00:00 | 39.24 | 0.15755 | 0 | 39.0825 | 169.82 | -4.2633e-14 | 39.0825
2025-11-24 17:00:00 | 47.64 | 0 | 0 | 47.64 | 122.18 | 0 | 47.64
2025-11-24 18:00:00 | 57.18 | 0 | 0 | 57.18 | 65 | 0 | 57.18
2025-11-24 19:00:00 | 49.38 | 0 | 67.4474 | 0 | 124.3537 | 116.8274 | 49.38
2025-11-24 20:00:00 | 54.48 | 0 | 0 | 0 | 124.3537 | 54.48 | 54.48
2025-11-24 21:00:00 | 52.86 | 0 | 0 | 0 | 124.3537 | 52.86 | 52.86
2025-11-24 22:00:00 | 52.98 | 0 | 0 | 0 | 124.3537 | 52.98 | 52.98
2025-11-24 23:00:00 | 50.04 | 0 | 0 | 0 | 124.3537 | 50.04 | 50.04
2025-11-25 00:00:00 | 40.26 | 0 | 0 | 0 | 124.3537 | 40.26 | 40.26
2025-11-25 01:00:00 | 40.2 | 0 | 0 | 0 | 124.3537 | 40.2 | 40.2
2025-11-25 02:00:00 | 39.12 | 0 | 75 | 0 | 190.3537 | 114.12 | 39.12
2025-11-25 03:00:00 | 39 | 0 | 75 | 0 | 256.3537 | 114 | 39
2025-11-25 04:00:00 | 39.36 | 0 | 75 | 0 | 322.3537 | 114.36 | 39.36
2025-11-25 05:00:00 | 19.32 | 0 | 75 | 0 | 388.3537 | 94.32 | 19.32
2025-11-25 06:00:00 | 20.28 | 0 | 75 | 0 | 454.3537 | 95.28 | 20.28
2025-11-25 07:00:00 | 36.3 | 0.11202 | 0 | 36.188 | 418.1658 | -2.1316e-14 | 36.188
2025-11-25 08:00:00 | 36 | 3.115 | 0 | 32.885 | 385.2808 | 3.5527e-14 | 32.885
2025-11-25 09:00:00 | 36.42 | 5.567 | 0 | 30.853 | 354.4278 | 2.8422e-14 | 30.853
2025-11-25 10:00:00 | 36.48 | 7.3008 | 0 | 29.1792 | 325.2486 | -7.1054e-15 | 29.1792
2025-11-25 11:00:00 | 36.48 | 8.1983 | 0 | 28.2817 | 296.9669 | 0 | 28.2817
2025-11-25 12:00:00 | 36.78 | 8.1983 | 0 | 28.5817 | 268.3851 | 3.5527e-15 | 28.5817
2025-11-25 13:00:00 | 36 | 7.3008 | 0 | 28.6992 | 239.6859 | -3.5527e-15 | 28.6992
2025-11-25 14:00:00 | 37.38 | 5.567 | 0 | 31.813 | 207.8729 | 2.8422e-14 | 31.813
2025-11-25 15:00:00 | 36 | 3.115 | 0 | 32.885 | 174.988 | 3.5527e-14 | 32.885
2025-11-25 16:00:00 | 35.4 | 0.11202 | 0 | 35.288 | 139.7 | -2.1316e-14 | 35.288
2025-11-25 17:00:00 | 35.58 | 0 | 0 | 35.58 | 104.12 | 0 | 35.58
2025-11-25 18:00:00 | 39.12 | 0 | 0 | 39.12 | 65 | 0 | 39.12
2025-11-25 19:00:00 | 52.08 | 0 | 75 | 0 | 131 | 127.08 | 52.08
2025-11-25 20:00:00 | 56.94 | 0 | 3.8495 | 0 | 134.3875 | 60.7895 | 56.94
2025-11-25 21:00:00 | 60.48 | 0 | 0 | 0 | 134.3875 | 60.48 | 60.48
2025-11-25 22:00:00 | 53.94 | 0 | 0 | 0 | 134.3875 | 53.94 | 53.94
2025-11-25 23:00:00 | 45.6 | 0 | 0 | 0 | 134.3875 | 45.6 | 45.6
2025-11-26 00:00:00 | 43.08 | 0 | 0 | 0 | 134.3875 | 43.08 | 43.08
2025-11-26 01:00:00 | 42.72 | 0 | 75 | 0 | 200.3875 | 117.72 | 42.72
2025-11-26 02:00:00 | 41.82 | 0 | 75 | 0 | 266.3875 | 116.82 | 41.82
2025-11-26 03:00:00 | 39.9 | 0 | 75 | 0 | 332.3875 | 114.9 | 39.9
2025-11-26 04:00:00 | 40.5 | 0 | 75 | 0 | 398.3875 | 115.5 | 40.5
2025-11-26 05:00:00 | 40.68 | 0 | 75 | 0 | 464.3875 | 115.68 | 40.68
2025-11-26 06:00:00 | 40.2 | 0 | 75 | 0 | 530.3875 | 115.2 | 40.2
2025-11-26 07:00:00 | 40.44 | 0.068123 | 0 | 40.3719 | 490.0156 | -2.8422e-14 | 40.3719
2025-11-26 08:00:00 | 49.26 | 3.0677 | 0 | 46.1923 | 443.8233 | 3.5527e-14 | 46.1923
2025-11-26 09:00:00 | 48.84 | 5.5168 | 0 | 43.3232 | 400.5001 | 1.4211e-14 | 43.3232
2025-11-26 10:00:00 | 48.6 | 7.2486 | 0 | 41.3514 | 359.1487 | -2.8422e-14 | 41.3514
2025-11-26 11:00:00 | 51.9 | 8.145 | 0 | 43.755 | 315.3938 | -2.1316e-14 | 43.755
2025-11-26 12:00:00 | 45.78 | 8.145 | 0 | 37.635 | 277.7588 | -2.1316e-14 | 37.635
2025-11-26 13:00:00 | 38.58 | 7.2486 | 0 | 31.3314 | 246.4274 | -2.8422e-14 | 31.3314
2025-11-26 14:00:00 | 37.5 | 5.5168 | 0 | 31.9832 | 214.4442 | 1.0658e-14 | 31.9832
2025-11-26 15:00:00 | 34.92 | 3.0677 | 0 | 31.8523 | 182.5919 | 4.6185e-14 | 31.8523
2025-11-26 16:00:00 | 34.92 | 0.068123 | 0 | 34.8519 | 147.74 | -2.8422e-14 | 34.8519
2025-11-26 17:00:00 | 36.18 | 0 | 0 | 36.18 | 111.56 | 0 | 36.18
2025-11-26 18:00:00 | 46.56 | 0 | 0 | 46.56 | 65 | 0 | 46.56
2025-11-26 19:00:00 | 44.64 | 0 | 0 | 0 | 65 | 44.64 | 44.64
2025-11-26 20:00:00 | 51.72 | 0 | 0 | 0 | 65 | 51.72 | 51.72
2025-11-26 21:00:00 | 49.98 | 0 | 0 | 0 | 65 | 49.98 | 49.98
2025-11-26 22:00:00 | 45 | 0 | 0 | 0 | 65 | 45 | 45
2025-11-26 23:00:00 | 38.28 | 0 | 0 | 0 | 65 | 38.28 | 38.28
2025-11-27 00:00:00 | 37.8 | 0 | 0 | 0 | 65 | 37.8 | 37.8
2025-11-27 01:00:00 | 35.46 | 0 | 0 | 0 | 65 | 35.46 | 35.46
2025-11-27 02:00:00 | 35.16 | 0 | 0 | 0 | 65 | 35.16 | 35.16
2025-11-27 03:00:00 | 35.7 | 0 | 0 | 0 | 65 | 35.7 | 35.7
2025-11-27 04:00:00 | 19.2 | 0 | 0 | 0 | 65 | 19.2 | 19.2
2025-11-27 05:00:00 | 19.8 | 0 | 0 | 0 | 65 | 19.8 | 19.8
2025-11-27 06:00:00 | 19.32 | 0 | 0 | 0 | 65 | 19.32 | 19.32
2025-11-27 07:00:00 | 28.68 | 0.025856 | 0 | 0 | 65 | 28.6541 | 28.6541
2025-11-27 08:00:00 | 36.84 | 3.022 | 0 | 0 | 65 | 33.818 | 33.818
2025-11-27 09:00:00 | 38.34 | 5.4684 | 0 | 0 | 65 | 32.8716 | 32.8716
2025-11-27 10:00:00 | 34.62 | 7.1983 | 0 | 0 | 65 | 27.4217 | 27.4217
2025-11-27 11:00:00 | 35.22 | 8.0937 | 0 | 0 | 65 | 27.1263 | 27.1263
2025-11-27 12:00:00 | 44.58 | 8.0937 | 0 | 0 | 65 | 36.4863 | 36.4863
2025-11-27 13:00:00 | 43.92 | 7.1983 | 0 | 0 | 65 | 36.7217 | 36.7217
2025-11-27 14:00:00 | 42.9 | 5.4684 | 0 | 0 | 65 | 37.4316 | 37.4316
2025-11-27 15:00:00 | 41.52 | 3.022 | 0 | 0 | 65 | 38.498 | 38.498
2025-11-27 16:00:00 | 36.54 | 0.025856 | 75 | 0 | 131 | 111.5141 | 36.5141
2025-11-27 17:00:00 | 36 | 0 | 53.8312 | 0 | 178.3715 | 89.8312 | 36
2025-11-27 18:00:00 | 20.82 | 0 | 0 | 0 | 178.3715 | 20.82 | 20.82
2025-11-27 19:00:00 | 22.74 | 0 | 0 | 0 | 178.3715 | 22.74 | 22.74
2025-11-27 20:00:00 | 18.96 | 0 | 0 | 0 | 178.3715 | 18.96 | 18.96
2025-11-27 21:00:00 | 32.04 | 0 | 0 | 0 | 178.3715 | 32.04 | 32.04
2025-11-27 22:00:00 | 35.94 | 0 | 0 | 0 | 178.3715 | 35.94 | 35.94
2025-11-27 23:00:00 | 34.8 | 0 | 0 | 0 | 178.3715 | 34.8 | 34.8
2025-11-28 00:00:00 | 35.58 | 0 | 0 | 0 | 178.3715 | 35.58 | 35.58
2025-11-28 01:00:00 | 31.5 | 0 | 0 | 0 | 178.3715 | 31.5 | 31.5
2025-11-28 02:00:00 | 19.38 | 0 | 75 | 0 | 244.3715 | 94.38 | 19.38
2025-11-28 03:00:00 | 19.2 | 0 | 75 | 0 | 310.3715 | 94.2 | 19.2
2025-11-28 04:00:00 | 19.08 | 0 | 75 | 0 | 376.3715 | 94.08 | 19.08
2025-11-28 05:00:00 | 29.58 | 0 | 75 | 0 | 442.3715 | 104.58 | 29.58
2025-11-28 06:00:00 | 36.24 | 0 | 75 | 0 | 508.3715 | 111.24 | 36.24
2025-11-28 07:00:00 | 34.86 | 0 | 0 | 34.86 | 473.5115 | 0 | 34.86
2025-11-28 08:00:00 | 36.96 | 2.9782 | 0 | 33.9818 | 439.5296 | 7.1054e-15 | 33.9818
2025-11-28 09:00:00 | 33.9 | 5.4219 | 0 | 28.4781 | 411.0515 | -4.6185e-14 | 28.4781
2025-11-28 10:00:00 | 19.56 | 7.1499 | 0 | 12.4101 | 398.6414 | -1.2434e-14 | 12.4101
2025-11-28 11:00:00 | 20.16 | 8.0443 | 0 | 12.1157 | 386.5257 | -4.4409e-14 | 12.1157
2025-11-28 12:00:00 | 27.6 | 8.0443 | 0 | 19.5557 | 366.9701 | -4.6185e-14 | 19.5557
2025-11-28 13:00:00 | 39.06 | 7.1499 | 0 | 31.9101 | 335.0599 | -1.0658e-14 | 31.9101
2025-11-28 14:00:00 | 40.92 | 5.4219 | 0 | 35.4981 | 299.5618 | -4.9738e-14 | 35.4981
2025-11-28 15:00:00 | 53.22 | 2.9782 | 0 | 50.2418 | 249.32 | 7.1054e-15 | 50.2418
2025-11-28 16:00:00 | 64.14 | 0 | 0 | 64.14 | 185.18 | 0 | 64.14
2025-11-28 17:00:00 | 63.36 | 0 | 0 | 63.36 | 121.82 | 0 | 63.36
2025-11-28 18:00:00 | 56.82 | 0 | 0 | 56.82 | 65 | 0 | 56.82
2025-11-28 19:00:00 | 54.54 | 0 | 0 | 0 | 65 | 54.54 | 54.54
2025-11-28 20:00:00 | 42 | 0 | 0 | 0 | 65 | 42 | 42
2025-11-28 21:00:00 | 38.94 | 0 | 0 | 0 | 65 | 38.94 | 38.94
2025-11-28 22:00:00 | 35.22 | 0 | 0 | 0 | 65 | 35.22 | 35.22
2025-11-28 23:00:00 | 21.18 | 0 | 0 | 0 | 65 | 21.18 | 21.18
2025-11-29 00:00:00 | 20.46 | 0 | 0 | 0 | 65 | 20.46 | 20.46
2025-11-29 01:00:00 | 28.02 | 0 | 0 | 0 | 65 | 28.02 | 28.02
2025-11-29 02:00:00 | 37.68 | 0 | 0 | 0 | 65 | 37.68 | 37.68
2025-11-29 03:00:00 | 36.72 | 0 | 0 | 0 | 65 | 36.72 | 36.72
2025-11-29 04:00:00 | 33.66 | 0 | 0 | 0 | 65 | 33.66 | 33.66
2025-11-29 05:00:00 | 20.46 | 0 | 0 | 0 | 65 | 20.46 | 20.46
2025-11-29 06:00:00 | 20.16 | 0 | 0 | 0 | 65 | 20.16 | 20.16
2025-11-29 07:00:00 | 20.22 | 0 | 0 | 0 | 65 | 20.22 | 20.22
2025-11-29 08:00:00 | 20.88 | 2.9361 | 0 | 0 | 65 | 17.9439 | 17.9439
2025-11-29 09:00:00 | 34.38 | 5.3772 | 0 | 0 | 65 | 29.0028 | 29.0028
2025-11-29 10:00:00 | 44.82 | 7.1034 | 0 | 0 | 65 | 37.7166 | 37.7166
2025-11-29 11:00:00 | 44.16 | 7.9969 | 0 | 0 | 65 | 36.1631 | 36.1631
2025-11-29 12:00:00 | 41.88 | 7.9969 | 0 | 0 | 65 | 33.8831 | 33.8831
2025-11-29 13:00:00 | 39.36 | 7.1034 | 0 | 0 | 65 | 32.2566 | 32.2566
2025-11-29 14:00:00 | 37.38 | 5.3772 | 0 | 0 | 65 | 32.0028 | 32.0028
2025-11-29 15:00:00 | 44.7 | 2.9361 | 0 | 0 | 65 | 41.7639 | 41.7639
2025-11-29 16:00:00 | 45.54 | 0 | 0 | 0 | 65 | 45.54 | 45.54
2025-11-29 17:00:00 | 38.7 | 0 | 0 | 0 | 65 | 38.7 | 38.7
2025-11-29 18:00:00 | 27.12 | 0 | 0 | 0 | 65 | 27.12 | 27.12
2025-11-29 19:00:00 | 21.96 | 0 | 0 | 0 | 65 | 21.96 | 21.96
2025-11-29 20:00:00 | 20.76 | 0 | 0 | 0 | 65 | 20.76 | 20.76
2025-11-29 21:00:00 | 20.88 | 0 | 0 | 0 | 65 | 20.88 | 20.88
2025-11-29 22:00:00 | 32.82 | 0 | 0 | 0 | 65 | 32.82 | 32.82
2025-11-29 23:00:00 | 38.34 | 0 | 0 | 0 | 65 | 38.34 | 38.34
2025-11-30 00:00:00 | 37.98 | 0 | 0 | 0 | 65 | 37.98 | 37.98
2025-11-30 01:00:00 | 36.42 | 0 | 0 | 0 | 65 | 36.42 | 36.42
2025-11-30 02:00:00 | 22.44 | 0 | 0 | 0 | 65 | 22.44 | 22.44
2025-11-30 03:00:00 | 20.52 | 0 | 0 | 0 | 65 | 20.52 | 20.52
2025-11-30 04:00:00 | 19.86 | 0 | 0 | 0 | 65 | 19.86 | 19.86
2025-11-30 05:00:00 | 21.36 | 0 | 0 | 0 | 65 | 21.36 | 21.36
2025-11-30 06:00:00 | 36.84 | 0 | 0 | 0 | 65 | 36.84 | 36.84
2025-11-30 07:00:00 | 36.6 | 0 | 0 | 0 | 65 | 36.6 | 36.6
2025-11-30 08:00:00 | 42.66 | 2.8957 | 0 | 0 | 65 | 39.7643 | 39.7643
2025-11-30 09:00:00 | 49.02 | 5.3344 | 0 | 0 | 65 | 43.6856 | 43.6856
2025-11-30 10:00:00 | 52.74 | 7.0588 | 0 | 0 | 65 | 45.6812 | 45.6812
2025-11-30 11:00:00 | 46.86 | 7.9515 | 0 | 0 | 65 | 38.9085 | 38.9085
2025-11-30 12:00:00 | 41.88 | 7.9515 | 0 | 0 | 65 | 33.9285 | 33.9285
2025-11-30 13:00:00 | 39.48 | 7.0588 | 0 | 0 | 65 | 32.4212 | 32.4212
2025-11-30 14:00:00 | 38.82 | 5.3344 | 0 | 0 | 65 | 33.4856 | 33.4856
2025-11-30 15:00:00 | 37.02 | 2.8957 | 0 | 0 | 65 | 34.1243 | 34.1243
2025-11-30 16:00:00 | 35.04 | 0 | 0 | 0 | 65 | 35.04 | 35.04
2025-11-30 17:00:00 | 27.96 | 0 | 0 | 0 | 65 | 27.96 | 27.96
2025-11-30 18:00:00 | 19.92 | 0 | 0 | 0 | 65 | 19.92 | 19.92
2025-11-30 19:00:00 | 19.98 | 0 | 70.4545 | 0 | 127 | 90.4345 | 19.98
2025-11-30 20:00:00 | 25.56 | 0 | 75 | 0 | 193 | 100.56 | 25.56
2025-11-30 21:00:00 | 36.54 | 0 | 75 | 0 | 259 | 111.54 | 36.54
2025-11-30 22:00:00 | 35.94 | 0 | 75 | 0 | 325 | 110.94 | 35.94
2025-11-30 23:00:00 | 35.52 | 0 | 0 | 0 | 325 | 35.52 | 35.52
2025-12-01 00:00:00 | 31.86 | 0 | 0 | 0 | 325 | 31.86 | 31.86
2025-12-01 01:00:00 | 20.94 | 0 | 0 | 0 | 325 | 20.94 | 20.94
2025-12-01 02:00:00 | 19.86 | 0 | 0 | 0 | 325 | 19.86 | 19.86
2025-12-01 03:00:00 | 19.98 | 0 | 0 | 0 | 325 | 19.98 | 19.98
2025-12-01 04:00:00 | 20.64 | 0 | 0 | 0 | 325 | 20.64 | 20.64
2025-12-01 05:00:00 | 20.04 | 0 | 75 | 0 | 391 | 95.04 | 20.04
2025-12-01 06:00:00 | 21.42 | 0 | 75 | 0 | 457 | 96.42 | 21.42
2025-12-01 07:00:00 | 22.2 | 0 | 0 | 22.2 | 434.8 | 0 | 22.2
2025-12-01 08:00:00 | 21.6 | 2.381 | 0 | 19.219 | 415.581 | -4.6185e-14 | 19.219
2025-12-01 09:00:00 | 33.36 | 4.4113 | 0 | 28.9487 | 386.6323 | 7.1054e-15 | 28.9487
2025-12-01 10:00:00 | 45.42 | 5.8469 | 0 | 39.5731 | 347.0592 | 0 | 39.5731
2025-12-01 11:00:00 | 46.74 | 6.59 | 0 | 40.15 | 306.9092 | -1.4211e-14 | 40.15
2025-12-01 12:00:00 | 43.38 | 6.59 | 0 | 36.79 | 270.1193 | -1.4211e-14 | 36.79
2025-12-01 13:00:00 | 41.34 | 5.8469 | 0 | 35.4931 | 234.6262 | 0 | 35.4931
2025-12-01 14:00:00 | 38.22 | 4.4113 | 0 | 33.8087 | 200.8174 | 7.1054e-15 | 33.8087
2025-12-01 15:00:00 | 28.2 | 2.381 | 0 | 25.819 | 174.9985 | -4.6185e-14 | 25.819
2025-12-01 16:00:00 | 19.14 | 0 | 0 | 19.14 | 155.8585 | 0 | 19.14
2025-12-01 17:00:00 | 30.06 | 0 | 0 | 30.06 | 125.7985 | 0 | 30.06
2025-12-01 18:00:00 | 32.04 | 0 | 0 | 32.04 | 93.7585 | 0 | 32.04
2025-12-01 19:00:00 | 35.76 | 0 | 42.4839 | 0 | 131.1443 | 78.2439 | 35.76
2025-12-01 20:00:00 | 47.7 | 0 | 0 | 0 | 131.1443 | 47.7 | 47.7
2025-12-01 21:00:00 | 56.76 | 0 | 0 | 0 | 131.1443 | 56.76 | 56.76
2025-12-01 22:00:00 | 36.66 | 0 | 0 | 0 | 131.1443 | 36.66 | 36.66
2025-12-01 23:00:00 | 34.44 | 0 | 0 | 0 | 131.1443 | 34.44 | 34.44
2025-12-02 00:00:00 | 17.88 | 0 | 0 | 0 | 131.1443 | 17.88 | 17.88
2025-12-02 01:00:00 | 18.42 | 0 | 0 | 0 | 131.1443 | 18.42 | 18.42
2025-12-02 02:00:00 | 18.12 | 0 | 75 | 0 | 197.1443 | 93.12 | 18.12
2025-12-02 03:00:00 | 17.76 | 0 | 75 | 0 | 263.1443 | 92.76 | 17.76
2025-12-02 04:00:00 | 18.3 | 0 | 75 | 0 | 329.1443 | 93.3 | 18.3
2025-12-02 05:00:00 | 23.64 | 0 | 75 | 0 | 395.1443 | 98.64 | 23.64
2025-12-02 06:00:00 | 34.26 | 0 | 75 | 0 | 461.1443 | 109.26 | 34.26
2025-12-02 07:00:00 | 33.42 | 0 | 0 | 33.42 | 427.7243 | 0 | 33.42
2025-12-02 08:00:00 | 47.64 | 2.3504 | 0 | 45.2896 | 382.4348 | -1.4211e-14 | 45.2896
2025-12-02 09:00:00 | 51.3 | 4.3788 | 0 | 46.9212 | 335.5136 | 2.1316e-14 | 46.9212
2025-12-02 10:00:00 | 37.26 | 5.8131 | 0 | 31.4469 | 304.0667 | 3.908e-14 | 31.4469
2025-12-02 11:00:00 | 28.38 | 6.5555 | 0 | 21.8245 | 282.2422 | -3.908e-14 | 21.8245
2025-12-02 12:00:00 | 23.82 | 6.5555 | 0 | 17.2645 | 264.9777 | -3.908e-14 | 17.2645
2025-12-02 13:00:00 | 28.44 | 5.8131 | 0 | 22.6269 | 242.3508 | 4.2633e-14 | 22.6269
2025-12-02 14:00:00 | 37.02 | 4.3788 | 0 | 32.6412 | 209.7096 | 2.1316e-14 | 32.6412
2025-12-02 15:00:00 | 39.3 | 2.3504 | 0 | 36.9496 | 172.76 | -1.4211e-14 | 36.9496
2025-12-02 16:00:00 | 36.72 | 0 | 0 | 36.72 | 136.04 | 0 | 36.72
2025-12-02 17:00:00 | 35.34 | 0 | 0 | 35.34 | 100.7 | 0 | 35.34
2025-12-02 18:00:00 | 35.7 | 0 | 0 | 35.7 | 65 | 0 | 35.7
2025-12-02 19:00:00 | 23.64 | 0 | 75 | 0 | 131 | 98.64 | 23.64
2025-12-02 20:00:00 | 25.68 | 0 | 24.5161 | 0 | 152.5742 | 50.1961 | 25.68
2025-12-02 21:00:00 | 28.8 | 0 | 0 | 0 | 152.5742 | 28.8 | 28.8
2025-12-02 22:00:00 | 27.78 | 0 | 0 | 0 | 152.5742 | 27.78 | 27.78
2025-12-02 23:00:00 | 23.1 | 0 | 0 | 0 | 152.5742 | 23.1 | 23.1
2025-12-03 00:00:00 | 22.26 | 0 | 0 | 0 | 152.5742 | 22.26 | 22.26
2025-12-03 01:00:00 | 20.4 | 0 | 0 | 0 | 152.5742 | 20.4 | 20.4
2025-12-03 02:00:00 | 20.04 | 0 | 0 | 0 | 152.5742 | 20.04 | 20.04
2025-12-03 03:00:00 | 19.44 | 0 | 75 | 0 | 218.5742 | 94.44 | 19.44
2025-12-03 04:00:00 | 19.5 | 0 | 75 | 0 | 284.5742 | 94.5 | 19.5
2025-12-03 05:00:00 | 20.88 | 0 | 75 | 0 | 350.5742 | 95.88 | 20.88
2025-12-03 06:00:00 | 21.54 | 0 | 75 | 0 | 416.5742 | 96.54 | 21.54
2025-12-03 07:00:00 | 21.3 | 0 | 0 | 21.3 | 395.2742 | 0 | 21.3
2025-12-03 08:00:00 | 27.54 | 2.3214 | 0 | 25.2186 | 370.0555 | -3.1974e-14 | 25.2186
2025-12-03 09:00:00 | 37.74 | 4.3479 | 0 | 33.3921 | 336.6635 | -3.5527e-14 | 33.3921
2025-12-03 10:00:00 | 46.74 | 5.7809 | 0 | 40.9591 | 295.7044 | 2.8422e-14 | 40.9591
2025-12-03 11:00:00 | 44.28 | 6.5227 | 0 | 37.7573 | 257.9471 | 4.2633e-14 | 37.7573
2025-12-03 12:00:00 | 42.18 | 6.5227 | 0 | 35.6573 | 222.2898 | 4.2633e-14 | 35.6573
2025-12-03 13:00:00 | 36.9 | 5.7809 | 0 | 31.1191 | 191.1707 | 2.4869e-14 | 31.1191
2025-12-03 14:00:00 | 34.92 | 4.3479 | 0 | 30.5721 | 160.5986 | -3.5527e-14 | 30.5721
2025-12-03 15:00:00 | 35.64 | 2.3214 | 0 | 33.3186 | 127.28 | -3.5527e-14 | 33.3186
2025-12-03 16:00:00 | 22.62 | 0 | 0 | 22.62 | 104.66 | 0 | 22.62
2025-12-03 17:00:00 | 19.5 | 0 | 0 | 19.5 | 85.16 | 0 | 19.5
2025-12-03 18:00:00 | 20.16 | 0 | 0 | 20.16 | 65 | 0 | 20.16
2025-12-03 19:00:00 | 30.6 | 0 | 75 | 0 | 131 | 105.6 | 30.6
2025-12-03 20:00:00 | 43.98 | 0 | 11.2169 | 0 | 140.8709 | 55.1969 | 43.98
2025-12-03 21:00:00 | 61.14 | 0 | 0 | 0 | 140.8709 | 61.14 | 61.14
2025-12-03 22:00:00 | 58.8 | 0 | 0 | 0 | 140.8709 | 58.8 | 58.8
2025-12-03 23:00:00 | 44.04 | 0 | 0 | 0 | 140.8709 | 44.04 | 44.04
2025-12-04 00:00:00 | 39.3 | 0 | 0 | 0 | 140.8709 | 39.3 | 39.3
2025-12-04 01:00:00 | 19.56 | 0 | 0 | 0 | 140.8709 | 19.56 | 19.56
2025-12-04 02:00:00 | 19.56 | 0 | 0 | 0 | 140.8709 | 19.56 | 19.56
2025-12-04 03:00:00 | 19.38 | 0 | 75 | 0 | 206.8709 | 94.38 | 19.38
2025-12-04 04:00:00 | 18.96 | 0 | 75 | 0 | 272.8709 | 93.96 | 18.96
2025-12-04 05:00:00 | 19.44 | 0 | 75 | 0 | 338.8709 | 94.44 | 19.44
2025-12-04 06:00:00 | 34.5 | 0 | 75 | 0 | 404.8709 | 109.5 | 34.5
2025-12-04 07:00:00 | 36.6 | 0 | 0 | 36.6 | 368.2709 | 0 | 36.6
2025-12-04 08:00:00 | 39.48 | 2.2938 | 0 | 37.1862 | 331.0847 | 4.2633e-14 | 37.1862
2025-12-04 09:00:00 | 29.16 | 4.3187 | 0 | 24.8413 | 306.2434 | 7.1054e-15 | 24.8413
2025-12-04 10:00:00 | 28.92 | 5.7505 | 0 | 23.1695 | 283.0738 | -1.7764e-14 | 23.1695
2025-12-04 11:00:00 | 27.96 | 6.4916 | 0 | 21.4684 | 261.6054 | -4.2633e-14 | 21.4684
2025-12-04 12:00:00 | 41.82 | 6.4916 | 0 | 35.3284 | 226.277 | -4.2633e-14 | 35.3284
2025-12-04 13:00:00 | 36.54 | 5.7505 | 0 | 30.7895 | 195.4875 | -2.1316e-14 | 30.7895
2025-12-04 14:00:00 | 36.36 | 4.3187 | 0 | 32.0413 | 163.4462 | 1.0658e-13 | 32.0413
2025-12-04 15:00:00 | 34.26 | 2.2938 | 0 | 31.9662 | 131.48 | 3.908e-14 | 31.9662
2025-12-04 16:00:00 | 24.78 | 0 | 0 | 24.78 | 106.7 | 0 | 24.78
2025-12-04 17:00:00 | 21.6 | 0 | 0 | 21.6 | 85.1 | 0 | 21.6
2025-12-04 18:00:00 | 20.1 | 0 | 0 | 20.1 | 65 | 0 | 20.1
2025-12-04 19:00:00 | 22.2 | 0 | 24.7663 | 0 | 86.7944 | 46.9663 | 22.2
2025-12-04 20:00:00 | 29.1 | 0 | 0 | 0 | 86.7944 | 29.1 | 29.1
2025-12-04 21:00:00 | 27.78 | 0 | 0 | 0 | 86.7944 | 27.78 | 27.78
2025-12-04 22:00:00 | 32.22 | 0 | 0 | 0 | 86.7944 | 32.22 | 32.22
2025-12-04 23:00:00 | 24.9 | 0 | 0 | 0 | 86.7944 | 24.9 | 24.9
2025-12-05 00:00:00 | 18.9 | 0 | 0 | 0 | 86.7944 | 18.9 | 18.9
2025-12-05 01:00:00 | 19.14 | 0 | 0 | 0 | 86.7944 | 19.14 | 19.14
2025-12-05 02:00:00 | 18.3 | 0 | 0 | 0 | 86.7944 | 18.3 | 18.3
2025-12-05 03:00:00 | 18.9 | 0 | 75 | 0 | 152.7944 | 93.9 | 18.9
2025-12-05 04:00:00 | 18.78 | 0 | 75 | 0 | 218.7944 | 93.78 | 18.78
2025-12-05 05:00:00 | 19.62 | 0 | 75 | 0 | 284.7944 | 94.62 | 19.62
2025-12-05 06:00:00 | 20.64 | 0 | 75 | 0 | 350.7944 | 95.64 | 20.64
2025-12-05 07:00:00 | 20.28 | 0 | 0 | 20.28 | 330.5144 | 0 | 20.28
2025-12-05 08:00:00 | 29.22 | 2.2679 | 0 | 26.9521 | 303.5622 | -4.2633e-14 | 26.9521
2025-12-05 09:00:00 | 28.74 | 4.2911 | 0 | 24.4489 | 279.1133 | 0 | 24.4489
2025-12-05 10:00:00 | 26.76 | 5.7217 | 0 | 21.0383 | 258.075 | 0 | 21.0383
2025-12-05 11:00:00 | 24.72 | 6.4622 | 0 | 18.2578 | 239.8172 | -1.7764e-14 | 18.2578
2025-12-05 12:00:00 | 22.08 | 6.4622 | 0 | 15.6178 | 224.1994 | -1.7764e-14 | 15.6178
2025-12-05 13:00:00 | 19.08 | 5.7217 | 0 | 13.3583 | 210.8411 | -1.7764e-15 | 13.3583
2025-12-05 14:00:00 | 18.12 | 4.2911 | 0 | 13.8289 | 197.0121 | 3.5527e-15 | 13.8289
2025-12-05 15:00:00 | 19.32 | 2.2679 | 0 | 17.0521 | 179.96 | -3.908e-14 | 17.0521
2025-12-05 16:00:00 | 32.22 | 0 | 0 | 32.22 | 147.74 | 0 | 32.22
2025-12-05 17:00:00 | 43.02 | 0 | 0 | 43.02 | 104.72 | 0 | 43.02
2025-12-05 18:00:00 | 39.72 | 0 | 0 | 39.72 | 65 | 0 | 39.72
2025-12-05 19:00:00 | 37.38 | 0 | 0 | 0 | 65 | 37.38 | 37.38
2025-12-05 20:00:00 | 28.56 | 0 | 0 | 0 | 65 | 28.56 | 28.56
2025-12-05 21:00:00 | 18.96 | 0 | 0 | 0 | 65 | 18.96 | 18.96
2025-12-05 22:00:00 | 19.86 | 0 | 0 | 0 | 65 | 19.86 | 19.86
2025-12-05 23:00:00 | 19.98 | 0 | 0 | 0 | 65 | 19.98 | 19.98
2025-12-06 00:00:00 | 17.82 | 0 | 0 | 0 | 65 | 17.82 | 17.82
2025-12-06 01:00:00 | 27 | 0 | 0 | 0 | 65 | 27 | 27
2025-12-06 02:00:00 | 35.22 | 0 | 0 | 0 | 65 | 35.22 | 35.22
2025-12-06 03:00:00 | 34.92 | 0 | 0 | 0 | 65 | 34.92 | 34.92
2025-12-06 04:00:00 | 31.44 | 0 | 0 | 0 | 65 | 31.44 | 31.44
2025-12-06 05:00:00 | 19.62 | 0 | 0 | 0 | 65 | 19.62 | 19.62
2025-12-06 06:00:00 | 20.22 | 0 | 0 | 0 | 65 | 20.22 | 20.22
2025-12-06 07:00:00 | 17.88 | 0 | 0 | 0 | 65 | 17.88 | 17.88
2025-12-06 08:00:00 | 18.6 | 2.2434 | 0 | 0 | 65 | 16.3566 | 16.3566
2025-12-06 09:00:00 | 34.14 | 4.2651 | 0 | 0 | 65 | 29.8749 | 29.8749
2025-12-06 10:00:00 | 42.72 | 5.6946 | 0 | 0 | 65 | 37.0254 | 37.0254
2025-12-06 11:00:00 | 42.42 | 6.4346 | 0 | 0 | 65 | 35.9854 | 35.9854
2025-12-06 12:00:00 | 42.78 | 6.4346 | 0 | 0 | 65 | 36.3454 | 36.3454
2025-12-06 13:00:00 | 40.5 | 5.6946 | 0 | 0 | 65 | 34.8054 | 34.8054
2025-12-06 14:00:00 | 36.78 | 4.2651 | 0 | 0 | 65 | 32.5149 | 32.5149
2025-12-06 15:00:00 | 42.54 | 2.2434 | 0 | 0 | 65 | 40.2966 | 40.2966
2025-12-06 16:00:00 | 46.26 | 0 | 0 | 0 | 65 | 46.26 | 46.26
2025-12-06 17:00:00 | 34.38 | 0 | 0 | 0 | 65 | 34.38 | 34.38
2025-12-06 18:00:00 | 21.06 | 0 | 0 | 0 | 65 | 21.06 | 21.06
2025-12-06 19:00:00 | 31.86 | 0 | 0 | 0 | 65 | 31.86 | 31.86
2025-12-06 20:00:00 | 43.62 | 0 | 0 | 0 | 65 | 43.62 | 43.62
2025-12-06 21:00:00 | 43.74 | 0 | 0 | 0 | 65 | 43.74 | 43.74
2025-12-06 22:00:00 | 41.46 | 0 | 0 | 0 | 65 | 41.46 | 41.46
2025-12-06 23:00:00 | 37.02 | 0 | 0 | 0 | 65 | 37.02 | 37.02
2025-12-07 00:00:00 | 22.5 | 0 | 0 | 0 | 65 | 22.5 | 22.5
2025-12-07 01:00:00 | 19.32 | 0 | 0 | 0 | 65 | 19.32 | 19.32
2025-12-07 02:00:00 | 18.96 | 0 | 0 | 0 | 65 | 18.96 | 18.96
2025-12-07 03:00:00 | 18.54 | 0 | 0 | 0 | 65 | 18.54 | 18.54
2025-12-07 04:00:00 | 19.26 | 0 | 0 | 0 | 65 | 19.26 | 19.26
2025-12-07 05:00:00 | 34.74 | 0 | 0 | 0 | 65 | 34.74 | 34.74
2025-12-07 06:00:00 | 35.1 | 0 | 0 | 0 | 65 | 35.1 | 35.1
2025-12-07 07:00:00 | 35.88 | 0 | 0 | 0 | 65 | 35.88 | 35.88
2025-12-07 08:00:00 | 21.54 | 2.2206 | 0 | 0 | 65 | 19.3194 | 19.3194
2025-12-07 09:00:00 | 24.42 | 4.2408 | 0 | 0 | 65 | 20.1792 | 20.1792
2025-12-07 10:00:00 | 28.92 | 5.6693 | 0 | 0 | 65 | 23.2507 | 23.2507
2025-12-07 11:00:00 | 35.34 | 6.4087 | 0 | 0 | 65 | 28.9313 | 28.9313
2025-12-07 12:00:00 | 38.94 | 6.4087 | 0 | 0 | 65 | 32.5313 | 32.5313
2025-12-07 13:00:00 | 38.04 | 5.6693 | 0 | 0 | 65 | 32.3707 | 32.3707
2025-12-07 14:00:00 | 39.3 | 4.2408 | 0 | 0 | 65 | 35.0592 | 35.0592
2025-12-07 15:00:00 | 38.34 | 2.2206 | 0 | 0 | 65 | 36.1194 | 36.1194
2025-12-07 16:00:00 | 37.8 | 0 | 0 | 0 | 65 | 37.8 | 37.8
2025-12-07 17:00:00 | 23.46 | 0 | 0 | 0 | 65 | 23.46 | 23.46
2025-12-07 18:00:00 | 21.72 | 0 | 0 | 0 | 65 | 21.72 | 21.72
2025-12-07 19:00:00 | 21.36 | 0 | 27.5508 | 0 | 89.2447 | 48.9108 | 21.36
2025-12-07 20:00:00 | 21.24 | 0 | 0 | 0 | 89.2447 | 21.24 | 21.24
2025-12-07 21:00:00 | 20.88 | 0 | 0 | 0 | 89.2447 | 20.88 | 20.88
2025-12-07 22:00:00 | 21.6 | 0 | 0 | 0 | 89.2447 | 21.6 | 21.6
2025-12-07 23:00:00 | 21.12 | 0 | 0 | 0 | 89.2447 | 21.12 | 21.12
2025-12-08 00:00:00 | 21.66 | 0 | 0 | 0 | 89.2447 | 21.66 | 21.66
2025-12-08 01:00:00 | 21.54 | 0 | 0 | 0 | 89.2447 | 21.54 | 21.54
2025-12-08 02:00:00 | 21.36 | 0 | 0 | 0 | 89.2447 | 21.36 | 21.36
2025-12-08 03:00:00 | 21.06 | 0 | 75 | 0 | 155.2447 | 96.06 | 21.06
2025-12-08 04:00:00 | 21.3 | 0 | 75 | 0 | 221.2447 | 96.3 | 21.3
2025-12-08 05:00:00 | 22.56 | 0 | 75 | 0 | 287.2447 | 97.56 | 22.56
2025-12-08 06:00:00 | 21.36 | 0 | 75 | 0 | 353.2447 | 96.36 | 21.36
2025-12-08 07:00:00 | 21.66 | 0 | 0 | 21.66 | 331.5847 | 0 | 21.66
2025-12-08 08:00:00 | 21.3 | 2.1993 | 0 | 19.1007 | 312.484 | -2.1316e-14 | 19.1007
2025-12-08 09:00:00 | 24 | 4.2181 | 0 | 19.7819 | 292.7021 | 2.1316e-14 | 19.7819
2025-12-08 10:00:00 | 23.64 | 5.6457 | 0 | 17.9943 | 274.7078 | 3.5527e-15 | 17.9943
2025-12-08 11:00:00 | 22.74 | 6.3846 | 0 | 16.3554 | 258.3524 | -2.8422e-14 | 16.3554
2025-12-08 12:00:00 | 21.72 | 6.3846 | 0 | 15.3354 | 243.017 | -3.0198e-14 | 15.3354
2025-12-08 13:00:00 | 22.2 | 5.6457 | 0 | 16.5543 | 226.4626 | 0 | 16.5543
2025-12-08 14:00:00 | 23.94 | 4.2181 | 0 | 19.7219 | 206.7407 | 1.7764e-14 | 19.7219
2025-12-08 15:00:00 | 20.88 | 2.1993 | 0 | 18.6807 | 188.06 | -2.1316e-14 | 18.6807
2025-12-08 16:00:00 | 31.02 | 0 | 0 | 31.02 | 157.04 | 0 | 31.02
2025-12-08 17:00:00 | 45.48 | 0 | 0 | 45.48 | 111.56 | 0 | 45.48
2025-12-08 18:00:00 | 46.56 | 0 | 0 | 46.56 | 65 | 0 | 46.56
2025-12-08 19:00:00 | 46.56 | 0 | 0 | 0 | 65 | 46.56 | 46.56
2025-12-08 20:00:00 | 50.52 | 0 | 44.1075 | 0 | 103.8146 | 94.6275 | 50.52
2025-12-08 21:00:00 | 42.84 | 0 | 0 | 0 | 103.8146 | 42.84 | 42.84
2025-12-08 22:00:00 | 28.62 | 0 | 0 | 0 | 103.8146 | 28.62 | 28.62
2025-12-08 23:00:00 | 24.72 | 0 | 0 | 0 | 103.8146 | 24.72 | 24.72
2025-12-09 00:00:00 | 23.16 | 0 | 0 | 0 | 103.8146 | 23.16 | 23.16
2025-12-09 01:00:00 | 22.2 | 0 | 0 | 0 | 103.8146 | 22.2 | 22.2
2025-12-09 02:00:00 | 23.88 | 0 | 0 | 0 | 103.8146 | 23.88 | 23.88
2025-12-09 03:00:00 | 23.28 | 0 | 75 | 0 | 169.8146 | 98.28 | 23.28
2025-12-09 04:00:00 | 23.22 | 0 | 75 | 0 | 235.8146 | 98.22 | 23.22
2025-12-09 05:00:00 | 23.64 | 0 | 75 | 0 | 301.8146 | 98.64 | 23.64
2025-12-09 06:00:00 | 23.82 | 0 | 75 | 0 | 367.8146 | 98.82 | 23.82
2025-12-09 07:00:00 | 23.52 | 0 | 0 | 23.52 | 344.2946 | 0 | 23.52
2025-12-09 08:00:00 | 31.5 | 2.1795 | 0 | 29.3205 | 314.9741 | -4.9738e-14 | 29.3205
2025-12-09 09:00:00 | 33.3 | 4.1971 | 0 | 29.1029 | 285.8712 | 4.2633e-14 | 29.1029
2025-12-09 10:00:00 | 31.98 | 5.6238 | 0 | 26.3562 | 259.515 | 7.1054e-15 | 26.3562
2025-12-09 11:00:00 | 31.5 | 6.3623 | 0 | 25.1377 | 234.3773 | 2.4869e-14 | 25.1377
2025-12-09 12:00:00 | 27.54 | 6.3623 | 0 | 21.1777 | 213.1995 | 2.4869e-14 | 21.1777
2025-12-09 13:00:00 | 22.26 | 5.6238 | 0 | 16.6362 | 196.5633 | 7.1054e-15 | 16.6362
2025-12-09 14:00:00 | 21.48 | 4.1971 | 0 | 17.2829 | 179.2805 | 4.6185e-14 | 17.2829
2025-12-09 15:00:00 | 24.36 | 2.1795 | 0 | 22.1805 | 157.1 | -4.9738e-14 | 22.1805
2025-12-09 16:00:00 | 21.12 | 0 | 0 | 21.12 | 135.98 | 0 | 21.12
2025-12-09 17:00:00 | 32.58 | 0 | 0 | 32.58 | 103.4 | 0 | 32.58
2025-12-09 18:00:00 | 38.4 | 0 | 0 | 38.4 | 65 | 0 | 38.4
2025-12-09 19:00:00 | 37.62 | 0 | 75 | 0 | 131 | 112.62 | 37.62
2025-12-09 20:00:00 | 42.3 | 0 | 66.035 | 0 | 189.1108 | 108.335 | 42.3
2025-12-09 21:00:00 | 45.3 | 0 | 0 | 0 | 189.1108 | 45.3 | 45.3
2025-12-09 22:00:00 | 31.08 | 0 | 0 | 0 | 189.1108 | 31.08 | 31.08
2025-12-09 23:00:00 | 24.12 | 0 | 0 | 0 | 189.1108 | 24.12 | 24.12
2025-12-10 00:00:00 | 23.94 | 0 | 0 | 0 | 189.1108 | 23.94 | 23.94
2025-12-10 01:00:00 | 27.24 | 0 | 0 | 0 | 189.1108 | 27.24 | 27.24
2025-12-10 02:00:00 | 36.6 | 0 | 75 | 0 | 255.1108 | 111.6 | 36.6
2025-12-10 03:00:00 | 37.02 | 0 | 75 | 0 | 321.1108 | 112.02 | 37.02
2025-12-10 04:00:00 | 37.14 | 0 | 75 | 0 | 387.1108 | 112.14 | 37.14
2025-12-10 05:00:00 | 37.44 | 0 | 75 | 0 | 453.1108 | 112.44 | 37.44
2025-12-10 06:00:00 | 37.08 | 0 | 75 | 0 | 519.1108 | 112.08 | 37.08
2025-12-10 07:00:00 | 30.54 | 0 | 0 | 30.54 | 488.5708 | 0 | 30.54
2025-12-10 08:00:00 | 20.7 | 2.1614 | 0 | 18.5386 | 470.0322 | 7.1054e-15 | 18.5386
2025-12-10 09:00:00 | 31.92 | 4.1778 | 0 | 27.7422 | 442.29 | -7.1054e-15 | 27.7422
2025-12-10 10:00:00 | 51.18 | 5.6037 | 0 | 45.5763 | 396.7137 | 0 | 45.5763
2025-12-10 11:00:00 | 45.84 | 6.3417 | 0 | 39.4983 | 357.2154 | -2.1316e-14 | 39.4983
2025-12-10 12:00:00 | 42.9 | 6.3417 | 0 | 36.5583 | 320.6571 | -2.1316e-14 | 36.5583
2025-12-10 13:00:00 | 40.2 | 5.6037 | 0 | 34.5963 | 286.0608 | 7.1054e-15 | 34.5963
2025-12-10 14:00:00 | 37.44 | 4.1778 | 0 | 33.2622 | 252.7986 | -1.4211e-14 | 33.2622
2025-12-10 15:00:00 | 45.72 | 2.1614 | 0 | 43.5586 | 209.24 | 7.1054e-15 | 43.5586
2025-12-10 16:00:00 | 51.78 | 0 | 0 | 51.78 | 157.46 | 0 | 51.78
2025-12-10 17:00:00 | 46.68 | 0 | 0 | 46.68 | 110.78 | 0 | 46.68
2025-12-10 18:00:00 | 45.78 | 0 | 0 | 45.78 | 65 | 0 | 45.78
2025-12-10 19:00:00 | 44.94 | 0 | 67.1515 | 0 | 124.0933 | 112.0915 | 44.94
2025-12-10 20:00:00 | 35.46 | 0 | 0 | 0 | 124.0933 | 35.46 | 35.46
2025-12-10 21:00:00 | 31.86 | 0 | 0 | 0 | 124.0933 | 31.86 | 31.86
2025-12-10 22:00:00 | 24.78 | 0 | 0 | 0 | 124.0933 | 24.78 | 24.78
2025-12-10 23:00:00 | 24.18 | 0 | 0 | 0 | 124.0933 | 24.18 | 24.18
2025-12-11 00:00:00 | 22.92 | 0 | 0 | 0 | 124.0933 | 22.92 | 22.92
2025-12-11 01:00:00 | 21.18 | 0 | 0 | 0 | 124.0933 | 21.18 | 21.18
2025-12-11 02:00:00 | 21.84 | 0 | 0 | 0 | 124.0933 | 21.84 | 21.84
2025-12-11 03:00:00 | 21.66 | 0 | 75 | 0 | 190.0933 | 96.66 | 21.66
2025-12-11 04:00:00 | 22.02 | 0 | 75 | 0 | 256.0933 | 97.02 | 22.02
2025-12-11 05:00:00 | 20.94 | 0 | 75 | 0 | 322.0933 | 95.94 | 20.94
2025-12-11 06:00:00 | 20.94 | 0 | 75 | 0 | 388.0933 | 95.94 | 20.94
2025-12-11 07:00:00 | 21.36 | 0 | 0 | 21.36 | 366.7333 | 0 | 21.36
2025-12-11 08:00:00 | 32.7 | 2.1449 | 0 | 30.5551 | 336.1781 | 0 | 30.5551
2025-12-11 09:00:00 | 33.84 | 4.1602 | 0 | 29.6798 | 306.4984 | 3.1974e-14 | 29.6798
2025-12-11 10:00:00 | 29.82 | 5.5853 | 0 | 24.2347 | 282.2637 | 2.8422e-14 | 24.2347
2025-12-11 11:00:00 | 27 | 6.323 | 0 | 20.677 | 261.5866 | -3.5527e-15 | 20.677
2025-12-11 12:00:00 | 23.76 | 6.323 | 0 | 17.437 | 244.1496 | 0 | 17.437
2025-12-11 13:00:00 | 27.78 | 5.5853 | 0 | 22.1947 | 221.9549 | 2.8422e-14 | 22.1947
2025-12-11 14:00:00 | 39.72 | 4.1602 | 0 | 35.5598 | 186.3951 | 2.8422e-14 | 35.5598
2025-12-11 15:00:00 | 37.74 | 2.1449 | 0 | 35.5951 | 150.8 | 0 | 35.5951
2025-12-11 16:00:00 | 37.38 | 0 | 0 | 37.38 | 113.42 | 0 | 37.38
2025-12-11 17:00:00 | 26.34 | 0 | 0 | 26.34 | 87.08 | 0 | 26.34
2025-12-11 18:00:00 | 22.08 | 0 | 0 | 22.08 | 65 | 0 | 22.08
2025-12-11 19:00:00 | 36.18 | 0 | 75 | 0 | 131 | 111.18 | 36.18
2025-12-11 20:00:00 | 36.78 | 0 | 55.0933 | 0 | 179.4821 | 91.8733 | 36.78
2025-12-11 21:00:00 | 37.8 | 0 | 0 | 0 | 179.4821 | 37.8 | 37.8
2025-12-11 22:00:00 | 39.18 | 0 | 0 | 0 | 179.4821 | 39.18 | 39.18
2025-12-11 23:00:00 | 37.02 | 0 | 0 | 0 | 179.4821 | 37.02 | 37.02
2025-12-12 00:00:00 | 35.88 | 0 | 0 | 0 | 179.4821 | 35.88 | 35.88
2025-12-12 01:00:00 | 36.6 | 0 | 0 | 0 | 179.4821 | 36.6 | 36.6
2025-12-12 02:00:00 | 30.54 | 0 | 0 | 0 | 179.4821 | 30.54 | 30.54
2025-12-12 03:00:00 | 21.48 | 0 | 75 | 0 | 245.4821 | 96.48 | 21.48
2025-12-12 04:00:00 | 21.54 | 0 | 75 | 0 | 311.4821 | 96.54 | 21.54
2025-12-12 05:00:00 | 21.66 | 0 | 75 | 0 | 377.4821 | 96.66 | 21.66
2025-12-12 06:00:00 | 25.44 | 0 | 75 | 0 | 443.4821 | 100.44 | 25.44
2025-12-12 07:00:00 | 23.28 | 0 | 0 | 23.28 | 420.2021 | 0 | 23.28
2025-12-12 08:00:00 | 28.44 | 2.1299 | 0 | 26.3101 | 393.892 | -3.1974e-14 | 26.3101
2025-12-12 09:00:00 | 30.3 | 4.1443 | 0 | 26.1557 | 367.7363 | -4.2633e-14 | 26.1557
2025-12-12 10:00:00 | 29.88 | 5.5687 | 0 | 24.3113 | 343.425 | 7.1054e-15 | 24.3113
2025-12-12 11:00:00 | 27.54 | 6.306 | 0 | 21.234 | 322.191 | 7.1054e-15 | 21.234
2025-12-12 12:00:00 | 26.22 | 6.306 | 0 | 19.914 | 302.2771 | 7.1054e-15 | 19.914
2025-12-12 13:00:00 | 22.38 | 5.5687 | 0 | 16.8113 | 285.4658 | 7.1054e-15 | 16.8113
2025-12-12 14:00:00 | 23.4 | 4.1443 | 0 | 19.2557 | 266.2101 | -4.2633e-14 | 19.2557
2025-12-12 15:00:00 | 25.26 | 2.1299 | 0 | 23.1301 | 243.08 | -3.1974e-14 | 23.1301
2025-12-12 16:00:00 | 59.34 | 0 | 0 | 59.34 | 183.74 | -9.9476e-14 | 59.34
2025-12-12 17:00:00 | 62.28 | 0 | 0 | 62.28 | 121.46 | 0 | 62.28
2025-12-12 18:00:00 | 56.46 | 0 | 0 | 56.46 | 65 | 0 | 56.46
2025-12-12 19:00:00 | 55.02 | 0 | 0 | 0 | 65 | 55.02 | 55.02
2025-12-12 20:00:00 | 24.84 | 0 | 0 | 0 | 65 | 24.84 | 24.84
2025-12-12 21:00:00 | 21.78 | 0 | 0 | 0 | 65 | 21.78 | 21.78
2025-12-12 22:00:00 | 22.26 | 0 | 0 | 0 | 65 | 22.26 | 22.26
2025-12-12 23:00:00 | 20.94 | 0 | 0 | 0 | 65 | 20.94 | 20.94
2025-12-13 00:00:00 | 21.06 | 0 | 0 | 0 | 65 | 21.06 | 21.06
2025-12-13 01:00:00 | 21.78 | 0 | 0 | 0 | 65 | 21.78 | 21.78
2025-12-13 02:00:00 | 24.36 | 0 | 0 | 0 | 65 | 24.36 | 24.36
2025-12-13 03:00:00 | 36.96 | 0 | 0 | 0 | 65 | 36.96 | 36.96
2025-12-13 04:00:00 | 37.14 | 0 | 0 | 0 | 65 | 37.14 | 37.14
2025-12-13 05:00:00 | 30.96 | 0 | 0 | 0 | 65 | 30.96 | 30.96
2025-12-13 06:00:00 | 20.7 | 0 | 0 | 0 | 65 | 20.7 | 20.7
2025-12-13 07:00:00 | 21.84 | 0 | 0 | 0 | 65 | 21.84 | 21.84
2025-12-13 08:00:00 | 20.64 | 2.1166 | 0 | 0 | 65 | 18.5234 | 18.5234
2025-12-13 09:00:00 | 21.12 | 4.1301 | 0 | 0 | 65 | 16.9899 | 16.9899
2025-12-13 10:00:00 | 24 | 5.5539 | 0 | 0 | 65 | 18.4461 | 18.4461
2025-12-13 11:00:00 | 37.8 | 6.2909 | 0 | 0 | 65 | 31.5091 | 31.5091
2025-12-13 12:00:00 | 37.86 | 6.2909 | 0 | 0 | 65 | 31.5691 | 31.5691
2025-12-13 13:00:00 | 47.4 | 5.5539 | 0 | 0 | 65 | 41.8461 | 41.8461
2025-12-13 14:00:00 | 48.72 | 4.1301 | 0 | 0 | 65 | 44.5899 | 44.5899
2025-12-13 15:00:00 | 54.6 | 2.1166 | 0 | 0 | 65 | 52.4834 | 52.4834
2025-12-13 16:00:00 | 51.36 | 0 | 0 | 0 | 65 | 51.36 | 51.36
2025-12-13 17:00:00 | 33.18 | 0 | 0 | 0 | 65 | 33.18 | 33.18
2025-12-13 18:00:00 | 39.48 | 0 | 0 | 0 | 65 | 39.48 | 39.48
2025-12-13 19:00:00 | 41.22 | 0 | 0 | 0 | 65 | 41.22 | 41.22
2025-12-13 20:00:00 | 44.52 | 0 | 0 | 0 | 65 | 44.52 | 44.52
2025-12-13 21:00:00 | 36.72 | 0 | 0 | 0 | 65 | 36.72 | 36.72
2025-12-13 22:00:00 | 33.54 | 0 | 0 | 0 | 65 | 33.54 | 33.54
2025-12-13 23:00:00 | 27.42 | 0 | 0 | 0 | 65 | 27.42 | 27.42
2025-12-14 00:00:00 | 25.32 | 0 | 0 | 0 | 65 | 25.32 | 25.32
2025-12-14 01:00:00 | 24.24 | 0 | 0 | 0 | 65 | 24.24 | 24.24
2025-12-14 02:00:00 | 23.4 | 0 | 0 | 0 | 65 | 23.4 | 23.4
2025-12-14 03:00:00 | 22.56 | 0 | 0 | 0 | 65 | 22.56 | 22.56
2025-12-14 04:00:00 | 22.44 | 0 | 0 | 0 | 65 | 22.44 | 22.44
2025-12-14 05:00:00 | 22.5 | 0 | 0 | 0 | 65 | 22.5 | 22.5
2025-12-14 06:00:00 | 24.96 | 0 | 0 | 0 | 65 | 24.96 | 24.96
2025-12-14 07:00:00 | 23.76 | 0 | 0 | 0 | 65 | 23.76 | 23.76
2025-12-14 08:00:00 | 24.6 | 2.1048 | 0 | 0 | 65 | 22.4952 | 22.4952
2025-12-14 09:00:00 | 36.84 | 4.1176 | 0 | 0 | 65 | 32.7224 | 32.7224
2025-12-14 10:00:00 | 38.34 | 5.5409 | 0 | 0 | 65 | 32.7991 | 32.7991
2025-12-14 11:00:00 | 35.16 | 6.2776 | 0 | 0 | 65 | 28.8824 | 28.8824
2025-12-14 12:00:00 | 30.54 | 6.2776 | 0 | 0 | 65 | 24.2624 | 24.2624
2025-12-14 13:00:00 | 27.48 | 5.5409 | 0 | 0 | 65 | 21.9391 | 21.9391
2025-12-14 14:00:00 | 25.5 | 4.1176 | 0 | 0 | 65 | 21.3824 | 21.3824
2025-12-14 15:00:00 | 27.24 | 2.1048 | 0 | 0 | 65 | 25.1352 | 25.1352
2025-12-14 16:00:00 | 34.08 | 0 | 0 | 0 | 65 | 34.08 | 34.08
2025-12-14 17:00:00 | 23.52 | 0 | 0 | 0 | 65 | 23.52 | 23.52
2025-12-14 18:00:00 | 24.9 | 0 | 75 | 0 | 131 | 99.9 | 24.9
2025-12-14 19:00:00 | 23.16 | 0 | 19.6427 | 0 | 148.2856 | 42.8027 | 23.16
2025-12-14 20:00:00 | 22.98 | 0 | 0 | 0 | 148.2856 | 22.98 | 22.98
2025-12-14 21:00:00 | 23.52 | 0 | 0 | 0 | 148.2856 | 23.52 | 23.52
2025-12-14 22:00:00 | 22.44 | 0 | 0 | 0 | 148.2856 | 22.44 | 22.44
2025-12-14 23:00:00 | 22.74 | 0 | 0 | 0 | 148.2856 | 22.74 | 22.74
2025-12-15 00:00:00 | 22.62 | 0 | 0 | 0 | 148.2856 | 22.62 | 22.62
2025-12-15 01:00:00 | 22.92 | 0 | 0 | 0 | 148.2856 | 22.92 | 22.92
2025-12-15 02:00:00 | 22.86 | 0 | 0 | 0 | 148.2856 | 22.86 | 22.86
2025-12-15 03:00:00 | 23.28 | 0 | 75 | 0 | 214.2856 | 98.28 | 23.28
2025-12-15 04:00:00 | 22.44 | 0 | 75 | 0 | 280.2856 | 97.44 | 22.44
2025-12-15 05:00:00 | 22.98 | 0 | 75 | 0 | 346.2856 | 97.98 | 22.98
2025-12-15 06:00:00 | 22.62 | 0 | 75 | 0 | 412.2856 | 97.62 | 22.62
2025-12-15 07:00:00 | 22.26 | 0 | 0 | 22.26 | 390.0256 | 0 | 22.26
2025-12-15 08:00:00 | 26.88 | 2.0947 | 0 | 24.7853 | 365.2403 | -3.908e-14 | 24.7853
2025-12-15 09:00:00 | 31.92 | 4.1068 | 0 | 27.8132 | 337.4271 | 3.908e-14 | 27.8132
2025-12-15 10:00:00 | 31.44 | 5.5296 | 0 | 25.9104 | 311.5167 | 2.8422e-14 | 25.9104
2025-12-15 11:00:00 | 29.64 | 6.2661 | 0 | 23.3739 | 288.1428 | -3.908e-14 | 23.3739
2025-12-15 12:00:00 | 30.96 | 6.2661 | 0 | 24.6939 | 263.4489 | -3.908e-14 | 24.6939
2025-12-15 13:00:00 | 39.06 | 5.5296 | 0 | 33.5304 | 229.9185 | 2.8422e-14 | 33.5304
2025-12-15 14:00:00 | 35.88 | 4.1068 | 0 | 31.7732 | 198.1453 | -6.0396e-14 | 31.7732
2025-12-15 15:00:00 | 36.78 | 2.0947 | 0 | 34.6853 | 163.46 | -3.5527e-14 | 34.6853
2025-12-15 16:00:00 | 33.36 | 0 | 0 | 33.36 | 130.1 | 0 | 33.36
2025-12-15 17:00:00 | 31.86 | 0 | 0 | 31.86 | 98.24 | 0 | 31.86
2025-12-15 18:00:00 | 33.24 | 0 | 0 | 33.24 | 65 | 0 | 33.24
2025-12-15 19:00:00 | 34.92 | 0 | 75 | 0 | 131 | 109.92 | 34.92
2025-12-15 20:00:00 | 46.02 | 0 | 71.82 | 0 | 194.2016 | 117.84 | 46.02
2025-12-15 21:00:00 | 46.8 | 0 | 2.5879 | 0 | 196.479 | 49.3879 | 46.8
2025-12-15 22:00:00 | 31.62 | 0 | 0 | 0 | 196.479 | 31.62 | 31.62
2025-12-15 23:00:00 | 27.06 | 0 | 0 | 0 | 196.479 | 27.06 | 27.06
2025-12-16 00:00:00 | 25.08 | 0 | 0 | 0 | 196.479 | 25.08 | 25.08
2025-12-16 01:00:00 | 23.28 | 0 | 0 | 0 | 196.479 | 23.28 | 23.28
2025-12-16 02:00:00 | 23.88 | 0 | 0 | 0 | 196.479 | 23.88 | 23.88
2025-12-16 03:00:00 | 22.8 | 0 | 75 | 0 | 262.479 | 97.8 | 22.8
2025-12-16 04:00:00 | 24.06 | 0 | 75 | 0 | 328.479 | 99.06 | 24.06
2025-12-16 05:00:00 | 22.68 | 0 | 75 | 0 | 394.479 | 97.68 | 22.68
2025-12-16 06:00:00 | 22.86 | 0 | 75 | 0 | 460.479 | 97.86 | 22.86
2025-12-16 07:00:00 | 23.4 | 0 | 0 | 23.4 | 437.079 | 0 | 23.4
2025-12-16 08:00:00 | 37.86 | 2.0862 | 0 | 35.7738 | 401.3051 | -7.1054e-15 | 35.7738
2025-12-16 09:00:00 | 36.06 | 4.0978 | 0 | 31.9622 | 369.3429 | -3.5527e-15 | 31.9622
2025-12-16 10:00:00 | 45.84 | 5.5201 | 0 | 40.3199 | 329.023 | 2.1316e-14 | 40.3199
2025-12-16 11:00:00 | 48.06 | 6.2564 | 0 | 41.8036 | 287.2195 | -2.1316e-14 | 41.8036
2025-12-16 12:00:00 | 45.9 | 6.2564 | 0 | 39.6436 | 247.5759 | -2.8422e-14 | 39.6436
2025-12-16 13:00:00 | 42.72 | 5.5201 | 0 | 37.1999 | 210.3761 | -7.816e-14 | 37.1999
2025-12-16 14:00:00 | 39.24 | 4.0978 | 0 | 35.1422 | 175.2338 | -7.1054e-15 | 35.1422
2025-12-16 15:00:00 | 39.54 | 2.0862 | 0 | 37.4538 | 137.78 | 0 | 37.4538
2025-12-16 16:00:00 | 26.76 | 0 | 0 | 26.76 | 111.02 | 0 | 26.76
2025-12-16 17:00:00 | 23.58 | 0 | 0 | 23.58 | 87.44 | 0 | 23.58
2025-12-16 18:00:00 | 22.44 | 0 | 0 | 22.44 | 65 | 0 | 22.44
2025-12-16 19:00:00 | 23.76 | 0 | 75 | 0 | 131 | 98.76 | 23.76
2025-12-16 20:00:00 | 27.54 | 0 | 75 | 0 | 197 | 102.54 | 27.54
2025-12-16 21:00:00 | 31.32 | 0 | 47.68 | 0 | 238.9584 | 79 | 31.32
2025-12-16 22:00:00 | 51.54 | 0 | 0 | 0 | 238.9584 | 51.54 | 51.54
2025-12-16 23:00:00 | 42.66 | 0 | 0 | 0 | 238.9584 | 42.66 | 42.66
2025-12-17 00:00:00 | 40.92 | 0 | 0 | 0 | 238.9584 | 40.92 | 40.92
2025-12-17 01:00:00 | 40.68 | 0 | 0 | 0 | 238.9584 | 40.68 | 40.68
2025-12-17 02:00:00 | 35.28 | 0 | 75 | 0 | 304.9584 | 110.28 | 35.28
2025-12-17 03:00:00 | 21.78 | 0 | 75 | 0 | 370.9584 | 96.78 | 21.78
2025-12-17 04:00:00 | 23.52 | 0 | 75 | 0 | 436.9584 | 98.52 | 23.52
2025-12-17 05:00:00 | 22.02 | 0 | 75 | 0 | 502.9584 | 97.02 | 22.02
2025-12-17 06:00:00 | 33.9 | 0 | 75 | 0 | 568.9584 | 108.9 | 33.9
2025-12-17 07:00:00 | 39.54 | 0 | 0 | 39.54 | 529.4184 | 0 | 39.54
2025-12-17 08:00:00 | 41.52 | 2.0793 | 0 | 39.4407 | 489.9777 | -7.1054e-15 | 39.4407
2025-12-17 09:00:00 | 48.54 | 4.0904 | 0 | 44.4496 | 445.5281 | 2.1316e-14 | 44.4496
2025-12-17 10:00:00 | 46.68 | 5.5125 | 0 | 41.1675 | 404.3606 | 3.5527e-14 | 41.1675
2025-12-17 11:00:00 | 45.78 | 6.2486 | 0 | 39.5314 | 364.8292 | 7.1054e-15 | 39.5314
2025-12-17 12:00:00 | 43.86 | 6.2486 | 0 | 37.6114 | 327.2178 | 7.1054e-15 | 37.6114
2025-12-17 13:00:00 | 40.5 | 5.5125 | 0 | 34.9875 | 292.2303 | 3.5527e-14 | 34.9875
2025-12-17 14:00:00 | 44.16 | 4.0904 | 0 | 40.0696 | 252.1607 | 2.1316e-14 | 40.0696
2025-12-17 15:00:00 | 50.58 | 2.0793 | 0 | 48.5007 | 203.66 | -1.4211e-14 | 48.5007
2025-12-17 16:00:00 | 47.16 | 0 | 0 | 47.16 | 156.5 | 0 | 47.16
2025-12-17 17:00:00 | 47.16 | 0 | 0 | 47.16 | 109.34 | 0 | 47.16
2025-12-17 18:00:00 | 44.34 | 0 | 0 | 44.34 | 65 | 0 | 44.34
2025-12-17 19:00:00 | 53.4 | 0 | 64.44 | 0 | 121.7072 | 117.84 | 53.4
2025-12-17 20:00:00 | 60.9 | 0 | 56.94 | 0 | 171.8144 | 117.84 | 60.9
2025-12-17 21:00:00 | 62.7 | 0 | 55.0108 | 0 | 220.2239 | 117.7108 | 62.7
2025-12-17 22:00:00 | 58.86 | 0 | 0 | 0 | 220.2239 | 58.86 | 58.86
2025-12-17 23:00:00 | 47.7 | 0 | 0 | 0 | 220.2239 | 47.7 | 47.7
2025-12-18 00:00:00 | 39.42 | 0 | 0 | 0 | 220.2239 | 39.42 | 39.42
2025-12-18 01:00:00 | 24.54 | 0 | 0 | 0 | 220.2239 | 24.54 | 24.54
2025-12-18 02:00:00 | 22.68 | 0 | 0 | 0 | 220.2239 | 22.68 | 22.68
2025-12-18 03:00:00 | 22.92 | 0 | 75 | 0 | 286.2239 | 97.92 | 22.92
2025-12-18 04:00:00 | 38.22 | 0 | 75 | 0 | 352.2239 | 113.22 | 38.22
2025-12-18 05:00:00 | 38.82 | 0 | 75 | 0 | 418.2239 | 113.82 | 38.82
2025-12-18 06:00:00 | 37.8 | 0 | 75 | 0 | 484.2239 | 112.8 | 37.8
2025-12-18 07:00:00 | 34.56 | 0 | 0 | 34.56 | 449.6639 | 0 | 34.56
2025-12-18 08:00:00 | 23.22 | 2.074 | 0 | 21.146 | 428.5179 | 1.7764e-14 | 21.146
2025-12-18 09:00:00 | 22.26 | 4.0848 | 0 | 18.1752 | 410.3427 | 2.8422e-14 | 18.1752
2025-12-18 10:00:00 | 24.66 | 5.5066 | 0 | 19.1534 | 391.1893 | 3.1974e-14 | 19.1534
2025-12-18 11:00:00 | 38.28 | 6.2426 | 0 | 32.0374 | 359.152 | -3.5527e-14 | 32.0374
2025-12-18 12:00:00 | 38.76 | 6.2426 | 0 | 32.5174 | 326.6346 | -3.5527e-14 | 32.5174
2025-12-18 13:00:00 | 39.42 | 5.5066 | 0 | 33.9134 | 292.7212 | 3.5527e-14 | 33.9134
2025-12-18 14:00:00 | 38.7 | 4.0848 | 0 | 34.6152 | 258.106 | 2.8422e-14 | 34.6152
2025-12-18 15:00:00 | 38.76 | 2.074 | 0 | 36.686 | 221.42 | 2.1316e-14 | 36.686
2025-12-18 16:00:00 | 48.72 | 0 | 0 | 48.72 | 172.7 | 0 | 48.72
2025-12-18 17:00:00 | 53.94 | 0 | 0 | 53.94 | 118.76 | 0 | 53.94
2025-12-18 18:00:00 | 53.76 | 0 | 0 | 53.76 | 65 | 0 | 53.76
2025-12-18 19:00:00 | 47.22 | 0 | 0 | 0 | 65 | 47.22 | 47.22
2025-12-18 20:00:00 | 43.32 | 0 | 74.52 | 0 | 130.5776 | 117.84 | 43.32
2025-12-18 21:00:00 | 42.3 | 0 | 75 | 0 | 196.5776 | 117.3 | 42.3
2025-12-18 22:00:00 | 39.66 | 0 | 18.7248 | 0 | 213.0554 | 58.3848 | 39.66
2025-12-18 23:00:00 | 40.62 | 0 | 0 | 0 | 213.0554 | 40.62 | 40.62
2025-12-19 00:00:00 | 39.54 | 0 | 0 | 0 | 213.0554 | 39.54 | 39.54
2025-12-19 01:00:00 | 40.68 | 0 | 0 | 0 | 213.0554 | 40.68 | 40.68
2025-12-19 02:00:00 | 39.6 | 0 | 0 | 0 | 213.0554 | 39.6 | 39.6
2025-12-19 03:00:00 | 38.94 | 0 | 75 | 0 | 279.0554 | 113.94 | 38.94
2025-12-19 04:00:00 | 38.34 | 0 | 75 | 0 | 345.0554 | 113.34 | 38.34
2025-12-19 05:00:00 | 38.16 | 0 | 75 | 0 | 411.0554 | 113.16 | 38.16
2025-12-19 06:00:00 | 37.62 | 0 | 75 | 0 | 477.0554 | 112.62 | 37.62
2025-12-19 07:00:00 | 37.8 | 0 | 0 | 37.8 | 439.2554 | 0 | 37.8
2025-12-19 08:00:00 | 37.32 | 2.0704 | 0 | 35.2496 | 404.0058 | 2.1316e-14 | 35.2496
2025-12-19 09:00:00 | 38.16 | 4.0809 | 0 | 34.0791 | 369.9267 | 2.1316e-14 | 34.0791
2025-12-19 10:00:00 | 38.16 | 5.5026 | 0 | 32.6574 | 337.2692 | -3.5527e-14 | 32.6574
2025-12-19 11:00:00 | 31.02 | 6.2385 | 0 | 24.7815 | 312.4877 | 4.2633e-14 | 24.7815
2025-12-19 12:00:00 | 22.02 | 6.2385 | 0 | 15.7815 | 296.7062 | 4.4409e-14 | 15.7815
2025-12-19 13:00:00 | 26.28 | 5.5026 | 0 | 20.7774 | 275.9288 | 6.7502e-14 | 20.7774
2025-12-19 14:00:00 | 44.34 | 4.0809 | 0 | 40.2591 | 235.6696 | 2.8422e-14 | 40.2591
2025-12-19 15:00:00 | 46.26 | 2.0704 | 0 | 44.1896 | 191.48 | 1.4211e-14 | 44.1896
2025-12-19 16:00:00 | 52.5 | 0 | 0 | 52.5 | 138.98 | 0 | 52.5
2025-12-19 17:00:00 | 47.28 | 0 | 0 | 47.28 | 91.7 | 0 | 47.28
2025-12-19 18:00:00 | 26.7 | 0 | 0 | 26.7 | 65 | 0 | 26.7
2025-12-19 19:00:00 | 25.2 | 0 | 0 | 0 | 65 | 25.2 | 25.2
2025-12-19 20:00:00 | 24.96 | 0 | 0 | 0 | 65 | 24.96 | 24.96
2025-12-19 21:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-12-19 22:00:00 | 22.8 | 0 | 0 | 0 | 65 | 22.8 | 22.8
2025-12-19 23:00:00 | 21.84 | 0 | 0 | 0 | 65 | 21.84 | 21.84
2025-12-20 00:00:00 | 24.84 | 0 | 0 | 0 | 65 | 24.84 | 24.84
2025-12-20 01:00:00 | 50.04 | 0 | 0 | 0 | 65 | 50.04 | 50.04
2025-12-20 02:00:00 | 52.68 | 0 | 0 | 0 | 65 | 52.68 | 52.68
2025-12-20 03:00:00 | 52.92 | 0 | 0 | 0 | 65 | 52.92 | 52.92
2025-12-20 04:00:00 | 53.22 | 0 | 0 | 0 | 65 | 53.22 | 53.22
2025-12-20 05:00:00 | 47.4 | 0 | 0 | 0 | 65 | 47.4 | 47.4
2025-12-20 06:00:00 | 31.44 | 0 | 0 | 0 | 65 | 31.44 | 31.44
2025-12-20 07:00:00 | 25.02 | 0 | 0 | 0 | 65 | 25.02 | 25.02
2025-12-20 08:00:00 | 24.48 | 2.0683 | 0 | 0 | 65 | 22.4117 | 22.4117
2025-12-20 09:00:00 | 32.94 | 4.0787 | 0 | 0 | 65 | 28.8613 | 28.8613
2025-12-20 10:00:00 | 40.2 | 5.5003 | 0 | 0 | 65 | 34.6997 | 34.6997
2025-12-20 11:00:00 | 50.58 | 6.2362 | 0 | 0 | 65 | 44.3438 | 44.3438
2025-12-20 12:00:00 | 66.42 | 6.2362 | 0 | 0 | 65 | 60.1838 | 60.1838
2025-12-20 13:00:00 | 56.64 | 5.5003 | 0 | 0 | 65 | 51.1397 | 51.1397
2025-12-20 14:00:00 | 56.88 | 4.0787 | 0 | 0 | 65 | 52.8013 | 52.8013
2025-12-20 15:00:00 | 53.76 | 2.0683 | 0 | 0 | 65 | 51.6917 | 51.6917
2025-12-20 16:00:00 | 50.28 | 0 | 0 | 0 | 65 | 50.28 | 50.28
2025-12-20 17:00:00 | 55.86 | 0 | 0 | 0 | 65 | 55.86 | 55.86
2025-12-20 18:00:00 | 55.44 | 0 | 0 | 0 | 65 | 55.44 | 55.44
2025-12-20 19:00:00 | 55.98 | 0 | 0 | 0 | 65 | 55.98 | 55.98
2025-12-20 20:00:00 | 54.36 | 0 | 0 | 0 | 65 | 54.36 | 54.36
2025-12-20 21:00:00 | 51.24 | 0 | 0 | 0 | 65 | 51.24 | 51.24
2025-12-20 22:00:00 | 44.64 | 0 | 0 | 0 | 65 | 44.64 | 44.64
2025-12-20 23:00:00 | 43.5 | 0 | 0 | 0 | 65 | 43.5 | 43.5
2025-12-21 00:00:00 | 46.92 | 0 | 0 | 0 | 65 | 46.92 | 46.92
2025-12-21 01:00:00 | 26.28 | 0 | 0 | 0 | 65 | 26.28 | 26.28
2025-12-21 02:00:00 | 22.38 | 0 | 0 | 0 | 65 | 22.38 | 22.38
2025-12-21 03:00:00 | 23.52 | 0 | 0 | 0 | 65 | 23.52 | 23.52
2025-12-21 04:00:00 | 22.62 | 0 | 0 | 0 | 65 | 22.62 | 22.62
2025-12-21 05:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-12-21 06:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-12-21 07:00:00 | 22.8 | 0 | 0 | 0 | 65 | 22.8 | 22.8
2025-12-21 08:00:00 | 27.36 | 2.0679 | 0 | 0 | 65 | 25.2921 | 25.2921
2025-12-21 09:00:00 | 51.36 | 4.0783 | 0 | 0 | 65 | 47.2817 | 47.2817
2025-12-21 10:00:00 | 54.78 | 5.4999 | 0 | 0 | 65 | 49.2801 | 49.2801
2025-12-21 11:00:00 | 60.96 | 6.2357 | 0 | 0 | 65 | 54.7243 | 54.7243
2025-12-21 12:00:00 | 60.42 | 6.2357 | 0 | 0 | 65 | 54.1843 | 54.1843
2025-12-21 13:00:00 | 27.48 | 5.4999 | 0 | 0 | 65 | 21.9801 | 21.9801
2025-12-21 14:00:00 | 25.26 | 4.0783 | 0 | 0 | 65 | 21.1817 | 21.1817
2025-12-21 15:00:00 | 25.38 | 2.0679 | 0 | 0 | 65 | 23.3121 | 23.3121
2025-12-21 16:00:00 | 21.84 | 0 | 0 | 0 | 65 | 21.84 | 21.84
2025-12-21 17:00:00 | 22.8 | 0 | 75 | 0 | 131 | 97.8 | 22.8
2025-12-21 18:00:00 | 33.06 | 0 | 75 | 0 | 197 | 108.06 | 33.06
2025-12-21 19:00:00 | 39.54 | 0 | 32.5067 | 0 | 225.6059 | 72.0467 | 39.54
2025-12-21 20:00:00 | 37.02 | 0 | 0 | 0 | 225.6059 | 37.02 | 37.02
2025-12-21 21:00:00 | 22.08 | 0 | 0 | 0 | 225.6059 | 22.08 | 22.08
2025-12-21 22:00:00 | 22.14 | 0 | 0 | 0 | 225.6059 | 22.14 | 22.14
2025-12-21 23:00:00 | 23.76 | 0 | 0 | 0 | 225.6059 | 23.76 | 23.76
2025-12-22 00:00:00 | 22.32 | 0 | 0 | 0 | 225.6059 | 22.32 | 22.32
2025-12-22 01:00:00 | 22.02 | 0 | 0 | 0 | 225.6059 | 22.02 | 22.02
2025-12-22 02:00:00 | 22.44 | 0 | 0 | 0 | 225.6059 | 22.44 | 22.44
2025-12-22 03:00:00 | 22.92 | 0 | 75 | 0 | 291.6059 | 97.92 | 22.92
2025-12-22 04:00:00 | 23.22 | 0 | 75 | 0 | 357.6059 | 98.22 | 23.22
2025-12-22 05:00:00 | 22.2 | 0 | 75 | 0 | 423.6059 | 97.2 | 22.2
2025-12-22 06:00:00 | 22.5 | 0 | 75 | 0 | 489.6059 | 97.5 | 22.5
2025-12-22 07:00:00 | 22.56 | 0 | 0 | 22.56 | 467.0459 | 0 | 22.56
2025-12-22 08:00:00 | 42.96 | 2.0691 | 0 | 40.8909 | 426.155 | 0 | 40.8909
2025-12-22 09:00:00 | 47.46 | 4.0796 | 0 | 43.3804 | 382.7746 | 2.8422e-14 | 43.3804
2025-12-22 10:00:00 | 45.42 | 5.5012 | 0 | 39.9188 | 342.8559 | -4.2633e-14 | 39.9188
2025-12-22 11:00:00 | 38.1 | 6.2371 | 0 | 31.8629 | 310.993 | 2.1316e-14 | 31.8629
2025-12-22 12:00:00 | 29.52 | 6.2371 | 0 | 23.2829 | 287.7101 | 1.7764e-14 | 23.2829
2025-12-22 13:00:00 | 44.58 | 5.5012 | 0 | 39.0788 | 248.6313 | -4.2633e-14 | 39.0788
2025-12-22 14:00:00 | 38.16 | 4.0796 | 0 | 34.0804 | 214.5509 | -7.816e-14 | 34.0804
2025-12-22 15:00:00 | 37.62 | 2.0691 | 0 | 35.5509 | 179 | -7.1054e-15 | 35.5509
2025-12-22 16:00:00 | 37.38 | 0 | 0 | 37.38 | 141.62 | 0 | 37.38
2025-12-22 17:00:00 | 39.18 | 0 | 0 | 39.18 | 102.44 | 0 | 39.18
2025-12-22 18:00:00 | 37.44 | 0 | 0 | 37.44 | 65 | 0 | 37.44
2025-12-22 19:00:00 | 46.62 | 0 | 71.22 | 0 | 127.6736 | 117.84 | 46.62
2025-12-22 20:00:00 | 48.3 | 0 | 69.54 | 0 | 188.8688 | 117.84 | 48.3
2025-12-22 21:00:00 | 45.06 | 0 | 72.78 | 0 | 252.9152 | 117.84 | 45.06
2025-12-22 22:00:00 | 49.38 | 0 | 31.6661 | 0 | 280.7814 | 81.0461 | 49.38
2025-12-22 23:00:00 | 56.82 | 0 | 0 | 0 | 280.7814 | 56.82 | 56.82
2025-12-23 00:00:00 | 55.98 | 0 | 0 | 0 | 280.7814 | 55.98 | 55.98
2025-12-23 01:00:00 | 41.04 | 0 | 0 | 0 | 280.7814 | 41.04 | 41.04
2025-12-23 02:00:00 | 37.62 | 0 | 0 | 0 | 280.7814 | 37.62 | 37.62
2025-12-23 03:00:00 | 38.64 | 0 | 75 | 0 | 346.7814 | 113.64 | 38.64
2025-12-23 04:00:00 | 38.64 | 0 | 75 | 0 | 412.7814 | 113.64 | 38.64
2025-12-23 05:00:00 | 35.58 | 0 | 75 | 0 | 478.7814 | 110.58 | 35.58
2025-12-23 06:00:00 | 21.84 | 0 | 75 | 0 | 544.7814 | 96.84 | 21.84
2025-12-23 07:00:00 | 21.72 | 0 | 0 | 21.72 | 523.0614 | 0 | 21.72
2025-12-23 08:00:00 | 24.42 | 2.072 | 0 | 22.348 | 500.7134 | -1.4211e-14 | 22.348
2025-12-23 09:00:00 | 52.38 | 4.0826 | 0 | 48.2974 | 452.416 | 2.8422e-14 | 48.2974
2025-12-23 10:00:00 | 47.16 | 5.5044 | 0 | 41.6556 | 410.7604 | -4.2633e-14 | 41.6556
2025-12-23 11:00:00 | 46.62 | 6.2403 | 0 | 40.3797 | 370.3807 | 4.9738e-14 | 40.3797
2025-12-23 12:00:00 | 46.92 | 6.2403 | 0 | 40.6797 | 329.701 | -4.9738e-14 | 40.6797
2025-12-23 13:00:00 | 47.94 | 5.5044 | 0 | 42.4356 | 287.2654 | -4.2633e-14 | 42.4356
2025-12-23 14:00:00 | 50.52 | 4.0826 | 0 | 46.4374 | 240.828 | -7.1054e-14 | 46.4374
2025-12-23 15:00:00 | 47.34 | 2.072 | 0 | 45.268 | 195.56 | -1.4211e-14 | 45.268
2025-12-23 16:00:00 | 45.9 | 0 | 0 | 45.9 | 149.66 | -9.9476e-14 | 45.9
2025-12-23 17:00:00 | 42.24 | 0 | 0 | 42.24 | 107.42 | 0 | 42.24
2025-12-23 18:00:00 | 42.42 | 0 | 0 | 42.42 | 65 | 0 | 42.42
2025-12-23 19:00:00 | 42.54 | 0 | 75 | 0 | 131 | 117.54 | 42.54
2025-12-23 20:00:00 | 42.84 | 0 | 75 | 0 | 197 | 117.84 | 42.84
2025-12-23 21:00:00 | 39.96 | 0 | 40.2865 | 0 | 232.4521 | 80.2465 | 39.96
2025-12-23 22:00:00 | 39.78 | 0 | 0 | 0 | 232.4521 | 39.78 | 39.78
2025-12-23 23:00:00 | 40.32 | 0 | 0 | 0 | 232.4521 | 40.32 | 40.32
2025-12-24 00:00:00 | 39.54 | 0 | 0 | 0 | 232.4521 | 39.54 | 39.54
2025-12-24 01:00:00 | 43.14 | 0 | 0 | 0 | 232.4521 | 43.14 | 43.14
2025-12-24 02:00:00 | 40.26 | 0 | 0 | 0 | 232.4521 | 40.26 | 40.26
2025-12-24 03:00:00 | 39.96 | 0 | 75 | 0 | 298.4521 | 114.96 | 39.96
2025-12-24 04:00:00 | 31.14 | 0 | 75 | 0 | 364.4521 | 106.14 | 31.14
2025-12-24 05:00:00 | 20.88 | 0 | 75 | 0 | 430.4521 | 95.88 | 20.88
2025-12-24 06:00:00 | 2.34 | 0 | 75 | 0 | 496.4521 | 77.34 | 2.34
2025-12-24 07:00:00 | 0 | 0 | 0 | 0 | 496.4521 | 0 | 0
2025-12-24 08:00:00 | 0 | 2.0764 | 2.0764 | 0 | 498.2794 | 1.7764e-15 | -2.0764
2025-12-24 09:00:00 | 15.42 | 4.0874 | 0 | 11.3326 | 486.9467 | 2.4869e-14 | 11.3326
2025-12-24 10:00:00 | 39.42 | 5.5093 | 0 | 33.9107 | 453.0361 | -4.9738e-14 | 33.9107
2025-12-24 11:00:00 | 38.82 | 6.2454 | 0 | 32.5746 | 420.4615 | 7.1054e-15 | 32.5746
2025-12-24 12:00:00 | 38.88 | 6.2454 | 0 | 32.6346 | 387.8268 | 1.4211e-14 | 32.6346
2025-12-24 13:00:00 | 55.74 | 5.5093 | 0 | 50.2307 | 337.5962 | -4.9738e-14 | 50.2307
2025-12-24 14:00:00 | 70.92 | 4.0874 | 0 | 66.8326 | 270.7636 | 2.8422e-14 | 66.8326
2025-12-24 15:00:00 | 68.94 | 2.0764 | 0 | 66.8636 | 203.9 | 2.8422e-14 | 66.8636
2025-12-24 16:00:00 | 55.26 | 0 | 0 | 55.26 | 148.64 | 0 | 55.26
2025-12-24 17:00:00 | 42.3 | 0 | 0 | 42.3 | 106.34 | 0 | 42.3
2025-12-24 18:00:00 | 41.34 | 0 | 0 | 41.34 | 65 | 0 | 41.34
2025-12-24 19:00:00 | 41.04 | 0 | 0 | 0 | 65 | 41.04 | 41.04
2025-12-24 20:00:00 | 39.06 | 0 | 0 | 0 | 65 | 39.06 | 39.06
2025-12-24 21:00:00 | 38.1 | 0 | 0 | 0 | 65 | 38.1 | 38.1
2025-12-24 22:00:00 | 27.84 | 0 | 0 | 0 | 65 | 27.84 | 27.84
2025-12-24 23:00:00 | 22.62 | 0 | 0 | 0 | 65 | 22.62 | 22.62
2025-12-25 00:00:00 | 21.96 | 0 | 0 | 0 | 65 | 21.96 | 21.96
2025-12-25 01:00:00 | 22.62 | 0 | 0 | 0 | 65 | 22.62 | 22.62
2025-12-25 02:00:00 | 33.66 | 0 | 0 | 0 | 65 | 33.66 | 33.66
2025-12-25 03:00:00 | 38.4 | 0 | 0 | 0 | 65 | 38.4 | 38.4
2025-12-25 04:00:00 | 38.52 | 0 | 0 | 0 | 65 | 38.52 | 38.52
2025-12-25 05:00:00 | 37.8 | 0 | 0 | 0 | 65 | 37.8 | 37.8
2025-12-25 06:00:00 | 27.72 | 0 | 0 | 0 | 65 | 27.72 | 27.72
2025-12-25 07:00:00 | 23.1 | 0 | 0 | 0 | 65 | 23.1 | 23.1
2025-12-25 08:00:00 | 21.66 | 2.0825 | 0 | 0 | 65 | 19.5775 | 19.5775
2025-12-25 09:00:00 | 25.08 | 4.0939 | 0 | 0 | 65 | 20.9861 | 20.9861
2025-12-25 10:00:00 | 38.94 | 5.5161 | 0 | 0 | 65 | 33.4239 | 33.4239
2025-12-25 11:00:00 | 39.3 | 6.2523 | 0 | 0 | 65 | 33.0477 | 33.0477
2025-12-25 12:00:00 | 38.82 | 6.2523 | 0 | 0 | 65 | 32.5677 | 32.5677
2025-12-25 13:00:00 | 38.4 | 5.5161 | 0 | 0 | 65 | 32.8839 | 32.8839
2025-12-25 14:00:00 | 38.1 | 4.0939 | 0 | 0 | 65 | 34.0061 | 34.0061
2025-12-25 15:00:00 | 38.58 | 2.0825 | 0 | 0 | 65 | 36.4975 | 36.4975
2025-12-25 16:00:00 | 40.2 | 0 | 0 | 0 | 65 | 40.2 | 40.2
2025-12-25 17:00:00 | 38.58 | 0 | 0 | 0 | 65 | 38.58 | 38.58
2025-12-25 18:00:00 | 38.58 | 0 | 75 | 0 | 131 | 113.58 | 38.58
2025-12-25 19:00:00 | 38.7 | 0 | 75 | 0 | 197 | 113.7 | 38.7
2025-12-25 20:00:00 | 30.9 | 0 | 10.9591 | 0 | 206.644 | 41.8591 | 30.9
2025-12-25 21:00:00 | 33.6 | 0 | 0 | 0 | 206.644 | 33.6 | 33.6
2025-12-25 22:00:00 | 36.48 | 0 | 0 | 0 | 206.644 | 36.48 | 36.48
2025-12-25 23:00:00 | 36.66 | 0 | 0 | 0 | 206.644 | 36.66 | 36.66
2025-12-26 00:00:00 | 36.96 | 0 | 0 | 0 | 206.644 | 36.96 | 36.96
2025-12-26 01:00:00 | 36.78 | 0 | 0 | 0 | 206.644 | 36.78 | 36.78
2025-12-26 02:00:00 | 36.84 | 0 | 0 | 0 | 206.644 | 36.84 | 36.84
2025-12-26 03:00:00 | 36.84 | 0 | 0 | 0 | 206.644 | 36.84 | 36.84
2025-12-26 04:00:00 | 36.78 | 0 | 75 | 0 | 272.644 | 111.78 | 36.78
2025-12-26 05:00:00 | 28.02 | 0 | 75 | 0 | 338.644 | 103.02 | 28.02
2025-12-26 06:00:00 | 24.72 | 0 | 75 | 0 | 404.644 | 99.72 | 24.72
2025-12-26 07:00:00 | 22.8 | 0 | 0 | 22.8 | 381.844 | 0 | 22.8
2025-12-26 08:00:00 | 21.96 | 2.0902 | 0 | 19.8698 | 361.9742 | -3.1974e-14 | 19.8698
2025-12-26 09:00:00 | 22.8 | 4.1021 | 0 | 18.6979 | 343.2763 | -3.5527e-15 | 18.6979
2025-12-26 10:00:00 | 21.72 | 5.5247 | 0 | 16.1953 | 327.081 | -4.6185e-14 | 16.1953
2025-12-26 11:00:00 | 23.22 | 6.261 | 0 | 16.959 | 310.122 | 3.5527e-14 | 16.959
2025-12-26 12:00:00 | 22.38 | 6.261 | 0 | 16.119 | 294.003 | 3.5527e-14 | 16.119
2025-12-26 13:00:00 | 22.62 | 5.5247 | 0 | 17.0953 | 276.9077 | -4.2633e-14 | 17.0953
2025-12-26 14:00:00 | 38.46 | 4.1021 | 0 | 34.3579 | 242.5498 | 0 | 34.3579
2025-12-26 15:00:00 | 49.26 | 2.0902 | 0 | 47.1698 | 195.38 | -2.8422e-14 | 47.1698
2025-12-26 16:00:00 | 47.82 | 0 | 0 | 47.82 | 147.56 | 0 | 47.82
2025-12-26 17:00:00 | 44.94 | 0 | 0 | 44.94 | 102.62 | 0 | 44.94
2025-12-26 18:00:00 | 37.62 | 0 | 0 | 37.62 | 65 | 0 | 37.62
2025-12-26 19:00:00 | 23.94 | 0 | 0 | 0 | 65 | 23.94 | 23.94
2025-12-26 20:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-12-26 21:00:00 | 23.52 | 0 | 0 | 0 | 65 | 23.52 | 23.52
2025-12-26 22:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-12-26 23:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-12-27 00:00:00 | 23.1 | 0 | 0 | 0 | 65 | 23.1 | 23.1
2025-12-27 01:00:00 | 22.62 | 0 | 0 | 0 | 65 | 22.62 | 22.62
2025-12-27 02:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-12-27 03:00:00 | 22.56 | 0 | 0 | 0 | 65 | 22.56 | 22.56
2025-12-27 04:00:00 | 22.8 | 0 | 0 | 0 | 65 | 22.8 | 22.8
2025-12-27 05:00:00 | 22.5 | 0 | 0 | 0 | 65 | 22.5 | 22.5
2025-12-27 06:00:00 | 22.02 | 0 | 0 | 0 | 65 | 22.02 | 22.02
2025-12-27 07:00:00 | 22.86 | 0 | 0 | 0 | 65 | 22.86 | 22.86
2025-12-27 08:00:00 | 22.38 | 2.0996 | 0 | 0 | 65 | 20.2804 | 20.2804
2025-12-27 09:00:00 | 26.34 | 4.112 | 0 | 0 | 65 | 22.228 | 22.228
2025-12-27 10:00:00 | 39.66 | 5.535 | 0 | 0 | 65 | 34.125 | 34.125
2025-12-27 11:00:00 | 48.6 | 6.2716 | 0 | 0 | 65 | 42.3284 | 42.3284
2025-12-27 12:00:00 | 49.86 | 6.2716 | 0 | 0 | 65 | 43.5884 | 43.5884
2025-12-27 13:00:00 | 49.62 | 5.535 | 0 | 0 | 65 | 44.085 | 44.085
2025-12-27 14:00:00 | 47.22 | 4.112 | 0 | 0 | 65 | 43.108 | 43.108
2025-12-27 15:00:00 | 42.36 | 2.0996 | 0 | 0 | 65 | 40.2604 | 40.2604
2025-12-27 16:00:00 | 42.42 | 0 | 0 | 0 | 65 | 42.42 | 42.42
2025-12-27 17:00:00 | 41.1 | 0 | 0 | 0 | 65 | 41.1 | 41.1
2025-12-27 18:00:00 | 41.58 | 0 | 0 | 0 | 65 | 41.58 | 41.58
2025-12-27 19:00:00 | 35.04 | 0 | 0 | 0 | 65 | 35.04 | 35.04
2025-12-27 20:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-12-27 21:00:00 | 22.08 | 0 | 0 | 0 | 65 | 22.08 | 22.08
2025-12-27 22:00:00 | 22.68 | 0 | 0 | 0 | 65 | 22.68 | 22.68
2025-12-27 23:00:00 | 21.96 | 0 | 0 | 0 | 65 | 21.96 | 21.96
2025-12-28 00:00:00 | 22.32 | 0 | 0 | 0 | 65 | 22.32 | 22.32
2025-12-28 01:00:00 | 22.44 | 0 | 0 | 0 | 65 | 22.44 | 22.44
2025-12-28 02:00:00 | 22.26 | 0 | 0 | 0 | 65 | 22.26 | 22.26
2025-12-28 03:00:00 | 22.26 | 0 | 0 | 0 | 65 | 22.26 | 22.26
2025-12-28 04:00:00 | 28.56 | 0 | 0 | 0 | 65 | 28.56 | 28.56
2025-12-28 05:00:00 | 39 | 0 | 0 | 0 | 65 | 39 | 39
2025-12-28 06:00:00 | 38.22 | 0 | 0 | 0 | 65 | 38.22 | 38.22
2025-12-28 07:00:00 | 36.78 | 0 | 0 | 0 | 65 | 36.78 | 36.78
2025-12-28 08:00:00 | 21.66 | 2.1105 | 0 | 0 | 65 | 19.5495 | 19.5495
2025-12-28 09:00:00 | 26.82 | 4.1236 | 0 | 0 | 65 | 22.6964 | 22.6964
2025-12-28 10:00:00 | 29.94 | 5.5471 | 0 | 0 | 65 | 24.3929 | 24.3929
2025-12-28 11:00:00 | 38.16 | 6.284 | 0 | 0 | 65 | 31.876 | 31.876
2025-12-28 12:00:00 | 41.28 | 6.284 | 0 | 0 | 65 | 34.996 | 34.996
2025-12-28 13:00:00 | 38.52 | 5.5471 | 0 | 0 | 65 | 32.9729 | 32.9729
2025-12-28 14:00:00 | 37.98 | 4.1236 | 0 | 0 | 65 | 33.8564 | 33.8564
2025-12-28 15:00:00 | 38.7 | 2.1105 | 0 | 0 | 65 | 36.5895 | 36.5895
2025-12-28 16:00:00 | 37.62 | 0 | 0 | 0 | 65 | 37.62 | 37.62
2025-12-28 17:00:00 | 24.06 | 0 | 0 | 0 | 65 | 24.06 | 24.06
2025-12-28 18:00:00 | 22.02 | 0 | 75 | 0 | 131 | 97.02 | 22.02
2025-12-28 19:00:00 | 21.84 | 0 | 71.1833 | 0 | 193.6413 | 93.0233 | 21.84
2025-12-28 20:00:00 | 36.96 | 0 | 0 | 0 | 193.6413 | 36.96 | 36.96
2025-12-28 21:00:00 | 37.8 | 0 | 0 | 0 | 193.6413 | 37.8 | 37.8
2025-12-28 22:00:00 | 36.3 | 0 | 0 | 0 | 193.6413 | 36.3 | 36.3
2025-12-28 23:00:00 | 36.3 | 0 | 0 | 0 | 193.6413 | 36.3 | 36.3
2025-12-29 00:00:00 | 36.9 | 0 | 0 | 0 | 193.6413 | 36.9 | 36.9
2025-12-29 01:00:00 | 37.5 | 0 | 0 | 0 | 193.6413 | 37.5 | 37.5
2025-12-29 02:00:00 | 36.72 | 0 | 0 | 0 | 193.6413 | 36.72 | 36.72
2025-12-29 03:00:00 | 37.56 | 0 | 75 | 0 | 259.6413 | 112.56 | 37.56
2025-12-29 04:00:00 | 36.78 | 0 | 75 | 0 | 325.6413 | 111.78 | 36.78
2025-12-29 05:00:00 | 37.68 | 0 | 75 | 0 | 391.6413 | 112.68 | 37.68
2025-12-29 06:00:00 | 37.92 | 0 | 75 | 0 | 457.6413 | 112.92 | 37.92
2025-12-29 07:00:00 | 38.4 | 0 | 0 | 38.4 | 419.2413 | 0 | 38.4
2025-12-29 08:00:00 | 39.12 | 2.123 | 0 | 36.997 | 382.2444 | -2.1316e-14 | 36.997
2025-12-29 09:00:00 | 38.22 | 4.137 | 0 | 34.083 | 348.1613 | -7.1054e-15 | 34.083
2025-12-29 10:00:00 | 32.76 | 5.5611 | 0 | 27.1989 | 320.9624 | 2.4869e-14 | 27.1989
2025-12-29 11:00:00 | 21.3 | 6.2982 | 0 | 15.0018 | 305.9607 | 4.6185e-14 | 15.0018
2025-12-29 12:00:00 | 20.52 | 6.2982 | 0 | 14.2218 | 291.7389 | 4.4409e-14 | 14.2218
2025-12-29 13:00:00 | 20.76 | 5.5611 | 0 | 15.1989 | 276.54 | 2.8422e-14 | 15.1989
2025-12-29 14:00:00 | 28.8 | 4.137 | 0 | 24.663 | 251.877 | 0 | 24.663
2025-12-29 15:00:00 | 39.12 | 2.123 | 0 | 36.997 | 214.88 | -2.1316e-14 | 36.997
2025-12-29 16:00:00 | 42.06 | 0 | 0 | 42.06 | 172.82 | 0 | 42.06
2025-12-29 17:00:00 | 54.36 | 0 | 0 | 54.36 | 118.46 | 0 | 54.36
2025-12-29 18:00:00 | 53.46 | 0 | 0 | 53.46 | 65 | 0 | 53.46
2025-12-29 19:00:00 | 36.72 | 0 | 75 | 0 | 131 | 111.72 | 36.72
2025-12-29 20:00:00 | 31.8 | 0 | 0 | 0 | 131 | 31.8 | 31.8
2025-12-29 21:00:00 | 21.3 | 0 | 0 | 0 | 131 | 21.3 | 21.3
2025-12-29 22:00:00 | 21.24 | 0 | 0 | 0 | 131 | 21.24 | 21.24
2025-12-29 23:00:00 | 21.54 | 0 | 0 | 0 | 131 | 21.54 | 21.54
2025-12-30 00:00:00 | 21 | 0 | 0 | 0 | 131 | 21 | 21
2025-12-30 01:00:00 | 21.72 | 0 | 0 | 0 | 131 | 21.72 | 21.72
2025-12-30 02:00:00 | 21 | 0 | 0 | 0 | 131 | 21 | 21
2025-12-30 03:00:00 | 20.88 | 0 | 75 | 0 | 197 | 95.88 | 20.88
2025-12-30 04:00:00 | 21.9 | 0 | 75 | 0 | 263 | 96.9 | 21.9
2025-12-30 05:00:00 | 21.6 | 0 | 75 | 0 | 329 | 96.6 | 21.6
2025-12-30 06:00:00 | 21.36 | 0 | 75 | 0 | 395 | 96.36 | 21.36
2025-12-30 07:00:00 | 21.18 | 0 | 0 | 21.18 | 373.82 | 0 | 21.18
2025-12-30 08:00:00 | 20.82 | 2.1372 | 0 | 18.6828 | 355.1372 | -7.1054e-15 | 18.6828
2025-12-30 09:00:00 | 20.88 | 4.1521 | 0 | 16.7279 | 338.4092 | 1.7764e-14 | 16.7279
2025-12-30 10:00:00 | 21.9 | 5.5768 | 0 | 16.3232 | 322.086 | -4.6185e-14 | 16.3232
2025-12-30 11:00:00 | 21.3 | 6.3143 | 0 | 14.9857 | 307.1003 | -1.7764e-15 | 14.9857
2025-12-30 12:00:00 | 20.82 | 6.3143 | 0 | 14.5057 | 292.5946 | -1.7764e-15 | 14.5057
2025-12-30 13:00:00 | 20.88 | 5.5768 | 0 | 15.3032 | 277.2914 | -4.4409e-14 | 15.3032
2025-12-30 14:00:00 | 21.12 | 4.1521 | 0 | 16.9679 | 260.3234 | 1.7764e-14 | 16.9679
2025-12-30 15:00:00 | 27.12 | 2.1372 | 0 | 24.9828 | 235.3406 | -1.0658e-13 | 24.9828
2025-12-30 16:00:00 | 39.42 | 0 | 0 | 39.42 | 195.9206 | 0 | 39.42
2025-12-30 17:00:00 | 54.36 | 0 | 0 | 54.36 | 141.5606 | 0 | 54.36
2025-12-30 18:00:00 | 48.6 | 0 | 0 | 48.6 | 92.9606 | 0 | 48.6
2025-12-30 19:00:00 | 39.54 | 0 | 75 | 0 | 158.9606 | 114.54 | 39.54
2025-12-30 20:00:00 | 30.18 | 0 | 53.2309 | 0 | 205.8037 | 83.4109 | 30.18
2025-12-30 21:00:00 | 27 | 0 | 0 | 0 | 205.8037 | 27 | 27
2025-12-30 22:00:00 | 23.88 | 0 | 0 | 0 | 205.8037 | 23.88 | 23.88
2025-12-30 23:00:00 | 22.44 | 0 | 0 | 0 | 205.8037 | 22.44 | 22.44
2025-12-31 00:00:00 | 23.52 | 0 | 0 | 0 | 205.8037 | 23.52 | 23.52
2025-12-31 01:00:00 | 22.5 | 0 | 0 | 0 | 205.8037 | 22.5 | 22.5
2025-12-31 02:00:00 | 22.74 | 0 | 0 | 0 | 205.8037 | 22.74 | 22.74
2025-12-31 03:00:00 | 23.46 | 0 | 0 | 0 | 205.8037 | 23.46 | 23.46
2025-12-31 04:00:00 | 22.08 | 0 | 75 | 0 | 271.8037 | 97.08 | 22.08
2025-12-31 05:00:00 | 22.56 | 0 | 75 | 0 | 337.8037 | 97.56 | 22.56
2025-12-31 06:00:00 | 23.46 | 0 | 75 | 0 | 403.8037 | 98.46 | 23.46
2025-12-31 07:00:00 | 22.14 | 0 | 0 | 22.14 | 381.6637 | 0 | 22.14
2025-12-31 08:00:00 | 21.96 | 2.1529 | 0 | 19.8071 | 361.8567 | 2.8422e-14 | 19.8071
2025-12-31 09:00:00 | 26.7 | 4.1688 | 0 | 22.5312 | 339.3255 | 3.5527e-14 | 22.5312
2025-12-31 10:00:00 | 24.78 | 5.5943 | 0 | 19.1857 | 320.1397 | -4.2633e-14 | 19.1857
2025-12-31 11:00:00 | 23.1 | 6.3321 | 0 | 16.7679 | 303.3719 | -3.5527e-14 | 16.7679
2025-12-31 12:00:00 | 22.02 | 6.3321 | 0 | 15.6879 | 287.684 | -3.7303e-14 | 15.6879
2025-12-31 13:00:00 | 38.46 | 5.5943 | 0 | 32.8657 | 254.8183 | -4.2633e-14 | 32.8657
2025-12-31 14:00:00 | 45.18 | 4.1688 | 0 | 41.0112 | 213.8071 | 1.35e-13 | 41.0112
2025-12-31 15:00:00 | 45.6 | 2.1529 | 0 | 43.4471 | 170.36 | -7.1054e-14 | 43.4471
2025-12-31 16:00:00 | 46.44 | 0 | 0 | 46.44 | 123.92 | 0 | 46.44
2025-12-31 17:00:00 | 31.8 | 0 | 0 | 31.8 | 92.12 | 0 | 31.8
2025-12-31 18:00:00 | 27.12 | 0 | 0 | 27.12 | 65 | 0 | 27.12
2025-12-31 19:00:00 | 25.02 | 0 | 70.4545 | 0 | 127 | 95.4745 | 25.02
2025-12-31 20:00:00 | 24 | 0 | 75 | 0 | 193 | 99 | 24
2025-12-31 21:00:00 | 22.32 | 0 | 75 | 0 | 259 | 97.32 | 22.32
2025-12-31 22:00:00 | 22.74 | 0 | 75 | 0 | 325 | 97.74 | 22.74
2025-12-31 23:00:00 | 22.26 | 0 | 0 | 0 | 325 | 22.26 | 22.26